## Year to Date
ALIGNED |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 14610580.6649 | 14622282.106 | -11701.4411 | -0.08002% | 15654671.846 | -1044091.1811 | -6.67%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 1614913.395 | 1536598.695 | 78314.7 | 5.097% | 1393700 | -213898.105 | -15.35%
Loudon - 7046 Pleasant Street | NH | 1729294.8755 | 1796636.37 | -67341.4945 | -3.748% | 1951173.596 | -221878.7205 | -11.37%
Nashua - Pennichuck Water East | NH | 1668835.5001 | 1586536.245 | 82299.2551 | 5.187% | 1337808 | 331027.5001 | 24.74%
Nashua - Pennichuck Water West | NH | 1297017.3311 | 961368.057 | 335649.2741 | 34.91% | 705300 | -29056.5002 | -4.12%
Boothbay - Wiscasset Road | ME | 1459125.813 | 1583407.602 | -124281.789 | -7.849% | 1558392.5 | -99266.687 | -6.37%
Thorndike - Leonard Road | ME | 1448377 | 1362062.954 | 86314.046 | 6.337% | 2880197.25 | -1431820.25 | -49.71%
Topsham - Solarize LLC | ME | 1158444.5003 | 1185797.615 | -27353.1148 | -2.307% | 1614205 | -455760.4997 | -28.23%
Cherryfield - 727 North Main St (IRA) | ME | 2180792 | 2351770.3 | -170978.3 | -7.27% | 2122817.9 | 57974.1 | 2.731%
ME: Bucksport - 258 Route 1 (IRA) | ME | 1007565 | 1152165.7 | -144600.7 | -12.55% | 1150920.1 | -143355.1 | -12.46%
ME: Union - Route 131 (IRA) | ME | 1046215.25 | 1105938.568 | -59723.318 | -5.4% | 940157.5 | 106057.75 | 11.28%

## 1st Qtr
ALIGNED |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1148376.8312 | 1241693.46 | -93316.6288 | -7.515% | 720076.4 | 428300.4312 | 59.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 265531 | 297220.15 | -31689.15 | -10.66% | 0 | 0
Loudon - 7046 Pleasant Street | NH | 304616.5 | 396427 | -91810.5 | -23.16% | 430004.4 | -125387.9 | -29.16%
Nashua - Pennichuck Water East | NH | 331162.5 | 294876.74 | 36285.76 | 12.31% | 290072 | 41090.5 | 14.17%
Nashua - Pennichuck Water West | NH | 247066.8312 | 253169.57 | -6102.7388 | -2.411% | 0 | 0
Boothbay - Wiscasset Road | ME | 0 | 0 | 0 |  | 0 | 0
Thorndike - Leonard Road | ME | 0 | 0 | 0 |  | 0 | 0
Topsham - Solarize LLC | ME | 0 | 0 | 0 |  | 0 | 0
Cherryfield - 727 North Main St (IRA) | ME | 0 | 0 | 0 |  | 0 | 0
ME: Bucksport - 258 Route 1 (IRA) | ME | 0 | 0 | 0 |  | 0 | 0
ME: Union - Route 131 (IRA) | ME | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
ALIGNED |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 3748877.5631 | 3799021.618 | -50144.0549 | -1.32% | 4076410.066 | -327532.5029 | -8.035%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 488150 | 479099.015 | 9050.985 | 1.889% | 432000 | -113430.5 | -26.26%
Loudon - 7046 Pleasant Street | NH | 509622.9999 | 491386.03 | 18236.9699 | 3.711% | 596309.116 | -86686.1161 | -14.54%
Nashua - Pennichuck Water East | NH | 484488 | 531144.565 | -46656.565 | -8.784% | 417272 | 67216 | 16.11%
Nashua - Pennichuck Water West | NH | 373707 | 275557.057 | 98149.943 | 35.62% | 0 | 0
Boothbay - Wiscasset Road | ME | 532951.813 | 564398.352 | -31446.539 | -5.572% | 611598.5 | -78646.687 | -12.86%
Thorndike - Leonard Road | ME | 495412.1875 | 557091.494 | -61679.3065 | -11.07% | 1251734.55 | -756322.3625 | -60.42%
Topsham - Solarize LLC | ME | 420394.2503 | 419567.005 | 827.2453 | 0.1972% | 335730 | 84664.2503 | 25.22%
Cherryfield - 727 North Main St (IRA) | ME | 444151.3125 | 480778.1 | -36626.7875 | -7.618% | 431765.9 | 12385.4125 | 2.869%
ME: Bucksport - 258 Route 1 (IRA) | ME | 0 | 0 | 0 |  | 0 | 0
ME: Union - Route 131 (IRA) | ME | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
ALIGNED |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 5975550.5685 | 5862893.868 | 112656.7005 | 1.922% | 6436669.3 | -461118.7315 | -7.164%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 593255.08 | 539017.6 | 54237.48 | 10.06% | 614000 | -20744.92 | -3.379%
Loudon - 7046 Pleasant Street | NH | 606757.5 | 574404.1 | 32353.4 | 5.633% | 593353.4 | 13404.1 | 2.259%
Nashua - Pennichuck Water East | NH | 547500.5 | 553981.3 | -6480.8 | -1.17% | 411544 | 135956.5 | 33.04%
Nashua - Pennichuck Water West | NH | 441646.2385 | 322511.4 | 119134.8385 | 36.94% | 451700 | -10053.7615 | -2.226%
Boothbay - Wiscasset Road | ME | 621978 | 653090.3 | -31112.3 | -4.764% | 642676 | -20698 | -3.221%
Thorndike - Leonard Road | ME | 658191.8125 | 606091.7 | 52100.1125 | 8.596% | 1280411.5 | -622219.6875 | -48.6%
Topsham - Solarize LLC | ME | 490844.25 | 493451 | -2606.75 | -0.5283% | 467119 | 23725.25 | 5.079%
Cherryfield - 727 North Main St (IRA) | ME | 1236861.6875 | 1322815.7 | -85954.0125 | -6.498% | 1224259.4 | 12602.2875 | 1.029%
ME: Bucksport - 258 Route 1 (IRA) | ME | 388976 | 407109.4 | -18133.4 | -4.454% | 393074.5 | -4098.5 | -1.043%
ME: Union - Route 131 (IRA) | ME | 389539.5 | 390421.368 | -881.868 | -0.2259% | 358531.5 | 31008 | 8.649%

## 4th Qtr
ALIGNED |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 3737775.7019 | 3718673.16 | 19102.5419 | 0.5137% | 4421516.08 | -683740.3781 | -15.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 267977.315 | 221261.93 | 46715.385 | 21.11% | 347700 | -79722.685 | -22.93%
Loudon - 7046 Pleasant Street | NH | 308297.8756 | 334419.24 | -26121.3644 | -7.811% | 331506.68 | -23208.8044 | -7.001%
Nashua - Pennichuck Water East | NH | 305684.5 | 206533.64 | 99150.86 | 48.01% | 218920 | 86764.5 | 39.63%
Nashua - Pennichuck Water West | NH | 234597.2613 | 110130.03 | 124467.2313 | 113% | 253600 | -19002.7387 | -7.493%
Boothbay - Wiscasset Road | ME | 304196 | 365918.95 | -61722.95 | -16.87% | 304118 | 78 | 0.02565%
Thorndike - Leonard Road | ME | 294773 | 198879.76 | 95893.24 | 48.22% | 348051.2 | -53278.2 | -15.31%
Topsham - Solarize LLC | ME | 247206 | 272779.61 | -25573.61 | -9.375% | 811356 | -564150 | -69.53%
Cherryfield - 727 North Main St (IRA) | ME | 499779 | 548176.5 | -48397.5 | -8.829% | 466792.6 | 32986.4 | 7.067%
ME: Bucksport - 258 Route 1 (IRA) | ME | 618589 | 745056.3 | -126467.3 | -16.97% | 757845.6 | -139256.6 | -18.38%
ME: Union - Route 131 (IRA) | ME | 656675.75 | 715517.2 | -58841.45 | -8.224% | 581626 | 75049.75 | 12.9%

## Jan
ALIGNED |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 346871.4782 | 348784.49 | -1913.0118 | -0.5485% | 194816.2 | 152055.2782 | 78.05% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 80975 | 75060.55 | 5914.45 | 7.88% | N/A |  |  | 1. The Site tripped offline at 10:00AM to 12:15 on 01/10 due to tech on site to work on the air break switch at the pole. 2. The site tripped offline at 01:15 AM on 01/20 due to the main breaker tripping. The site back online at 10:15 on 01/21 after resetting the SEL and main breaker. 3. Inverter 4 offline from 11/30/2024 due to Permanent fault of power module - Fault and it has been RMA'd & remain offline from 12/02/2024. | 1. SR094963 2. SR095713 3. SR093738
Loudon - 7046 Pleasant Street | NH | 94149.5 | 123337.6 | -29188.1 | -23.67% | 122352.2 | -28202.7 | -23.05% | 1. The site tripped offline from 10:15 to 13:15 on 01/08 due to Grid Phase Voltage out of range. After being re-energized, the site is back online. | 1. SR095389
Nashua - Pennichuck Water East | NH | 97358.6357 | 67312.38 | 30046.2557 | 44.64% | 72464 | 24894.6357 | 34.35% | 1. Weather station experiencing seasonal shading from January to March resulting in expected energy value reporting low. Actual production is not being impacted | 1. SR099647
Nashua - Pennichuck Water West | NH | 74388.3425 | 83073.96 | -8685.6175 | -10.46% | N/A |  |  | 1. Site generation was low due to rain/snow
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## Feb
ALIGNED |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 260811.3697 | 383101.45 | -122290.0803 | -31.92% | 231043.9 | 29767.4697 | 12.88% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 50574.1816 | 92518.7 | -41944.5184 | -45.34% | N/A |  |  | 1. Inverter 4 offline from 11/30/2024 due to Permanent fault of power module - Fault and it has been RMA'd & remain offline from 12/02/24. | 1.SR093738
Loudon - 7046 Pleasant Street | NH | 68847.5 | 123029.3 | -54181.8 | -44.04% | 139243.9 | -70396.4 | -50.56% | 1. Site generation was low due to rain/snow
Nashua - Pennichuck Water East | NH | 84190.3643 | 90026.76 | -5836.3957 | -6.483% | 91800 | -7609.6357 | -8.289% | 1. Weather station experiencing seasonal shading from January to March resulting in expected energy value reporting low. Actual production is not being impacted | 1. SR099647
Nashua - Pennichuck Water West | NH | 57199.3238 | 77526.69 | -20327.3662 | -26.22% | N/A |  |  | 1. Site generation was low due to rain/snow
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## Mar
ALIGNED |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 540693.9834 | 509807.52 | 30886.4634 | 6.058% | 294216.3 | 246477.6834 | 83.77% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 133981.8184 | 129640.9 | 4340.9184 | 3.348% | N/A |  |  | 1. Site tripped offline at 11:00 AM due to main breaker trip and back online at 15:45 on 03/07 after technician has reset the relay. 2.Site tripped offline at 5:15 AM on 03/17 due to main breaker trip and back online at 8:15AM on 03/18 after technician reset relay. 3.Inverter 4 was offline from 11/30/2024 due to Permanent fault of power module - Fault0010 and it has been RMA'd from 12/02/24. Technician has replaced the RMA'd inverter with a new Chint inverter, bringing it back online and producing from 03/12 at 13:00. | 1.SR098258 2.SR098648 3.SR093738 | SR098648 | SR093738
Loudon - 7046 Pleasant Street | NH | 141619.5 | 150060.1 | -8440.6 | -5.625% | 168408.3 | -26788.8 | -15.91% | 1.Site tripped offline at 5:33AM on 03/07 due to utility outage and was back online at 14:45 on 03/08 after technician has reset SEL and re-energize the site. | 1.SR098240
Nashua - Pennichuck Water East | NH | 149613.5 | 137537.6 | 12075.9 | 8.78% | 125808 | 23805.5 | 18.92% | 1. Weather station experiencing seasonal shading from January to March resulting in expected energy value reporting low. Actual production is not being impacted | 1. SR099647
Nashua - Pennichuck Water West | NH | 115479.165 | 92568.92 | 22910.245 | 24.75% | N/A
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## Apr
ALIGNED |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 1104316.488 | 1080231.758 | 24084.73 | 2.23% | 893850.366 | 210466.122 | 23.55% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 169580.5 | 161751.515 | 7828.985 | 4.84% | N/A |  |  | 1.Site tripped offline between 8:45AM to 11:45Am on 04/07 due to loss of utility power later technician reset main breaker and re-energised the site. | 1.SR099472
Loudon - 7046 Pleasant Street | NH | 169913.505 | 165500.23 | 4413.275 | 2.667% | 174527.016 | -4613.511 | -2.643% | 1. Inverter 1.2 has tripped offline 13:30 on 04/29 due to Grid Phase Voltage Out of Range - GridV.OutLim fault. Inverter self resolved at 15:45 on the same day. | 1.SR100664
Nashua - Pennichuck Water East | NH | 164578.201 | 175490.065 | -10911.864 | -6.218% | 131376 | 33202.201 | 25.27% | 1.Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. | 1.SR099647
Nashua - Pennichuck Water West | NH | 126556 | 96930.197 | 29625.803 | 30.56% | N/A |  |  | 1. Inverter 5 experienced derating of approximately 44 kW to 50 kW during peak hours on 04/19, 04/24, 04/28, and 04/29 due to an External Fan Error. The issue self-resolved on the following days. | 1.SR100020
Boothbay - Wiscasset Road | ME | 174667.813 | 176099.452 | -1431.639 | -0.813% | 186747.5 | -12079.687 | -6.468%
Thorndike - Leonard Road | ME | 165038.875 | 172328.694 | -7289.819 | -4.23% | 380764.85 | -215725.975 | -56.66% | 1.Site tripped offline from 12:15AM to 14:00 on 04/07. | 1.SR099480
Topsham - Solarize LLC | ME | 133981.594 | 132131.605 | 1849.989 | 1.4% | 20435 | 113546.594 | 555.6% | 1.Inverter 1 tripped offline at 12:30 AM on 04/24 due to a "Grid Voltage > Installation" fault related to a grid connection issue. It was brought back online at 4:45 PM the same day after a technician reset the breaker. 2.The weather station has been starting late on multiple days throughout the month. | 1.SR100347
Cherryfield - 727 North Main St (IRA) | ME
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## May
ALIGNED |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 1018446.9401 | 1011175.54 | 7271.4001 | 0.7191% | 1376423.3 | -357976.3599 | -26.01% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 133175 | 133034.1 | 140.9 | 0.1059% | 216200 | -83025 | -38.4% | 1. The site tripped offline at 08:00 on 05/12 due to a main breaker trip. A technician was on-site on 05/13 and reset the breaker. The site came back online at 16:00 on 05/13. 2. The site was taken offline from 12:53 to 13:27 on 05/16 while a technician was on-site for a preventive maintenance work. | 1. SR101376 2. PM8049
Loudon - 7046 Pleasant Street | NH | 157983.6224 | 148646.9 | 9336.7224 | 6.281% | 211772.2 | -53788.5776 | -25.4%
Nashua - Pennichuck Water East | NH | 142766.1615 | 162107 | -19340.8385 | -11.93% | 144688 | -1921.8385 | -1.328% | 1. The site tripped offline at 08:30 on 05/28. The technician later re-energized the site, and it came back online at 15:00 on 05/28. 2. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. | 1. SR102029 2. SR099647 | SR099647
Nashua - Pennichuck Water West | NH | 109093 | 83703.94 | 25389.06 | 30.33% | N/A |  |  | 1. The site tripped offline at 08:30 on 05/28. The technician later re-energized the site, and it came back online at 15:00 on 05/28. 2. The site tripped offline at 11:45 on 05/31. The technician later re-energized the site, and it came back online at 13:45 on 05/31. 3. Inverter 5 has been experiencing derating of approximately 44 to 50 kW during peak hours due to an "External Fan Err" since 04/19. A technician was on-site on 05/19, removed the faulty fan, and installed a new RMA’d fan. The inverter has been producing in line with its peers since 15:00 on 05/19. | 1. SR102030 2. SR102218 3. SR100020 | SR102218 | SR100020
Boothbay - Wiscasset Road | ME | 173991 | 176162 | -2171 | -1.232% | 213942 | -39951 | -18.67% | 1. Site production was low on 05/08 and 05/09 because a technician was on-site performing preventive maintenance work. | 1. PM13669
Thorndike - Leonard Road | ME | 172047.625 | 178637.2 | -6589.575 | -3.689% | 432588.1 | -260540.475 | -60.23% | 1. Inverters 2 and 3 tripped offline at 14:15 on 05/28 due to "Waiting for grid voltage > Installation failure grid connection > Check grid and fuses". A technician was on-site on 05/29 and closed the inverter breakers. Both inverters came back online at 15:00 on 05/29. However, Inverter 2 tripped offline again at 10:15 on 05/30, followed by Inverter 3 at 13:30 on 05/30, both due to "Waiting for grid voltage". | 1. SR102061
Topsham - Solarize LLC | ME | 129390.5312 | 128884.4 | 506.1313 | 0.3927% | 157233 | -27842.4688 | -17.71% | 1. Inverter 1 tripped offline at 11:30 on 05/01due to "Waiting for grid voltage > Installation failure grid connection > Check grid and fuses". A technician was on-site on 05/01 and replaced the faulty inverter breaker with a spare one. The inverter came back online at 15:30 on 05/21. | 1. SR100825
Cherryfield - 727 North Main St (IRA) | ME
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## Jun
ALIGNED |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 1626114.135 | 1707614.32 | -81500.185 | -4.773% | 1806136.4 | -180022.265 | -9.967% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 185394.5 | 184313.4 | 1081.1 | 0.5866% | 215800 | -30405.5 | -14.09% | 1. The site tripped offline at 11:15 on 06/11 and came back online at 16:04 on the same day. 2. Inverter 2 tripped offline at 15:00 on 06/23 due to 'Grid Line Voltage Out of Range' and came back online at 10:00 on 06/24. 3. Inverter 3 tripped offline at 07:00 on 06/12 and came back online at 07:15 on 06/13. | 1. SR102825 2. SR103332 3. SR102780 | SR103332 | SR102780
Loudon - 7046 Pleasant Street | NH | 181725.8725 | 177238.9 | 4486.9725 | 2.532% | 210009.9 | -28284.0275 | -13.47% | 1. The site tripped offline at 13:30 on 06/20 and came back online at 12:45 on 06/21. | 1. SR103230
Nashua - Pennichuck Water East | NH | 177143.6375 | 193547.5 | -16403.8625 | -8.475% | 141208 | 35935.6375 | 25.45% | 1. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. | 1. SR099647
Nashua - Pennichuck Water West | NH | 138058 | 94922.92 | 43135.08 | 45.44%
Boothbay - Wiscasset Road | ME | 184293 | 212136.9 | -27843.9 | -13.13% | 210909 | -26616 | -12.62% | 1. Inverter 4 tripped offline at 14:45 on 06/05 due to 'Waiting for Grid Voltages' and came back online at 14:45 on 06/06. It tripped offline again at 11:45 on 06/08 due to 'Installation Failure - Grid Connection' and later came back online at 13:00 on 06/10. 2. Inverter 5 tripped offline at 10:00 on 06/11 and has been offline since then. | 1. SR102549 2. SR102549, SR102969 | SR102549 | SR102969
Thorndike - Leonard Road | ME | 158325.6875 | 206125.6 | -47799.9125 | -23.19% | 438381.6 | -280055.9125 | -63.88% | 1. Inverter 2 was offline from 10:15 on 05/30, and Inverter 3 was offline from 13:30 on 05/30 due to 'Waiting for Grid Voltage.' Inverter 2 came back online at 13:00 on 06/20, but Inverter 3 has remained offline since then. | 1. SR102971, SR102367, SR102061 | SR102367 | SR102061
Topsham - Solarize LLC | ME | 157022.125 | 158551 | -1528.875 | -0.9643% | 158062 | -1039.875 | -0.6579% | 1. The site tripped offline at 06:00 on 06/17 and came back online at 10:30 on the same day. 2. Inverter 5 tripped offline at 12:15 on 06/24 due to 'Installation Failure - Grid Connection' and came back online at 07:30 on 06/25. | 1. SR103058 2. SR103397 | SR103397
Cherryfield - 727 North Main St (IRA) | ME | 444151.3125 | 480778.1 | -36626.7875 | -7.618% | 431765.9 | 12385.4125 | 2.869% | 1. The site tripped offline at 09:15 on 06/24 and came back online at 09:15 on 06/25. | 1. SR103383
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## Jul
ALIGNED |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 1805182.967 | 1776830.1 | 28352.867 | 1.596% | 2122246.2 | -317063.233 | -14.94% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 201197 | 191786.9 | 9410.1 | 4.907% | 224100 | -22903 | -10.22% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Loudon - 7046 Pleasant Street | NH | 205885.5 | 193269.9 | 12615.6 | 6.527% | 216609.6 | -10724.1 | -4.951%
Nashua - Pennichuck Water East | NH | 194384.592 | 210900.6 | -16516.008 | -7.831% | 151360 | 43024.592 | 28.43% | 1. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. | 1. SR099647
Nashua - Pennichuck Water West | NH | 148623 | 104898.5 | 43724.5 | 41.68% | 164800 | -16177 | -9.816% | 1.Site tripped offline at 20:20 on 07/25 and back online at 11:45 on 07/26 | 1.SR105084
Boothbay - Wiscasset Road | ME | 191341 | 211803.8 | -20462.8 | -9.661% | 235877 | -44536 | -18.88% | 1. Inverter 7 is experiencing multiple trippings since 07/15. 2. Inverter 4 tripped offline at 14:00 on 07/13 and back online at 08:30 on 07/21 3. Inverter 5 was offline from 10:00 on 06/11 is back online 09:30 on 07/07 | 1.SR104551 2.SR104369 3.SR102969 | SR104369 | SR102969
Thorndike - Leonard Road | ME | 220715.8125 | 191371.6 | 29344.2125 | 15.33% | 486810.4 | -266094.5875 | -54.66% | 1. Inverter 3 is back online at 09:45 on 07/02, while on site the site was taken offline from 08:30 to 09:30. On 07/07 EPC has taken site offline from 17:15 to 17:45 for site maintenance. 2.POA and BOM lost communications on 7/3/25. | 1.SR102971 2.SR107542 | SR107542
Topsham - Solarize LLC | ME | 161276.375 | 162785.6 | -1509.225 | -0.9271% | 163168 | -1891.625 | -1.159%
Cherryfield - 727 North Main St (IRA) | ME | 481759.6875 | 510013.2 | -28253.5125 | -5.54% | 479521.2 | 2238.4875 | 0.4668%
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## Aug
ALIGNED |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 1961593.9375 | 1910025.2 | 51568.7375 | 2.7% | 1944646.3 | 16947.6375 | 0.8715% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 210117.5 | 193427.2 | 16690.3 | 8.629% | 212600 | -2482.5 | -1.168%
Loudon - 7046 Pleasant Street | NH | 215115 | 204071.2 | 11043.8 | 5.412% | 204920 | 10195 | 4.975%
Nashua - Pennichuck Water East | NH | 209315.408 | 215567.7 | -6252.292 | -2.9% | 141456 | 67859.408 | 47.97% | 1. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading.
Nashua - Pennichuck Water West | NH | 163002.1545 | 116792.6 | 46209.5545 | 39.57% | 156000 | 7002.1545 | 4.489%
Boothbay - Wiscasset Road | ME | 232713 | 240320.3 | -7607.3 | -3.165% | 219824 | 12889 | 5.863%
Thorndike - Leonard Road | ME | 237568 | 215222.1 | 22345.9 | 10.38% | 445043.2 | -207475.2 | -46.62% | 1.Inverter 5 tripped offline at 14:45 on 08/12 and back online at 10:15 on 08/14. 2. Site was taken offline from 13:45 to 14:45 on 08/11 due to thermals of transformers. 3.POA and BOM lost communications on 7/3/25. | 1.SR106143 2.SR106009 3.SR107542 | SR106009 | SR107542
Topsham - Solarize LLC | ME | 179485.875 | 180255.7 | -769.825 | -0.4271% | 163234 | 16251.875 | 9.956%
Cherryfield - 727 North Main St (IRA) | ME | 514277 | 544368.4 | -30091.4 | -5.528% | 401569.1 | 112707.9 | 28.07% | 1. Site tripped offline at 16:26 on 08/14 and back online at 08:15 on 08/15 | 1.SR106311
ME: Bucksport - 258 Route 1 (IRA) | ME
ME: Union - Route 131 (IRA) | ME

## Sep
ALIGNED |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 2208773.664 | 2176038.568 | 32735.096 | 1.504% | 2369776.8 | -161003.136 | -6.794%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 181940.58 | 153803.5 | 28137.08 | 18.29% | 177300 | 4640.58 | 2.617% | 1. Site tripped offline at 11:00 on 09/17 and after resetting the breaker site is back online at 14:30 on 09/17. 2. Site tripped offline at 11:15 on 09/25 and after resetting the breaker site is back online at 14:45 on 09/25. and again triiped offline at 18:45 on 09/25 and back online at 08:15 on 09/26. | 1. SR108124 2. SR108542 | SR108542
Loudon - 7046 Pleasant Street | NH | 185757 | 177063 | 8694 | 4.91% | 171823.8 | 13933.2 | 8.109%
Nashua - Pennichuck Water East | NH | 143800.5 | 127513 | 16287.5 | 12.77% | 118728 | 25072.5 | 21.12% | 1. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. 2. Site tripped offline at 03:15 on 09/07 and back online at 16:00 on 09/09. | 1. SR107541 2. SR107568 | SR107568
Nashua - Pennichuck Water West | NH | 130021.084 | 100820.3 | 29200.784 | 28.96% | 130900 | -878.916 | -0.6714% | 1.Site tripped offline at 18:18 on 09/12 and later back online at 12:30 on 09/13 | 1.SR107916
Boothbay - Wiscasset Road | ME | 197924 | 200966.2 | -3042.2 | -1.514% | 186975 | 10949 | 5.856%
Thorndike - Leonard Road | ME | 199908 | 199498 | 410 | 0.2055% | 348557.9 | -148649.9 | -42.65% | 1.POA and BOM lost communications on 7/3/25. | 1.SR107542
Topsham - Solarize LLC | ME | 150082 | 150409.7 | -327.7 | -0.2179% | 140717 | 9365 | 6.655%
Cherryfield - 727 North Main St (IRA) | ME | 240825 | 268434.1 | -27609.1 | -10.29% | 343169.1 | -102344.1 | -29.82% | 1. Site was offline from 09:15 on 09/15 to 13:00 on 09/26 due to utility planned outage | 1.SR107957
ME: Bucksport - 258 Route 1 (IRA) | ME | 388976 | 407109.4 | -18133.4 | -4.454% | 393074.5 | -4098.5 | -1.043%
ME: Union - Route 131 (IRA) | ME | 389539.5 | 390421.368 | -881.868 | -0.2259% | 358531.5 | 31008 | 8.649% | 1. Site tripped offline at 18:00 on 09/06 and back online at 12:30 on 09/07. 2. Site tripped offline at 12:45 on 09/18 and back online at 08:00 on 09/19. | 1. SR107565 2. SR108245

## Oct
ALIGNED |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 1818455.1813 | 1637164.99 | 181290.1913 | 11.07% | 1677149.2 | 141305.9813 | 8.425%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Conway -US 302 and Stirch Road | NH | 144882.42 | 112577 | 32305.42 | 28.7% | 147500 | -2617.58 | -1.775% | 1. The site went offline at 08:45 on 10/24 and came back online at 16:30 on 10/24. It went offline again at 07:45 on 10/25 and came back online at 07:45 on 10/26. 2.Weather station(GHI) is reporting erronous values on high irradiance days. | 1. SR109964, SR109979 | 1. Closed | SR109979
Loudon - 7046 Pleasant Street | NH | 155678.5 | 151566.5 | 4112 | 2.713% | 141212.7 | 14465.8 | 10.24% | 1. The site went offline at 02:30 on 10/31 and came back online at 08:15 on 11/01. | 1. SR110392 | 1. Closed
Nashua - Pennichuck Water East | NH | 142557 | 107816.6 | 34740.4 | 32.22% | 89568 | 52989 | 59.16% | 1. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. 2. Site tripped offline at 11:45 on 10/07 and back online at 15:15 on 10/07. 3. Inverter 3 was offline at 11:45 on 10/07 and back online at 07:00 on 10/08. 4. Inverter 5 is tripped offline at 13:15 on 10/22 and reporting "Inverter Over Current - ProtectOO30" and back online at 07:00 on 10/23. 5. Site tripped offline at 09:30 on 10/29 and back online at 14:40 on 10/29. | 1. SR107541 2. SR109149 3. SR109162 4. SR109853 5. SR107568 | 1. Pending 2. Closed 3. Closed 4. Pending 5. Pending | SR109149 | SR109162 | SR109853 | SR107568
Nashua - Pennichuck Water West | NH | 111510.7613 | 84581.88 | 26928.8813 | 31.84% | 107600 | 3910.7613 | 3.635% | 1. Site tripped offline at 11:45 on 10/07 and back online at 15:15 on 10/07. 2. The meter and weather stations (GHI and ALB) stopped communicating at 08:15 on 10/27. The meter came back online at 17:00 on 10/28. The GHI weather station came back online at 11:00 on 10/31, but the ALB weather station still requires further troubleshooting and is currently under RMA. | 1. SR109150 2. SR110034 | 1. Closed 2. Pending | SR110034
Boothbay - Wiscasset Road | ME | 153950 | 161523 | -7573 | -4.688% | 139990 | 13960 | 9.972%
Thorndike - Leonard Road | ME | 151184 | 35846.21 | 115337.79 | 321.8% | 136674.2 | 14509.8 | 10.62% | 1.POA and BOM lost communications on 7/3/25. | 1. SR107542 | 1. Pending
Topsham - Solarize LLC | ME | 118666 | 121926.9 | -3260.9 | -2.674% | 108363 | 10303 | 9.508% | 1. The site went offline at 20:45 on 10/23 due to the breaker being in an open state. After the technician closed the breaker, the site came back online at 15:45 on 10/24. | 1. SR109959 | 1. Closed
Cherryfield - 727 North Main St (IRA) | ME | 234811 | 240158.3 | -5347.3 | -2.227% | 216719.1 | 18091.9 | 8.348%
ME: Bucksport - 258 Route 1 (IRA) | ME | 298261 | 316795.1 | -18534.1 | -5.851% | 313649.2 | -15388.2 | -4.906% | 1. Inverter 1 tripped offline at 10:45 on 10/10 and reporting Arc fault and back online at 07:00 on 10/11. | 1. SR108135 | 1. Closed
ME: Union - Route 131 (IRA) | ME | 306954.5 | 304373.5 | 2581 | 0.848% | 275873 | 31081.5 | 11.27% | 1. The site went offline at 07:30 on 10/18 due to the recloser being in an open state. After the technician closed the relay, the site came back online at 11:45 on 10/18. | 1. SR109657 | 1. Closed

## Nov
ALIGNED |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 1118205.9785 | 1056266.98 | 61938.9985 | 5.864% | 1195505.4 | -77299.4215 | -6.466%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Conway -US 302 and Stirch Road | NH | 73130.5 | 60397.32 | 12733.18 | 21.08% | 108300 | -35169.5 | -32.47% | 1.Site tripped offline from 09:30 to 14:30 on 11/04 2.Site tripped offline at 20:30 on 11/07 and later back online at 11:45 on 11/08 3.Site offline from 07:45 to 11:15 on 11/19 4.Site tripped offline at 09:15 on 11/28 and back online at 08:30 on 11/29 Weather station(GHI) is reporting erronous values on high irradiance days. | 1.SR110599 2.SR110802 3.SR111312 4.SR111816 | 1.Closed 2.Closed 3.Closed 4.Closed | SR110802 | SR111312 | SR111816
Loudon - 7046 Pleasant Street | NH | 88401.0275 | 88469.77 | -68.7425 | -0.0777% | 102183.5 | -13782.4725 | -13.49% | 1. The site was offline at 02:30 on 10/31 and came back online at 08:15 on 11/01. 2.Inverter 1.8 is having evening shading | 1. SR110392 | 1. Closed
Nashua - Pennichuck Water East | NH | 82698.4897 | 56006.04 | 26692.4497 | 47.66% | 68416 | 14282.4897 | 20.88% | 1.Site tripped offline at 13:00 on 11/04 and later back online at 08:00 on 11/05 2.1.Site tripped offline at 10:30 on 11/28 and later back online at 13:30 on 11/29 3.Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading.GHI has not communicated since 10/15/24. | 1.SR110617 2.SR111815 3.SR107541 | 1. Closed 2.Closed 3.Pending | SR111815 | SR107541
Nashua - Pennichuck Water West | NH | 61727.7113 | 25548.15 | 36179.5612 | 141.6% | 78700 | -16972.2887 | -21.57% | 1.ALB pyranometer is being RMA'd, on 11/14 weather station has removed for RMA'd process 2.Site tripped offline at 13:00 on 11/04 and later back online at 08:00 on 11/05 3.Site tripped offline at 11:15 on 11/14 and later back online at 10:45 on 11/16 | 1.SR110034 2.SR110618 3.SR111164 | 1.Pending 2.Closed 3.Closed | SR110618 | SR111164
Boothbay - Wiscasset Road | ME | 90484 | 106830.5 | -16346.5 | -15.3% | 96312 | -5828 | -6.051% | 1.Inverters having morning and evening shading
Thorndike - Leonard Road | ME | 89550 | 58534.35 | 31015.65 | 52.99% | 111189.2 | -21639.2 | -19.46% | 1.POA and BOM started communicating from 08:15 on 11/13 2.Inverters having morning and evening shading | 1.SR107542 | 1. Closed
Topsham - Solarize LLC | ME | 77378 | 77246.55 | 131.45 | 0.1702% | 80744 | -3366 | -4.169%
Cherryfield - 727 North Main St (IRA) | ME | 158781 | 161641.6 | -2860.6 | -1.77% | 139781.8 | 18999.2 | 13.59%
ME: Bucksport - 258 Route 1 (IRA) | ME | 197940 | 217643 | -19703 | -9.053% | 221948.9 | -24008.9 | -10.82% | 1. Inverters have morning shading
ME: Union - Route 131 (IRA) | ME | 198115.25 | 203949.7 | -5834.45 | -2.861% | 187930 | 10185.25 | 5.42%

## Dec
ALIGNED |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 801114.5421 | 1025241.19 | -224126.6479 | -21.86% | 1548861.48 | -747746.9379 | -48.28%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Conway -US 302 and Stirch Road | NH | 49964.395 | 48287.61 | 1676.785 | 3.472% | 91900 | -41935.605 | -45.63% | 1.Site tripped at 18:45 on 12/01 and later back online at 07:45 on 12/02 and again tripped offline on 12/03 from 08:15 to 10:00 2.Site tripped offline at 16:45 on 12/04 and back online at 09:00 on 12/05 3.Site tripped offline at 08:45 on 12/29 and back online at 08:30 on 12/30 | 1.SR111885 2.SR112241 3.SR113714 | 1.Closed 2.Closed 3.Closed | SR112241 | SR113714
Loudon - 7046 Pleasant Street | NH | 64218.3481 | 94382.97 | -30164.6219 | -31.96% | 88110.48 | -23892.1319 | -27.12% | 1.Site tripped offline at 05:00 on 12/29 and back online at 11:00 on 12/30 | 1.SR113704 | 1.Closed
Nashua - Pennichuck Water East | NH | 80429.0103 | 42711 | 37718.0103 | 88.31% | 60936 | 19493.0103 | 31.99% | 1.Site tripped offline at 11:30 on 12/19 and back online at 10:30 on 12/20 2.Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading.GHI has not communicated since 10/15/24. | 1.SR113205 2. SR107541 | 1.Closed 2.Pending | SR107541
Nashua - Pennichuck Water West | NH | 61358.7887 | 0 | 61358.7887 |  | 67300 | -5941.2113 | -8.828% | 1.ALB pyranometer is being RMA'd, on 11/14 weather station has removed for RMA'd process 2.Site tripped offline at 11:30 on 12/19 and back online at 11:15 on 12/20 | 1.SR110034 2.SR113207 | 1.Pending 2.Closed | SR113207
Boothbay - Wiscasset Road | ME | 59762 | 97565.45 | -37803.45 | -38.75% | 67816 | -8054 | -11.88% | 1. Site was barely producing from 12/02, 12/06, 12/14, 12/16 12/24 to 12/29
Thorndike - Leonard Road | ME | 54039 | 104499.2 | -50460.2 | -48.29% | 100187.8 | -46148.8 | -46.06% | 1. Site was barely producing from 12/02, 12/06, 12/14, 12/16 12/24 to 12/29
Topsham - Solarize LLC | ME | 51162 | 73606.16 | -22444.16 | -30.49% | 622249 | -571087 | -91.78% | 1. Site was offline from 06:00 on 12/20 to 11:00 on 12/21. 2. Site was offline from 01:30 on 12/24 to 09:30 on 12/26. | 1. SR113321 2. SR113570 | 1. Closed 2. closed | SR113570
Cherryfield - 727 North Main St (IRA) | ME | 106187 | 146376.6 | -40189.6 | -27.46% | 110291.7 | -4104.7 | -3.722% | 1. Site was offline from 15:55 on 12/19 to 07:00 on 12/21. | 1. SR113263 | 1. Closed
ME: Bucksport - 258 Route 1 (IRA) | ME | 122388 | 210618.2 | -88230.2 | -41.89% | 222247.5 | -99859.5 | -44.93% | 1. Site was offline from 09:55 to 10:16 on 12/31. 2. Site production was low from 12/02 to 12/04, 12/24 to 12/28. | 1. SR113896 | 1. Closed
ME: Union - Route 131 (IRA) | ME | 151606 | 207194 | -55588 | -26.83% | 117823 | 33783 | 28.67% | 1. Site production was low from 12/02 to 12/04, 12/19, 12/24 to 12/28.

## Sites
Portfolio: | ALIGNED
Site DAS Name | Site | State | Update | DAS
Conway - Lake | Conway -US 302 and Stirch Road | NH | AEF | PowerTrack
Loudon Pleasant Street Solar GSSG | Loudon - 7046 Pleasant Street | NH | AEF | PowerTrack
Pennichuck Water East GSSG | Nashua - Pennichuck Water East | NH | AEF | PowerTrack
Pennichuck Water West GSSG | Nashua - Pennichuck Water West | NH | AEF | PowerTrack
Boothbay Solar | Boothbay - Wiscasset Road | ME |  | PowerTrack
Thorndike Solar | Thorndike - Leonard Road | ME |  | PowerTrack
Topsham Solar | Topsham - Solarize LLC | ME |  | PowerTrack
Cherryfield | Cherryfield - 727 North Main St (IRA) | ME |  | PowerTrack
Bucksport Solar 1, LLC | ME: Bucksport - 258 Route 1 (IRA) | ME |  | PowerTrack
Union ME 1, LLC | ME: Union - Route 131 (IRA) | ME |  | PowerTrack