## Glossary
Terminology | Definition
Total Actual Production (kWh): | total monthly production
Total Modeled Production (kWh): | total performance predicted monthly produciton
Total Actual Insolation (Wh/m2): | total monthly insolation received on site
Total Modeled Insolation (Wh/m2): | total predicted monthly insolation on site
Total Outage Adjusted Production (kWh): | expected energy production based off plant configuration specifications and measured environmental data. Calculated using actual weather data collected on the site throughout the month. A more accurate and refined version of the Weather-Adjusted Performance metric.
Outage-Adjusted Performance: | the actual production divided by the outage adjusted expected production for a PV system.
Weather-Adjusted Performance: | total actual production versus the weather-adjusted expected production
Actual vs Modeled Production: | total actual production versus the adjusted modeled production
Monthly PV System Availability: | calculates the percentage in which equipment is online and producing when irradiance exceeds a predetermined threshold.
YTD PV System Availability: | system availability since the beginning of the year to present time

## Merrimack
Merrimack
Monthly Operating Report
December' 2024
Monthly Total Performance
| Total Actual Production (kWh): |  |  |  |  | 152046.499
| Total Modeled Production (kWh): |  |  |  |  | 140863.4
| Total Actual Insolation (Wh/m2): |  |  |  |  | 81276.413
Total Modeled Insolation (Wh/m2):
| Total Outage Adjusted Production (kWh): |  |  |  |  | 186514
| Outage-Adjusted Performance: |  |  |  |  | 81.52%
| Actual vs Modeled Production: |  |  |  |  | 107.9%
| Monthly PV System Availability: |  |  |  |  | 100%
| YTD PV System Availability: |  |  |  |  | 99.89%
Chart of Daily Irradiance vs. Production
Day-by-Day Performance
|  | Date | Energy Produced (kWh) | Radiation Yield (Wh/m2) | Max Ambient Temp (°F)
|  | 2024-12-01 | 6506.543 | 3213.25 | 27.6081 |  | Note: The production meter has been reporting erroneous values overnight throughout the entire month. We reached out to AlsoEnergy( #529959 )and manually corrected the data by considering 6:00 AM to 7:00 PM as the production hours.
|  | 2024-12-02 | 8099.748 | 3828.998 | 24.8684
|  | 2024-12-03 | 7382.251 | 3706.271 | 28.4045
|  | 2024-12-04 | 8042.745 | 3817.13 | 30.4215
|  | 2024-12-05 | 204.25 | 901.6889 | 34.4163
|  | 2024-12-06 | 4188.748 | 4493.291 | 25.8844
|  | 2024-12-07 | 6251.751 | 3079.536 | 28.7517
|  | 2024-12-08 | 2377.893 | 1277.365 | 37.3895
|  | 2024-12-09 | 3463.497 | 1486.626 | 37.2342
|  | 2024-12-10 | 571.498 | 254.1411 | 31.7644
|  | 2024-12-11 | 450.501 | 190.9074 | 39.4004
|  | 2024-12-12 | 3973.755 | 1994.831 | 35.2686
|  | 2024-12-13 | 8628.249 | 4482.461 | 24.3754
|  | 2024-12-14 | 8565.254 | 4480.635 | 19.5736
|  | 2024-12-15 | 6326.15 | 3173.531 | 20.9271
|  | 2024-12-16 | 1708.808 | 686.3829 | 32.2912
|  | 2024-12-17 | 7486.051 | 3810.865 | 43.2968
|  | 2024-12-18 | 6870.417 | 3491.174 | 37.536
|  | 2024-12-19 | 3838.001 | 1997.601 | 34.5679
|  | 2024-12-20 | 785.394 | 346.9011 | 28.0209
|  | 2024-12-21 | 3439.415 | 2606.717 | 22.4953
|  | 2024-12-22 | 8887.747 | 4528.068 | 11.5708
|  | 2024-12-23 | 6658.5 | 3194.55 | 14.8393
|  | 2024-12-24 | 2748.146 | 2100.002 | 26.7857
|  | 2024-12-25 | 8454.497 | 4419.55 | 22.1653
|  | 2024-12-26 | 8323.749 | 4389.904 | 24.2644
|  | 2024-12-27 | 4560.249 | 2462.137 | 20.2451
|  | 2024-12-28 | 1571.65 | 639.6005 | 33.5483
|  | 2024-12-29 | 1221.397 | 498.9911 | 38.0749
|  | 2024-12-30 | 3208.644 | 1794.164 | 46.0209
|  | 2024-12-31 | 7251.001 | 3929.143 | 36.3154
O&M Activity
Performance Notes

## Smithfield
Smithfield
Monthly Operating Report
December' 2024
Monthly Total Performance
| Total Actual Production (kWh): |  |  |  |  | 150308
| Total Modeled Production (kWh): |  |  |  |  | 160442.8
| Total Actual Insolation (Wh/m2): |  |  |  |  | 65797.2784
Total Modeled Insolation (Wh/m2):
| Total Outage Adjusted Production (kWh): |  |  |  |  | 200509
| Outage-Adjusted Performance: |  |  |  |  | 74.96%
| Actual vs Modeled Production: |  |  |  |  | 93.68%
| Monthly PV System Availability: |  |  |  |  | 99.75%
| YTD PV System Availability: |  |  |  |  | 99.88%
Chart of Daily Irradiance vs. Production
Day-by-Day Performance
|  | Date | Energy Produced (kWh) | Radiation Yield (Wh/m2) | Max Ambient Temp (°F)
|  | 2024-12-01 | 8733.5 | 2830.849 | 24.8693
|  | 2024-12-02 | 10763.25 | 3513.32 | 24.2782
|  | 2024-12-03 | 9895.75 | 3199.607 | 25.3957
|  | 2024-12-04 | 9294.25 | 2953.926 | 31.3553
|  | 2024-12-05 | 165.5 | 747.7726 | 34.0075
|  | 2024-12-06 | 1132.25 | 2441.962 | 26.6992
|  | 2024-12-07 | 3886 | 3217.046 | 27.6091
|  | 2024-12-08 | 6073.25 | 1935.821 | 39.089
|  | 2024-12-09 | 5148.5 | 1553.15 | 37.798
|  | 2024-12-10 | 1434.25 | 403.1621 | 35.1694
|  | 2024-12-11 | 553 | 167.7668 | 49.3889
|  | 2024-12-12 | 8519 | 2839.15 | 34.3281
|  | 2024-12-13 | 1457 | 678.9088 | 20.9307
|  | 2024-12-14 | 10345.75 | 3448.271 | 19.9097
|  | 2024-12-15 | 7604.75 | 2384.478 | 23.4357
|  | 2024-12-16 | 1969 | 557.0768 | 37.1091
|  | 2024-12-17 | 7696.75 | 2609.588 | 50.0373
|  | 2024-12-18 | 9256.25 | 3130.971 | 39.8254
|  | 2024-12-19 | 8711.5 | 2846.625 | 36.1617
|  | 2024-12-20 | 857 | 324.7541 | 28.5863
|  | 2024-12-21 | 290.75 | 1663.866 | 22.7388
|  | 2024-12-22 | 647.5 | 3470.585 | 11.1183
|  | 2024-12-23 | 774 | 3374.053 | 13.9882
|  | 2024-12-24 | 195 | 631.2435 | 25.4374
|  | 2024-12-25 | 1609.75 | 3143.121 | 25.3586
|  | 2024-12-26 | 6435.5 | 2957.19 | 27.5998
|  | 2024-12-27 | 9764.5 | 3255.681 | 26.0531
|  | 2024-12-28 | 1838.5 | 522.1493 | 39.9915
|  | 2024-12-29 | 2231.75 | 645.7404 | 49.2897
|  | 2024-12-30 | 3283.75 | 1102.608 | 50.4722
|  | 2024-12-31 | 9740.5 | 3246.836 | 40.3747
O&M Activity
Performance Notes

## Westlake
Westlake
Monthly Operating Report
December 2024
Monthly Total Performance
| Total Actual Production (kWh): |  |  |  |  | 261187
| Total Modeled Production (kWh): |  |  |  |  | 357864
| Total Actual Insolation (Wh/m2): |  |  |  |  | 91366.6933
Total Modeled Insolation (Wh/m2):
| Total Outage Adjusted Production (kWh): |  |  |  |  | 250803
| Outage-Adjusted Performance: |  |  |  |  | 104.1%
| Actual vs Modeled Production: |  |  |  |  | 72.98%
| Monthly PV System Availability: |  |  |  |  | 100%
| YTD PV System Availability: |  |  |  |  | 99.65%
Chart of Daily Irradiance vs. Production
Day-by-Day Performance
|  | Date | Energy Produced (kWh) | Radiation Yield (Wh/m2) | Max Ambient Temp (°F)
|  | 2024-12-01 | 14142 | 4921.646 | 44.1822
|  | 2024-12-02 | 13741 | 4783.983 | 45.1258
|  | 2024-12-03 | 13411 | 4559.376 | 46.5925
|  | 2024-12-04 | 2321 | 410.1544 | 53.0218
|  | 2024-12-05 | 10628 | 3522.59 | 48.7254
|  | 2024-12-06 | 11807 | 3798.253 | 41.938
|  | 2024-12-07 | 1737 | 317.8748 | 45.416
|  | 2024-12-08 | 5098 | 1654.919 | 49.9067
|  | 2024-12-09 | 12353 | 4337.437 | 55.1873
|  | 2024-12-10 | 7304 | 2371.917 | 43.8934
|  | 2024-12-11 | 13000 | 4926.656 | 44.9634
|  | 2024-12-12 | 9849 | 3500.128 | 50.6765
|  | 2024-12-13 | 1767 | 376.6848 | 55.3529
|  | 2024-12-14 | 11629 | 4477.676 | 59.3478
|  | 2024-12-15 | 3435 | 1107.828 | 61.4808
|  | 2024-12-16 | 4108 | 1266.491 | 67.3129
|  | 2024-12-17 | 7703 | 2684.861 | 62.7314
|  | 2024-12-18 | 12549 | 4721.264 | 51.928
|  | 2024-12-19 | 12330 | 4559.473 | 44.7987
|  | 2024-12-20 | 12797 | 4820.771 | 44.4171
|  | 2024-12-21 | 12389 | 4531.163 | 41.9344
|  | 2024-12-22 | 8509 | 2947.14 | 51.1155
|  | 2024-12-23 | 3148 | 903.3281 | 60.7881
|  | 2024-12-24 | 878 | 65.8292 | 58.999
|  | 2024-12-25 | 1471 | 215.2034 | 53.0172
|  | 2024-12-26 | 1698 | 352.7296 | 54.8755
|  | 2024-12-27 | 11133 | 4141.424 | 56.5495
|  | 2024-12-28 | 3739 | 1152.611 | 58.3832
|  | 2024-12-29 | 10983 | 4160.739 | 56.8976
|  | 2024-12-30 | 12581 | 4875.921 | 59.871
|  | 2024-12-31 | 12949 | 4900.622 | 47.4572
O&M Activity
Performance Notes

## Availability
2020 YTD Availability |  |  |  | 2022 YTD Availability
| Smithfield | Merrimack |  |  | Smithfield | Merrimack
January |  |  |  | January | 99.9% | 99.68%
February |  |  |  | February | 99.98% | 96.02%
March |  |  |  | March | 99.83% | 99.97%
April |  |  |  | April | 100% | 100%
May |  |  |  | May | 100% | 100%
June |  |  |  | June | 100% | 99.91%
July | 98.02% | 100% |  | July | 100% | 100%
August | 98.09% | 100% |  | August | 99.8% | 100%
September | 97.18% | 100% |  | September | 100% | 97.93%
October | 99.82% | 99.46% |  | October | 100% | 100%
November | 100% | 100% |  | November | 100% | 98.5%
December | 100% | 99.82% |  | December | 98.17% | 100%
YTD Average | 98.85% | 99.88% |  | YTD Average | 99.81% | 99.33%
2021 YTD Availability |  |  |  | 2023 YTD Availability |  |  | 2023 YTD Availability
| Smithfield | Merrimack |  |  | Smithfield | Merrimack |  | Westlake
January | 100% | 100% |  | January | 100% | 99.86% | January | 96.47%
February | 100% | 99.87% |  | February | 100% | 99.96% | February | 82.14%
March | 100% | 100% |  | March | 100% | 100% | March | 100%
April | 100% | 100% |  | April | 100% | 100% | April | 100%
May | 99.95% | 99.92% |  | May | 100% | 100% | May | 100%
June | 100% | 100% |  | June | 100% | 88.14% | June | 100%
July | 100% | 100% |  | July | 99.54% | 100% | July | 100%
August | 100% | 99.94% |  | August | 100% | 100% | August | 98%
September | 100% | 100% |  | September | 100% | 100% | September | 100%
October | 100% | 99.97% |  | October | 99.95% | 100% | October | 100%
November | 100% | 99.95% |  | November | 100% | 99.8%% | November | 96%
December | 100% | 100% |  | December | 100% | 100% | December | 100%
YTD Average | 100% | 99.97% |  | YTD Average | 99.96% | 98.91% | YTD Average | 97.72%
2024 YTD Availability
| Smithfield | Merrimack | Westlake
January | 100% | 98.66% | 100%
February | 99.97% | 100% | 99.81%
March | 100% | 100% | 99.75%
April | 100% | 100% | 100%
May | 100% | 100% | 100%
June | 100% | 100% | 100%
July | 100% | 100% | 100%
August | 98.78% | 100% | 100%
September | 100% | 100% | 100%
October | 100% | 100% | 97.19%
November | 100% | 100% | 99.11%
December | 99.75% | 100% | 100%
YTD Average | 99.88% | 99.89% | 99.65%

## Plant Health
2020 Plant Health Data
| Smithfield |  |  | Merrimack |  |  | Portfolio
| Actual | Adjusted | % | Actual | Adjusted | % | Actual | Adjusted | %
January | - | - | - | - | - | - | - | - | -
February | - | - | - | - | - | - | - | - | -
March | - | - | - | - | - | - | - | - | -
April | - | - | - | - | - | - | - | - | -
May | - | - | - | - | - | - | - | - | -
June | - | - | - | - | - | - | - | - | -
July | 116911.2 | 261526.7 | 44.7% | 424573 | 269641.8 | 157.5% | 541484.2 | 531168.5 | 101.9%
August | 140722.4 | 498528.6 | 28.23% | 438642 | 0.001 | - | 579364.4 | 498528.601 | 116.2%
September | 110264.4 | 425599.2 | 25.91% | 381452 | 0.001 | - | 491716.4 | 425599.201 | 115.5%
October | 56659.41 | 143112.1 | 39.59% | 252863 | 213893.1 | 118.2% | 309522.41 | 357005.2 | 86.7%
November | 240103.9 | 256321.4 | 93.67% | 201336 | 218336.2 | 92.21% | 441439.9 | 474657.6 | 93%
December | 156599.8 | 200907.8 | 77.95% | 112849 | 155562.4 | 72.54% | 269448.8 | 356470.2 | 75.59%
Annual | 821261.11 | 1785995.8 | 45.98% | 1811715 | 857433.502 | 211.3% | 2632976.11 | 2643429.302 | 99.6%
2021 Plant Health Data
| Smithfield |  |  | Merrimack |  |  | Portfolio
| Actual | Adjusted | % | Actual | Adjusted | % | Actual | Adjusted | %
January | 227679.5 | 257471.3 | 88.43% | 183752 | 225537.8 | 81.47% | 411431.5 | 483009.1 | 85.18%
February | 143871.8 | 255271 | 56.36% | 126222 | 205320.8 | 61.48% | 270093.8 | 460591.8 | 58.64%
March | 492310.9 | 494013.2 | 99.66% | 437625 | 445515.7 | 98.23% | 929935.9 | 939528.9 | 98.98%
April | 439047 | 448567.2 | 97.88% | 367530 | 372152.7 | 98.76% | 806577 | 820719.9 | 98.28%
May | 501618.9 | 514260.1 | 97.54% | 436580 | 440019.8 | 99.22% | 938198.9 | 954279.9 | 98.31%
June | 543264.6 | 552014.8 | 98.41% | 459791 | 460611.1 | 99.82% | 1003055.6 | 1012625.9 | 99.05%
July | 420906.1 | 429467.7 | 98.01% | 350714 | 355421.8 | 98.68% | 771620.1 | 784889.5 | 98.31%
August | 441017.5 | 449526.7 | 98.11% | 367845 | 379397.1 | 96.96% | 808862.5 | 828923.8 | 97.58%
September | 385420.2 | 394461.6 | 97.71% | 326443 | 350030.6 | 93.26% | 711863.2 | 744492.2 | 95.62%
October | 305337.1 | 312573.2 | 97.68% | 249653 | 271991.8 | 91.79% | 554990.1 | 584565 | 94.94%
November | 303576.1 | 303145.1 | 100.1% | 251687.7 | 281496.9 | 89.41% | 555263.8 | 584642 | 94.98%
December | 161260.8 | 178274.2 | 90.46% | 126900.7 | 166144.7 | 76.38% | 288161.5 | 344418.9 | 83.67%
Annual | 4365310.5 | 4589046.1 | 95.12% | 3684743.4 | 3953640.8 | 93.2% | 8050053.9 | 8542686.9 | 94.23%
2022 Plant Health Data
| Smithfield |  |  | Merrimack |  |  | Portfolio
| Actual | Adjusted | % | Actual | Adjusted | % | Actual | Adjusted | %
January | 202947.9 | 251246.2 | 80.78% | 186214.4 | 234624.4 | 79.37% | 389162.3 | 485870.6 | 80.1%
February | 200639.6 | 292574.9 | 68.58% | 188160.6 | 272070.1 | 69.16% | 388800.2 | 564645 | 68.86%
March | 402985 | 413695.1 | 97.41% | 340534.4 | 359950.5 | 94.61% | 743519.4 | 773645.6 | 96.11%
April | 481629 | 485708.5 | 99.16% | 376650 | 377357.3 | 99.81% | 858279 | 863065.8 | 99.45%
May | 518502.9 | 533788.3 | 97.14% | 478677.5 | 472852.1 | 101.2% | 997180.4 | 1006640.4 | 99.06%
June | 513473.5 | 535108 | 95.96% | 440374.3 | 446764.9 | 98.57% | 953847.8 | 981872.9 | 97.15%
July | 580554.4 | 593414.8 | 97.83% | 489301.6 | 492918 | 99.27% | 1069856 | 1086332.8 | 98.48%
August | 503219 | 515233 | 97.67% | 438861 | 443561 | 98.9% | 942080 | 958794 | 98.3%
September | 409308 | 411175 | 100% | 340575 | 323126 | 105% | 749883 | 734301 | 102%
October | 334449.6113 | 336304.364 | 99.45% | 271839.6377 | 311452.858 | 87.28% | 606289.249 | 647757.222 | 93.6%
November | 276297.74 | 290335.56 | 95.16% | 218105.76 | 262568 | 83.07% | 494403.5 | 552903.56 | 89.42%
December | 183609 | 230716 | 79.58% | 157162 | 215864 | 72.81% | 340771 | 446580 | 76.31%
Annual | 4607615.6513 | 4889299.724 | 94.24% | 3926456.1977 | 4213109.158 | 93.2% | 8534071.849 | 4889299.724 | 174.5%
2023 Plant Health Data
| Smithfield |  |  | Merrimack |  |  | Westlake |  |  | Portfolio
| Actual | Adjusted | % | Actual | Adjusted | % | Actual | Adjusted | % | Actual | Adjusted | %
January | 142189 | 160873.491 | 88.39% | 103552 | 127331.577 | 81.32% | 74263.4208 | 82952 | 89.53% | 320004.4208 | 371157.068 | 86.22%
February | 266942 | 276241 | 96.63% | 180752 | 208700.522 | 86.61% | 221260.7657 | 227016 | 97.46% | 668954.7657 | 711957.522 | 93.96%
March | 409565 | 417304 | 98.15% | 308153 | 321220.88 | 95.93% | 286064.4375 | 346799 | 82.49% | 1003782.4375 | 1085323.88 | 92.49%
April | 430190 | 412086 | 104.4% | 328902 | 322311 | 102% | 339090.4375 | 392844 | 86.32% | 1098182.4375 | 1127241 | 97.42%
May | 612258 | 577875 | 105.9% | 471181 | 453222 | 104% | 511189 | 438062 | 116.7% | 1594628 | 1469159 | 108.5%
June | 444301 | 414597 | 107.2% | 324882 | 310497 | 104.6% | 600188 | 467714 | 128.3% | 1369371 | 1192808 | 114.8%
July | 498245 | 458945.995 | 108.6% | 367235.874 | 349396.213 | 105.1% | 652371 | 496657.508 | 131.4% | 1517851.874 | 1304999.716 | 116.3%
August | 436164 | 405408 | 107.6% | 352637 | 339249.26 | 103.9% | 667760 | 487676.83 | 136.9% | 1456561 | 1232334.09 | 118.2%
September | 370272.75 | 333333.368 | 111.1% | 287373.765 | 283946.673 | 101.2% | 489777.5 | 444764.081 | 110.1% | 1147424.015 | 1062044.122 | 108%
October | 332044 | 298236.435 | 111.3% | 240465.75 | 241283.6885 | 99.66% | 409184.25 | 385714.625 | 106.1% | 981694 | 925234.7485 | 106.1%
November | 269789.5 | 248912.23 | 108.4% | 205501 | 216124.568 | 95.08% | 290843 | 280653 | 103.6% | 766133.5 | 745689.798 | 102.7%
December | 177182.5 | 171320.8149 | 103.4% | 131479.25 | 147101.9315 | 89.38% | 304092.5 | 298353.0765 | 101.9% | 612754.25 | 616775.8229 | 99.35%
Annual | 4389142.75 | 4175133.3339 | 105.1% | 3302114.639 | 3320385.313 | 99.45% | 4846084.3115 | 4349206.1205 | 111.4% | 12537341.7005 | 11844724.7674 | 105.8%
2024 Plant Health Data
| Smithfield |  |  | Merrimack |  |  | Westlake |  |  | Portfolio
| Actual | Adjusted | % | Actual | Adjusted | % | Actual | Adjusted | % | Actual | Adjusted | %
January | 108163 | 172809.6428 | 62.59% | 86767.62 | 151534.5576 | 57.26% | 290245 | 287392.1013 | 101% | 485175.62 | 611736.3017 | 79.31%
February | 291709.5 | 299537 | 97.39% | 276717.49 | 278641 | 99.31% | 356261 | 335365 | 106.2% | 924687.99 | 913543 | 101.2%
March | 384849 | 349402 | 110.1% | 290874.485 | 290005 | 100.3% | 449834 | 418928 | 107.4% | 1125557.485 | 1058335 | 106.4%
April | 414025.5 | 375655.001 | 110.2% | 324347.375 | 310941.494 | 104.3% | 456273 | 424083.8012 | 107.6% | 1194645.875 | 1110680.2962 | 107.6%
May | 475700.7 | 439660 | 108.2% | 364333 | 345125 | 105.6% | 485088 | 456660.9 | 106.2% | 1325121.7 | 1241445.9 | 106.7%
June | 545003 | 507017 | 107.5% | 395194 | 373160 | 105.9% | 549490 | 571603 | 96.13% | 1489687 | 1451780 | 102.6%
July | 488518 | 449196.198 | 108.8% | 417508.625 | 397684.882 | 105% | 603952.5 | 574900.631 | 105.1% | 1509979.125 | 1421781.711 | 106.2%
August | 483924.5 | 443177.536 | 109.2% | 344011.75 | 331427.212 | 103.8% | 625539.5 | 592446.234 | 105.6% | 1453475.75 | 1367050.982 | 106.3%
September | 391241.75 | 349632.517 | 111.9% | 337959 | 331960.913 | 101.8% | 495010 | 465279.016 | 106.4% | 1224210.75 | 1146872.446 | 106.7%
October | 394041.25 | 349911.49 | 112.6% | 301213 | 303095 | 99.38% | 496884 | 462332.139 | 107.5% | 1192138.25 | 1115338.629 | 106.9%
November | 286999.5 | 263489.4845 | 108.9% | 220606 | 228078 | 96.72% | 330561 | 301310.374 | 109.7% | 838166.5 | 792877.8585 | 105.7%
December | 150308 | 200509 | 74.96% | 152046.499 | 186514 | 81.52% | 261187 | 250803 | 104.1% | 563541.499 | 637826 | 88.35%
Annual | 4414483.7 | 4199996.8693 | 105.1% | 3511578.844 | 3528167.0586 | 99.53% | 5400325 | 5141104.1965 | 105% | 13326387.544 | 12869268.1244 | 103.6%

## Predicted Data
Site Name | Month | Year | Total Modeled Production (kWh): | Total Modeled Insolation (Wh/m2):
Smithfield | 1 | 2024 | 173872.6
Smithfield | 2 | 2024 | 223465.4
Smithfield | 3 | 2024 | 344525.3
Smithfield | 4 | 2024 | 439674.5
Smithfield | 5 | 2024 | 455091.2
Smithfield | 6 | 2024 | 491177.6
Smithfield | 7 | 2024 | 524395
Smithfield | 8 | 2024 | 488163.4
Smithfield | 9 | 2024 | 412507.2
Smithfield | 10 | 2024 | 292225.1
Smithfield | 11 | 2024 | 204482.1
Smithfield | 12 | 2024 | 160442.8
Merrimack | 1 | 2024 | 148923.3
Merrimack | 2 | 2024 | 218895
Merrimack | 3 | 2024 | 315967.9
Merrimack | 4 | 2024 | 391436.4
Merrimack | 5 | 2024 | 412289
Merrimack | 6 | 2024 | 441106.2
Merrimack | 7 | 2024 | 465962.5
Merrimack | 8 | 2024 | 429405.9
Merrimack | 9 | 2024 | 359589.8
Merrimack | 10 | 2024 | 287672
Merrimack | 11 | 2024 | 186483.9
Merrimack | 12 | 2024 | 140863.4
Westlake | 1 | 2024 | 359065
Westlake | 2 | 2024 | 341764
Westlake | 3 | 2024 | 409489
Westlake | 4 | 2024 | 426854
Westlake | 5 | 2024 | 491560
Westlake | 6 | 2024 | 511081
Westlake | 7 | 2024 | 528500
Westlake | 8 | 2024 | 491649
Westlake | 9 | 2024 | 422985
Westlake | 10 | 2024 | 426835
Westlake | 11 | 2024 | 378158
Westlake | 12 | 2024 | 357864

## Ashley Config (hidden)
Field | E_Grid | GlobInc |  |  | Ashley kWh | [7 empty] | Ashley Insolation (Wh/m^2)
Units | kWh | Wh/m2 |  |  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2022
2015-01-01 | 430600 | 88900 |  | January | 430600 | 430600 | 428447 | 426304.765 | 424173.2412 | 422052.375 | 419942.1131 | 417842.4025 | 99200
2015-02-01 | 472000 | 99800 |  | February | 472000 | 472000 | 469640 | 467291.8 | 464955.341 | 462630.5643 | 460317.4115 | 458015.8244 | 108300
2015-03-01 | 637500 | 138300 | PIS Month | March | 637500 | 634312.5 | 631140.9375 | 627985.2328 | 624845.3066 | 621721.0801 | 618612.4747 | 615519.4123 | 150000
2015-04-01 | 719700 | 158700 |  | April | 719700 | 716101.5 | 712520.9925 | 708958.3875 | 705413.5956 | 701886.5276 | 698377.095 | 694885.2095 | 171200
2015-05-01 | 729800 | 162100 |  | May | 729800 | 726151 | 722520.245 | 718907.6438 | 715313.1056 | 711736.54 | 708177.8573 | 704636.968 | 174100
2015-06-01 | 764800 | 172600 |  | June | 764800 | 760976 | 757171.12 | 753385.2644 | 749618.3381 | 745870.2464 | 742140.8952 | 738430.1907 | 182400
2015-07-01 | 773600 | 175600 |  | July | 773600 | 769732 | 765883.34 | 762053.9233 | 758243.6537 | 754452.4354 | 750680.1732 | 746926.7724 | 185100
2015-08-01 | 753100 | 170100 |  | August | 753100 | 749334.5 | 745587.8275 | 741859.8884 | 738150.5889 | 734459.836 | 730787.5368 | 727133.5991 | 178400
2015-09-01 | 622300 | 138000 |  | September | 622300 | 619188.5 | 616092.5575 | 613012.0947 | 609947.0342 | 606897.2991 | 603862.8126 | 600843.4985 | 146600
2015-10-01 | 572800 | 124400 |  | October | 572800 | 569936 | 567086.32 | 564250.8884 | 561429.634 | 558622.4858 | 555829.3734 | 553050.2265 | 133800
2015-11-01 | 413200 | 88700 |  | November | 413200 | 411134 | 409078.33 | 407032.9384 | 404997.7737 | 402972.7848 | 400957.9209 | 398953.1313 | 96000
2015-12-01 | 420700 | 88000 |  | December | 420700 | 418596.5 | 416503.5175 | 414420.9999 | 412348.8949 | 410287.1504 | 408235.7147 | 406194.5361 | 98000
2016-01-01 | 430600 | 88900
2016-02-01 | 472000 | 99800
2016-03-01 | 634312.5 | 138300
2016-04-01 | 716101.5 | 158700
2016-05-01 | 726151 | 162100
2016-06-01 | 760976 | 172600
2016-07-01 | 769732 | 175600
2016-08-01 | 749334.5 | 170100
2016-09-01 | 619188.5 | 138000
2016-10-01 | 569936 | 124400
2016-11-01 | 411134 | 88700
2016-12-01 | 418596.5 | 88000
2017-01-01 | 428447 | 88900
2017-02-01 | 469640 | 99800
2017-03-01 | 631125 | 138300
2017-04-01 | 712503 | 158700
2017-05-01 | 722502 | 162100
2017-06-01 | 757152 | 172600
2017-07-01 | 765864 | 175600
2017-08-01 | 745569 | 170100
2017-09-01 | 616077 | 138000
2017-10-01 | 567072 | 124400
2017-11-01 | 409068 | 88700
2017-12-01 | 416493 | 88000
2018-01-01 | 426294 | 88900
2018-02-01 | 467280 | 99800
2018-03-01 | 627937.5 | 138300
2018-04-01 | 708904.5 | 158700
2018-05-01 | 718853 | 162100
2018-06-01 | 753328 | 172600
2018-07-01 | 761996 | 175600
2018-08-01 | 741803.5 | 170100
2018-09-01 | 612965.5 | 138000
2018-10-01 | 564208 | 124400
2018-11-01 | 407002 | 88700
2018-12-01 | 414389.5 | 88000
2019-01-01 | 424141 | 88900
2019-02-01 | 464920 | 99800
2019-03-01 | 624750 | 138300
2019-04-01 | 705306 | 158700
2019-05-01 | 715204 | 162100
2019-06-01 | 749504 | 172600
2019-07-01 | 758128 | 175600
2019-08-01 | 738038 | 170100
2019-09-01 | 609854 | 138000
2019-10-01 | 561344 | 124400
2019-11-01 | 404936 | 88700
2019-12-01 | 412286 | 88000
2020-01-01 | 421988 | 88900
2020-02-01 | 462560 | 99800
2020-03-01 | 627937.5 | 138300
2020-04-01 | 708904.5 | 158700
2020-05-01 | 718853 | 162100
2020-06-01 | 753328 | 172600
2020-07-01 | 761996 | 175600
2020-08-01 | 741803.5 | 170100
2020-09-01 | 612965.5 | 138000
2020-10-01 | 564208 | 124400
2020-11-01 | 407002 | 88700
2020-12-01 | 414389.5 | 88000
2021-01-01 | 421988 | 88900
2021-02-01 | 462560 | 99800
2021-03-01 | 624750 | 138300
2021-04-01 | 705306 | 158700
2021-05-01 | 715204 | 162100
2021-06-01 | 749504 | 172600
2021-07-01 | 758128 | 175600
2021-08-01 | 738038 | 170100
2021-09-01 | 609854 | 138000
2021-10-01 | 561344 | 124400
2021-11-01 | 404936 | 88700
2021-12-01 | 412286 | 88000
2022-01-01 | 417842.4025 | 99200
2022-02-01 | 458015.8244 | 108300
2022-03-01 | 615519.4123 | 150000
2022-04-01 | 694885.2095 | 171200
2022-05-01 | 704636.968 | 174100
2022-06-01 | 738430.1907 | 182400
2022-07-01 | 746926.7724 | 185100
2022-08-01 | 727133.5991 | 178400
2022-09-01 | 600843.4985 | 146600
2022-10-01 | 553050.2265 | 133800
2022-11-01 | 398953.1313 | 96000
2022-12-01 | 406194.5361 | 98000

## Lang Config (hidden)
Field | E_Grid | GlobInc |  |  | Lang kWh | [7 empty] | Lang Insolation (Wh/m^2)
Units | kWh | Wh/m2 |  |  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2022
2015-01-01 | 558000 | 89800 |  | January | 558000 | 558000 | 555210 | 552433.95 | 549671.7802 | 546923.4213 | 544188.8042 | 541467.8602 | 99500
2015-02-01 | 618000 | 100200 |  | February | 618000 | 618000 | 614910 | 611835.45 | 608776.2728 | 605732.3914 | 602703.7294 | 599690.2108 | 110300
2015-03-01 | 832000 | 140000 |  | March | 832000 | 832000 | 827840 | 823700.8 | 819582.296 | 815484.3845 | 811406.9626 | 807349.9278 | 152700
2015-04-01 | 960000 | 164500 |  | April | 960000 | 960000 | 955200 | 950424 | 945671.88 | 940943.5206 | 936238.803 | 931557.609 | 177600
2015-05-01 | 965000 | 166700 |  | May | 965000 | 965000 | 960175 | 955374.125 | 950597.2544 | 945844.2681 | 941115.0468 | 936409.4715 | 178000
2015-06-01 | 1010000 | 175600 |  | June | 1010000 | 1010000 | 1004950 | 999925.25 | 994925.6238 | 989950.9956 | 985001.2407 | 980076.2344 | 186200
2015-07-01 | 1006000 | 175400 |  | July | 1006000 | 1006000 | 1000970 | 995965.15 | 990985.3243 | 986030.3976 | 981100.2456 | 976194.7444 | 184400
2015-08-01 | 958000 | 166400 |  | August | 958000 | 958000 | 953210 | 948443.95 | 943701.7302 | 938983.2216 | 934288.3055 | 929616.864 | 176400
2015-09-01 | 804000 | 138400 |  | September | 804000 | 804000 | 799980 | 795980.1 | 792000.1995 | 788040.1985 | 784099.9975 | 780179.4975 | 147200
2015-10-01 | 772000 | 129600 | PIS date | October | 772000 | 768140 | 764299.3 | 760477.8035 | 756675.4145 | 752892.0374 | 749127.5772 | 745381.9393 | 139100
2015-11-01 | 546000 | 90200 |  | November | 546000 | 543270 | 540553.65 | 537850.8818 | 535161.6273 | 532485.8192 | 529823.3901 | 527174.2732 | 97900
2015-12-01 | 546000 | 88300 |  | December | 546000 | 543270 | 540553.65 | 537850.8818 | 535161.6273 | 532485.8192 | 529823.3901 | 527174.2732 | 97800
2016-01-01 | 558000 | 89800
2016-02-01 | 618000 | 100200
2016-03-01 | 832000 | 140000
2016-04-01 | 960000 | 164500
2016-05-01 | 965000 | 166700
2016-06-01 | 1010000 | 175600
2016-07-01 | 1006000 | 175400
2016-08-01 | 958000 | 166400
2016-09-01 | 804000 | 138400
2016-10-01 | 768140 | 129600
2016-11-01 | 543270 | 90200
2016-12-01 | 543270 | 88300
2017-01-01 | 555210 | 89800
2017-02-01 | 614910 | 100200
2017-03-01 | 827840 | 140000
2017-04-01 | 955200 | 164500
2017-05-01 | 960175 | 166700
2017-06-01 | 1004950 | 175600
2017-07-01 | 1000970 | 175400
2017-08-01 | 953210 | 166400
2017-09-01 | 799980 | 138400
2017-10-01 | 764280 | 129600
2017-11-01 | 540540 | 90200
2017-12-01 | 540540 | 88300
2018-01-01 | 552420 | 89800
2018-02-01 | 611820 | 100200
2018-03-01 | 823680 | 140000
2018-04-01 | 950400 | 164500
2018-05-01 | 955350 | 166700
2018-06-01 | 999900 | 175600
2018-07-01 | 995940 | 175400
2018-08-01 | 948420 | 166400
2018-09-01 | 795960 | 138400
2018-10-01 | 760420 | 129600
2018-11-01 | 537810 | 90200
2018-12-01 | 537810 | 88300
2019-01-01 | 549630 | 89800
2019-02-01 | 608730 | 100200
2019-03-01 | 819520 | 140000
2019-04-01 | 945600 | 164500
2019-05-01 | 950525 | 166700
2019-06-01 | 994850 | 175600
2019-07-01 | 990910 | 175400
2019-08-01 | 943630 | 166400
2019-09-01 | 791940 | 138400
2019-10-01 | 756560 | 129600
2019-11-01 | 535080 | 90200
2019-12-01 | 535080 | 88300
2020-01-01 | 546840 | 89800
2020-02-01 | 605640 | 100200
2020-03-01 | 815360 | 140000
2020-04-01 | 940800 | 164500
2020-05-01 | 945700 | 166700
2020-06-01 | 989800 | 175600
2020-07-01 | 985880 | 175400
2020-08-01 | 938840 | 166400
2020-09-01 | 787920 | 138400
2020-10-01 | 752700 | 129600
2020-11-01 | 532350 | 90200
2020-12-01 | 532350 | 88300
2021-01-01 | 544050 | 89800
2021-02-01 | 602550 | 100200
2021-03-01 | 811200 | 140000
2021-04-01 | 936000 | 164500
2021-05-01 | 940875 | 166700
2021-06-01 | 984750 | 175600
2021-07-01 | 980850 | 175400
2021-08-01 | 934050 | 166400
2021-09-01 | 783900 | 138400
2021-10-01 | 752700 | 129600
2021-11-01 | 532350 | 90200
2021-12-01 | 532350 | 88300
2022-01-01 | 541467.8602 | 99500
2022-02-01 | 599690.2108 | 110300
2022-03-01 | 807349.9278 | 152700
2022-04-01 | 931557.609 | 177600
2022-05-01 | 936409.4715 | 178000
2022-06-01 | 980076.2344 | 186200
2022-07-01 | 976194.7444 | 184400
2022-08-01 | 929616.864 | 176400
2022-09-01 | 780179.4975 | 147200
2022-10-01 | 745381.9393 | 139100
2022-11-01 | 527174.2732 | 97900
2022-12-01 | 527174.2732 | 97800

## Stikeleather Config (hidden)
Field | E_Grid | GlobInc |  |  | Stikeleather kWh | [7 empty] | Stikeleather Insolation (Wh/m^2)
Units | kWh | Wh/m2 |  |  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2022
2015-01-01 | 596000 | 95500 |  | January | 596000 | 596000 | 593020 | 590054.9 | 587104.6255 | 584169.1024 | 581248.2569 | 578342.0156 | 102800
2015-02-01 | 602000 | 98900 |  | February | 602000 | 602000 | 598990 | 595995.05 | 593015.0748 | 590049.9994 | 587099.7494 | 584164.2506 | 106600
2015-03-01 | 866000 | 144000 |  | March | 866000 | 866000 | 861670 | 857361.65 | 853074.8418 | 848809.4675 | 844565.4202 | 840342.5931 | 156000
2015-04-01 | 967000 | 164800 |  | April | 967000 | 967000 | 962165 | 957354.175 | 952567.4041 | 947804.5671 | 943065.5443 | 938350.2165 | 176800
2015-05-01 | 1006000 | 172700 |  | May | 1006000 | 1006000 | 1000970 | 995965.15 | 990985.3243 | 986030.3976 | 981100.2456 | 976194.7444 | 183300
2015-06-01 | 1031000 | 178800 |  | June | 1031000 | 1031000 | 1025845 | 1020715.775 | 1015612.1961 | 1010534.1351 | 1005481.4645 | 1000454.0571 | 188600
2015-07-01 | 1045000 | 182100 |  | July | 1045000 | 1045000 | 1039775 | 1034576.125 | 1029403.2444 | 1024256.2282 | 1019134.947 | 1014039.2723 | 189200
2015-08-01 | 967000 | 168000 |  | August | 967000 | 967000 | 962165 | 957354.175 | 952567.4041 | 947804.5671 | 943065.5443 | 938350.2165 | 175100
2015-09-01 | 845000 | 145300 | PIS DATE | September | 845000 | 840775 | 836571.125 | 832388.2694 | 828226.328 | 824085.1964 | 819964.7704 | 815864.9466 | 153100
2015-10-01 | 862000 | 144600 |  | October | 862000 | 857690 | 853401.55 | 849134.5423 | 844888.8695 | 840664.4252 | 836461.1031 | 832278.7975 | 153800
2015-11-01 | 629000 | 103400 |  | November | 629000 | 625855 | 622725.725 | 619612.0964 | 616514.0359 | 613431.4657 | 610364.3084 | 607312.4868 | 111400
2015-12-01 | 582000 | 94000 |  | December | 582000 | 579090 | 576194.55 | 573313.5773 | 570447.0094 | 567594.7743 | 564756.8004 | 561933.0164 | 103100
2016-01-01 | 596000 | 95500
2016-02-01 | 602000 | 98900
2016-03-01 | 866000 | 144000
2016-04-01 | 967000 | 164800
2016-05-01 | 1006000 | 172700
2016-06-01 | 1031000 | 178800
2016-07-01 | 1045000 | 182100
2016-08-01 | 967000 | 168000
2016-09-01 | 840775 | 145300
2016-10-01 | 857690 | 144600
2016-11-01 | 625855 | 103400
2016-12-01 | 579090 | 94000
2017-01-01 | 593020 | 95500
2017-02-01 | 598990 | 98900
2017-03-01 | 861670 | 144000
2017-04-01 | 962165 | 164800
2017-05-01 | 1000970 | 172700
2017-06-01 | 1025845 | 178800
2017-07-01 | 1039775 | 182100
2017-08-01 | 962165 | 168000
2017-09-01 | 836550 | 145300
2017-10-01 | 853380 | 144600
2017-11-01 | 622710 | 103400
2017-12-01 | 576180 | 94000
2018-01-01 | 590040 | 95500
2018-02-01 | 595980 | 98900
2018-03-01 | 857340 | 144000
2018-04-01 | 957330 | 164800
2018-05-01 | 995940 | 172700
2018-06-01 | 1020690 | 178800
2018-07-01 | 1034550 | 182100
2018-08-01 | 957330 | 168000
2018-09-01 | 832325 | 145300
2018-10-01 | 849070 | 144600
2018-11-01 | 619565 | 103400
2018-12-01 | 573270 | 94000
2019-01-01 | 587060 | 95500
2019-02-01 | 592970 | 98900
2019-03-01 | 853010 | 144000
2019-04-01 | 952495 | 164800
2019-05-01 | 990910 | 172700
2019-06-01 | 1015535 | 178800
2019-07-01 | 1029325 | 182100
2019-08-01 | 952495 | 168000
2019-09-01 | 828100 | 145300
2019-10-01 | 844760 | 144600
2019-11-01 | 616420 | 103400
2019-12-01 | 570360 | 94000
2020-01-01 | 584080 | 95500
2020-02-01 | 589960 | 98900
2020-03-01 | 848680 | 144000
2020-04-01 | 947660 | 164800
2020-05-01 | 985880 | 172700
2020-06-01 | 1010380 | 178800
2020-07-01 | 1024100 | 182100
2020-08-01 | 947660 | 168000
2020-09-01 | 823875 | 145300
2020-10-01 | 840450 | 144600
2020-11-01 | 613275 | 103400
2020-12-01 | 567450 | 94000
2021-01-01 | 581100 | 95500
2021-02-01 | 586950 | 98900
2021-03-01 | 844350 | 144000
2021-04-01 | 942825 | 164800
2021-05-01 | 980850 | 172700
2021-06-01 | 1005225 | 178800
2021-07-01 | 1018875 | 182100
2021-08-01 | 942825 | 168000
2021-09-01 | 823875 | 145300
2021-10-01 | 840450 | 144600
2021-11-01 | 613275 | 103400
2021-12-01 | 567450 | 94000
2022-01-01 | 578342.0156 | 102800
2022-02-01 | 584164.2506 | 106600
2022-03-01 | 840342.5931 | 156000
2022-04-01 | 938350.2165 | 176800
2022-05-01 | 976194.7444 | 183300
2022-06-01 | 1000454.0571 | 188600
2022-07-01 | 1014039.2723 | 189200
2022-08-01 | 938350.2165 | 175100
2022-09-01 | 815864.9466 | 153100
2022-10-01 | 832278.7975 | 153800
2022-11-01 | 607312.4868 | 111400
2022-12-01 | 561933.0164 | 103100

## Yadkin Config (hidden)
Field | E_Grid | GlobInc |  |  | Yadkin 601 kWh | [7 empty] | Yadkin 601 Insolation (Wh/m^2)
Units | kWh | Wh/m2 |  |  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2022
2015-01-01 | 349000 | 90100 |  | January | 349000 | 349000 | 347255 | 345518.725 | 343791.1314 | 342072.1757 | 340361.8148 | 338660.0058 | 99200
2015-02-01 | 379200 | 100800 |  | February | 379200 | 379200 | 377304 | 375417.48 | 373540.3926 | 371672.6906 | 369814.3272 | 367965.2555 | 108300
2015-03-01 | 508200 | 139500 |  | March | 508200 | 508200 | 505659 | 503130.705 | 500615.0515 | 498111.9762 | 495621.4163 | 493143.3093 | 150000
2015-04-01 | 571100 | 159800 |  | April | 571100 | 571100 | 568244.5 | 565403.2775 | 562576.2611 | 559763.3798 | 556964.5629 | 554179.7401 | 171200
2015-05-01 | 581500 | 163300 |  | May | 581500 | 581500 | 578592.5 | 575699.5375 | 572821.0398 | 569956.9346 | 567107.1499 | 564271.6142 | 174100
2015-06-01 | 613000 | 173900 |  | June | 613000 | 613000 | 609935 | 606885.325 | 603850.8984 | 600831.6439 | 597827.4857 | 594838.3482 | 182400
2015-07-01 | 621300 | 176800 |  | July | 621300 | 621300 | 618193.5 | 615102.5325 | 612027.0198 | 608966.8847 | 605922.0503 | 602892.4401 | 185100
2015-08-01 | 605900 | 171400 |  | August | 605900 | 605900 | 602870.5 | 599856.1475 | 596856.8668 | 593872.5824 | 590903.2195 | 587948.7034 | 178400
2015-09-01 | 500600 | 139100 | PIS Date | September | 500600 | 498097 | 495606.515 | 493128.4824 | 490662.84 | 488209.5258 | 485768.4782 | 483339.6358 | 146600
2015-10-01 | 460400 | 125500 |  | October | 460400 | 458098 | 455807.51 | 453528.4725 | 451260.8301 | 449004.5259 | 446759.5033 | 444525.7058 | 133800
2015-11-01 | 335300 | 89900 |  | November | 335300 | 333623.5 | 331955.3825 | 330295.6056 | 328644.1276 | 327000.9069 | 325365.9024 | 323739.0729 | 96000
2015-12-01 | 342700 | 89600 |  | December | 342700 | 340986.5 | 339281.5675 | 337585.1597 | 335897.2339 | 334217.7477 | 332546.659 | 330883.9257 | 98100
2016-01-01 | 349000 | 90100
2016-02-01 | 379200 | 100800
2016-03-01 | 508200 | 139500
2016-04-01 | 571100 | 159800
2016-05-01 | 581500 | 163300
2016-06-01 | 613000 | 173900
2016-07-01 | 621300 | 176800
2016-08-01 | 605900 | 171400
2016-09-01 | 498097 | 139100
2016-10-01 | 458098 | 125500
2016-11-01 | 333623.5 | 89900
2016-12-01 | 340986.5 | 89600
2017-01-01 | 347255 | 90100
2017-02-01 | 377304 | 100800
2017-03-01 | 505659 | 139500
2017-04-01 | 568244.5 | 159800
2017-05-01 | 578592.5 | 163300
2017-06-01 | 609935 | 173900
2017-07-01 | 618193.5 | 176800
2017-08-01 | 602870.5 | 171400
2017-09-01 | 495594 | 139100
2017-10-01 | 455796 | 125500
2017-11-01 | 331947 | 89900
2017-12-01 | 339273 | 89600
2018-01-01 | 345510 | 90100
2018-02-01 | 375408 | 100800
2018-03-01 | 503118 | 139500
2018-04-01 | 565389 | 159800
2018-05-01 | 575685 | 163300
2018-06-01 | 606870 | 173900
2018-07-01 | 615087 | 176800
2018-08-01 | 599841 | 171400
2018-09-01 | 493091 | 139100
2018-10-01 | 453494 | 125500
2018-11-01 | 330270.5 | 89900
2018-12-01 | 337559.5 | 89600
2019-01-01 | 343765 | 90100
2019-02-01 | 373512 | 100800
2019-03-01 | 500577 | 139500
2019-04-01 | 562533.5 | 159800
2019-05-01 | 572777.5 | 163300
2019-06-01 | 603805 | 173900
2019-07-01 | 611980.5 | 176800
2019-08-01 | 596811.5 | 171400
2019-09-01 | 490588 | 139100
2019-10-01 | 451192 | 125500
2019-11-01 | 328594 | 89900
2019-12-01 | 335846 | 89600
2020-01-01 | 342020 | 90100
2020-02-01 | 371616 | 100800
2020-03-01 | 498036 | 139500
2020-04-01 | 559678 | 159800
2020-05-01 | 569870 | 163300
2020-06-01 | 600740 | 173900
2020-07-01 | 608874 | 176800
2020-08-01 | 593782 | 171400
2020-09-01 | 488085 | 139100
2020-10-01 | 448890 | 125500
2020-11-01 | 326917.5 | 89900
2020-12-01 | 334132.5 | 89600
2021-01-01 | 340275 | 90100
2021-02-01 | 369720 | 100800
2021-03-01 | 495495 | 139500
2021-04-01 | 556822.5 | 159800
2021-05-01 | 566962.5 | 163300
2021-06-01 | 597675 | 173900
2021-07-01 | 605767.5 | 176800
2021-08-01 | 590752.5 | 171400
2021-09-01 | 488085 | 139100
2021-10-01 | 448890 | 125500
2021-11-01 | 326917.5 | 89900
2021-12-01 | 334132.5 | 89600
2022-01-01 | 338660.0058 | 99200
2022-02-01 | 367965.2555 | 108300
2022-03-01 | 493143.3093 | 150000
2022-04-01 | 554179.7401 | 171200
2022-05-01 | 564271.6142 | 174100
2022-06-01 | 594838.3482 | 182400
2022-07-01 | 602892.4401 | 185100
2022-08-01 | 587948.7034 | 178400
2022-09-01 | 483339.6358 | 146600
2022-10-01 | 444525.7058 | 133800
2022-11-01 | 323739.0729 | 96000
2022-12-01 | 330883.9257 | 98100