## Year to Date
Greenbacker Capital |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 42087608.3158 | 37232240.2559 | 4855368.0599 | 13.04% | 35755063.013 | 6332545.3028 | 17.71%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 163442.625 | 157448.325 | 5994.3 | 3.807% | 175542.883 | -12100.258 | -6.893%
15 Walpole Park South | MA | 596649 | 595502.4 | 1146.6 | 0.1925% | 609714.35 | -13065.35 | -2.143%
19 Walpole Park South | MA | 368900.125 | 362032.29 | 6867.835 | 1.897% | 390462.38 | -21562.255 | -5.522%
23 Walpole Park South | MA | 511125.25 | 473189.25 | 37936 | 8.017% | 511358.13 | -232.88 | -0.04554%
24 Walpole Park South | MA | 707462.75 | 619609.998 | 87852.752 | 14.18% | 786387.92 | -78925.17 | -10.04%
25 Walpole Park South | MA | 721706.5 | 716191.56 | 5514.94 | 0.77% | 797371.09 | -75664.59 | -9.489%
3 Walpole Park South | MA | 935370.8125 | 917610.02 | 17760.7925 | 1.936% | 950383.02 | -15012.2075 | -1.58%
4 Walpole Park South | MA | 519076.75 | 513308.75 | 5768 | 1.124% | 529439.37 | -10362.62 | -1.957%
Brockton | MA | 855813 | 777326.91 | 78486.09 | 10.1% | 883231.35 | -27418.35 | -3.104%
Canton | MA | 777426.75 | 754438.83 | 22987.92 | 3.047% | 857997.55 | -80570.8 | -9.391%
Chelsea | MA | 1434158 | 1430657.56 | 3500.44 | 0.2447% | 1408890.5 | 25267.5 | 1.793%
Hamilton Landfill | MA | 1155854.0705 | 1306341.713 | -150487.6425 | -11.52% | 0 | 1155854.0705
Holliston | MA | 2025332.5 | 2218077.97 | -192745.47 | -8.69% | 2291898.87 | -266566.37 | -11.63%
Natick HS - Carports | MA | 709096.7668 | 839629.9848 | -130533.218 | -15.55% | 0 | 709096.7668
Norton | MA | 673843 | 752643.907 | -78800.907 | -10.47% | 2483550 | -1809707 | -72.87%
Palmer - Boston Rd. | MA | 754331.0475 | 744761.11 | 9569.9375 | 1.285% | 799467 | -45135.9525 | -5.646%
Shirley Bartkus | MA | 1105873.9422 | 455610.283 | 650263.6592 | 142.7% | 1268969 | -163095.0578 | -12.85%
Stoughton | MA | 979808 | 594927.01 | 384880.99 | 64.69% | 958569.35 | 21238.65 | 2.216%
Wellfleet Landfill | MA | 1198467.774 | 1268071.369 | -69603.595 | -5.489% | 0 | 1198467.774
Wilmington Garage & Building 7 | MA | 1394371.24 | 1439477.7 | -45106.46 | -3.134% | 1458960.45 | -64589.21 | -4.427%
Woburn | MA | 2065290 | 2173939.17 | -108649.17 | -4.998% | 2095932.52 | -30642.52 | -1.462%
Friendship Solar 1 | MD | 4433246 | 4704206.2 | -270960.2 | -5.76% | 5071707.4 | -638461.4 | -12.59%
Friendship Solar 2 | MD | 4432407 | 4754341.5 | -321934.5 | -6.771% | 5022442.9 | -590035.9 | -11.75%
101 Carnegie Center | NJ | 1707641.22 | 2093500.97 | -385859.75 | -18.43% | 0 | 1707641.187
302 Carnegie Center | NJ | 750016.2905 | 824269.9071 | -74253.6166 | -9.008% | 0 | 750016.2905
510 Carnegie Center | NJ | 1884902.763 | 2241915.445 | -357012.682 | -15.92% | 0 | 1884902.763
701 Carnegie Center | NJ | 1486689.9275 | 1774433.694 | -287743.7665 | -16.22% | 72312.8 | 1414377.1275 | 1956%
Hudson County Correction | NJ | 2041105.5913 | 1728776.43 | 312329.1613 | 18.07% | 4227719.18 | -2186613.5887 | -51.72%
ER Bison Solar | PA | 2206040.5 | 0 | 2206040.5 |  | 2102755 | 103285.5 | 4.912%
Danville | IL | 3492159.12 | 0 | 3492159.12 |  | 0 | 2966076.106

## 1st Qtr
Greenbacker Capital |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 8106439.3749 | 7655316.204 | 451123.1709 | 5.893% | 6542628.072 | 1563811.3029 | 23.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 27279.1875 | 29350.804 | -2071.6165 | -7.058% | 31050.152 | -3770.9645 | -12.14%
15 Walpole Park South | MA | 100657.5 | 112350.87 | -11693.37 | -10.41% | 105870.23 | -5212.73 | -4.924%
19 Walpole Park South | MA | 60231 | 67805.21 | -7574.21 | -11.17% | 68109.16 | -7878.16 | -11.57%
23 Walpole Park South | MA | 84985.75 | 85604.47 | -618.72 | -0.7228% | 88577.15 | -3591.4 | -4.055%
24 Walpole Park South | MA | 123727 | 108020.74 | 15706.26 | 14.54% | 136334.19 | -12607.19 | -9.247%
25 Walpole Park South | MA | 125019.5 | 133559.05 | -8539.55 | -6.394% | 138727.98 | -13708.48 | -9.882%
3 Walpole Park South | MA | 150714.7025 | 172746.2 | -22031.4975 | -12.75% | 162772.93 | -12058.2275 | -7.408%
4 Walpole Park South | MA | 87160.25 | 96935.57 | -9775.32 | -10.08% | 92807.95 | -5647.7 | -6.085%
Brockton | MA | 141995.5 | 140784.93 | 1210.57 | 0.8599% | 154378.74 | -12383.24 | -8.021%
Canton | MA | 139223.5112 | 149863.23 | -10639.7188 | -7.1% | 148265.58 | -9042.0688 | -6.099%
Chelsea | MA | 258959 | 265501.42 | -6542.42 | -2.464% | 248557.13 | 10401.87 | 4.185%
Hamilton Landfill | MA | 206487.2665 | 252276 | -45788.7335 | -18.15% | 0 | 206487.2665
Holliston | MA | 335953 | 354261.62 | -18308.62 | -5.168% | 393997.22 | -58044.22 | -14.73%
Natick HS - Carports | MA | 114826 | 150902.6 | -36076.6 | -23.91% | 0 | 114826
Norton | MA | 665258 | 744061.3 | -78803.3 | -10.59% | 787612.1 | -122354.1 | -15.53%
Palmer - Boston Rd. | MA | 140541.5475 | 158020.53 | -17478.9825 | -11.06% | 177011 | -36469.4525 | -20.6%
Shirley Bartkus | MA | 100304.5 | 128316.91 | -28012.41 | -21.83% | 240628 | -140323.5 | -58.32%
Stoughton | MA | 162214.0129 | 120628.11 | 41585.9029 | 34.47% | 163750.41 | -1536.3971 | -0.9383%
Wellfleet Landfill | MA | 197584 | 216979 | -19395 | -8.939% | 0 | 197584
Wilmington Garage & Building 7 | MA | 236826.24 | 265956.24 | -29130 | -10.95% | 245303.76 | -8477.52 | -3.456%
Woburn | MA | 364419.1076 | 441019.47 | -76600.3624 | -17.37% | 347015.71 | 17403.3976 | 5.015%
Friendship Solar 1 | MD | 881961 | 927597.8 | -45636.8 | -4.92% | 1003756.9 | -121795.9 | -12.13%
Friendship Solar 2 | MD | 883022 | 944636.9 | -61614.9 | -6.523% | 1006610.5 | -123588.5 | -12.28%
101 Carnegie Center | NJ | 308138 | 379211.6 | -71073.6 | -18.74% | 0 | 308138
302 Carnegie Center | NJ | 134830.6 | 158870.5 | -24039.9 | -15.13% | 0 | 134830.6
510 Carnegie Center | NJ | 330124 | 410128 | -80004 | -19.51% | 0 | 330124
701 Carnegie Center | NJ | 259333 | 325235 | -65902 | -20.26% | 0 | 259333
Hudson County Correction | NJ | 336527.1992 | 314692.13 | 21835.0692 | 6.939% | 366551.28 | -30024.0808 | -8.191%
ER Bison Solar | PA | 406302 | 0 | 406302 |  | 434940 | -28638 | -6.584%
Danville | IL | 741835 | 0 | 741835 |  | 0 | 741835

## 2nd Qtr
Greenbacker Capital |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 13631117.2716 | 11940316.761 | 1690800.5106 | 14.16% | 14253727.4 | -622610.1284 | -4.368%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 55661.875 | 52124.8 | 3537.075 | 6.786% | 58827.13 | -3165.255 | -5.381%
15 Walpole Park South | MA | 202569 | 193291.2 | 9277.8 | 4.8% | 208090.63 | -5521.63 | -2.653%
19 Walpole Park South | MA | 128597.75 | 119373.17 | 9224.58 | 7.728% | 132254.06 | -3656.31 | -2.765%
23 Walpole Park South | MA | 175619.25 | 154323.6 | 21295.65 | 13.8% | 174344.02 | 1275.23 | 0.7314%
24 Walpole Park South | MA | 248823.5 | 222689.46 | 26134.04 | 11.74% | 268030.2 | -19206.7 | -7.166%
25 Walpole Park South | MA | 252567.75 | 233840.07 | 18727.68 | 8.009% | 271514.16 | -18946.41 | -6.978%
3 Walpole Park South | MA | 328233.7975 | 300987.9 | 27245.8975 | 9.052% | 326339.76 | 1894.0375 | 0.5804%
4 Walpole Park South | MA | 177763.5 | 164499.28 | 13264.22 | 8.063% | 178511.19 | -747.69 | -0.4188%
Brockton | MA | 287759 | 257000.67 | 30758.33 | 11.97% | 300530.63 | -12771.63 | -4.25%
Canton | MA | 243917.1117 | 228075.89 | 15841.2217 | 6.946% | 286487.94 | -42570.8283 | -14.86%
Chelsea | MA | 482782 | 471516.5 | 11265.5 | 2.389% | 479302.2 | 3479.8 | 0.726%
Hamilton Landfill | MA | 369142.39 | 393727.3 | -24584.91 | -6.244% | 0 | 369142.39
Holliston | MA | 692665 | 797227.8 | -104562.8 | -13.12% | 788375.9 | -95710.9 | -12.14%
Natick HS - Carports | MA | 253214.6 | 285080.6 | -31866 | -11.18% | 0 | 253214.6
Norton | MA | 8585 | 8582.607 | 2.393 | 0.02788% | 1695937.9 | -1687352.9 | -99.49%
Palmer - Boston Rd. | MA | 231751.5 | 201715 | 30036.5 | 14.89% | 242489 | -10737.5 | -4.428%
Shirley Bartkus | MA | 400027 | 317657.4 | 82369.6 | 25.93% | 405547 | -5520 | -1.361%
Stoughton | MA | 334258.4871 | 183879.18 | 150379.3071 | 81.78% | 325179.18 | 9079.3071 | 2.792%
Wellfleet Landfill | MA | 407838.6 | 388874.1 | 18964.5 | 4.877% | 0 | 407838.6
Wilmington Garage & Building 7 | MA | 484253.375 | 479985.3 | 4268.075 | 0.8892% | 500732.2 | -16478.825 | -3.291%
Woburn | MA | 688189.8924 | 668183.7 | 20006.1924 | 2.994% | 708035.4 | -19845.5076 | -2.803%
Friendship Solar 1 | MD | 1368673 | 1458244.1 | -89571.1 | -6.142% | 1673395.6 | -304722.6 | -18.21%
Friendship Solar 2 | MD | 1375416 | 1457132.8 | -81716.8 | -5.608% | 1644644 | -269228 | -16.37%
101 Carnegie Center | NJ | 569842.17 | 691651.45 | -121809.28 | -17.61% | 0 | 569842.17
302 Carnegie Center | NJ | 249960.89 | 262141.198 | -12180.308 | -4.646% | 0 | 249960.89
510 Carnegie Center | NJ | 637608.939 | 735350.216 | -97741.277 | -13.29% | 0 | 637608.939
701 Carnegie Center | NJ | 497821.79 | 591926.17 | -94104.38 | -15.9% | 0 | 497821.79
Hudson County Correction | NJ | 710863.5239 | 621235.3 | 89628.2239 | 14.43% | 2879962.3 | -2169098.7761 | -75.32%
ER Bison Solar | PA | 673745 | 0 | 673745 |  | 705197 | -31452 | -4.46%
Danville | IL | 1092965.58 | 0 | 1092965.58 |  |  | 1092965.58

## 3rd Qtr
Greenbacker Capital |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 12981778.7529 | 11090958.0609 | 1890820.692 | 17.05% | 10133175.06 | 2848603.6929 | 28.11%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 51812.625 | 47898.02 | 3914.605 | 8.173% | 58697.88 | -6885.255 | -11.73%
15 Walpole Park South | MA | 189269.5 | 178464.85 | 10804.65 | 6.054% | 206524.61 | -17255.11 | -8.355%
19 Walpole Park South | MA | 118882.875 | 109679.3 | 9203.575 | 8.391% | 131744.18 | -12861.305 | -9.762%
23 Walpole Park South | MA | 162363.25 | 145778.48 | 16584.77 | 11.38% | 173306.11 | -10942.86 | -6.314%
24 Walpole Park South | MA | 222295.28 | 202661.39 | 19633.89 | 9.688% | 266324.05 | -44028.77 | -16.53%
25 Walpole Park South | MA | 225081.6363 | 219656.11 | 5425.5263 | 2.47% | 269433.39 | -44351.7537 | -16.46%
3 Walpole Park South | MA | 302990.64 | 276961.72 | 26028.92 | 9.398% | 322244.91 | -19254.27 | -5.975%
4 Walpole Park South | MA | 165614 | 153139.65 | 12474.35 | 8.146% | 178657.19 | -13043.19 | -7.301%
Brockton | MA | 274632 | 238069.64 | 36562.36 | 15.36% | 293285.4 | -18653.4 | -6.36%
Canton | MA | 258372.877 | 235017.87 | 23355.007 | 9.938% | 291527.2 | -33154.323 | -11.37%
Chelsea | MA | 452729 | 439379.9 | 13349.1 | 3.038% | 471141 | -18412 | -3.908%
Hamilton Landfill | MA | 369195.183 | 394477.913 | -25282.73 | -6.409% | 0 | 369195.183
Holliston | MA | 651156.5 | 742640.9 | -91484.4 | -12.32% | 767006 | -115849.5 | -15.1%
Natick HS - Carports | MA | 231627.9668 | 264062.1838 | -32434.217 | -12.28% | 0 | 231627.9668
Norton | MA | 0 | 0 | 0 |  | 0 | 0
Palmer - Boston Rd. | MA | 232142 | 209831.21 | 22310.79 | 10.63% | 241724 | -9582 | -3.964%
Shirley Bartkus | MA | 375830.3866 | 9635.973 | 366194.4136 | 3800% | 403460 | -27629.6134 | -6.848%
Stoughton | MA | 307704.5 | 173677.64 | 134026.86 | 77.17% | 321101.14 | -13396.64 | -4.172%
Wellfleet Landfill | MA | 385394.374 | 437160.369 | -51765.995 | -11.84% | 0 | 385394.374
Wilmington Garage & Building 7 | MA | 454034.625 | 448267.2 | 5767.425 | 1.287% | 497937.3 | -43902.675 | -8.817%
Woburn | MA | 656033 | 632727.8 | 23305.2 | 3.683% | 725400.2 | -69367.2 | -9.563%
Friendship Solar 1 | MD | 1302606 | 1418652.4 | -116046.4 | -8.18% | 1597036.3 | -294430.3 | -18.44%
Friendship Solar 2 | MD | 1307389 | 1418502.4 | -111113.4 | -7.833% | 1547210.6 | -239821.6 | -15.5%
101 Carnegie Center | NJ | 541222.65 | 644026 | -102803.35 | -15.96% | 0 | 541222.617
302 Carnegie Center | NJ | 235303.8005 | 245147.0091 | -9843.2086 | -4.015% | 0 | 235303.8005
510 Carnegie Center | NJ | 601093.124 | 686838.229 | -85745.105 | -12.48% | 0 | 601093.124
701 Carnegie Center | NJ | 463171.732 | 548336.704 | -85164.972 | -15.53% | 0 | 463171.732
Hudson County Correction | NJ | 662627.7017 | 570267.2 | 92360.5017 | 16.2% | 668190.6 | -5562.8983 | -0.8325%
ER Bison Solar | PA | 649927 | 0 | 649927 |  | 701223 | -51296 | -7.315%
Danville | IL | 1131275.526 | 0 | 1131275.526 |  | 0 | 1131275.526

## 4th Qtr
Greenbacker Capital |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 7368272.9164 | 6545649.23 | 822623.6864 | 12.57% | 4825532.481 | 2542740.4354 | 52.69%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 28688.9375 | 28074.701 | 614.2365 | 2.188% | 26967.721 | 1721.2165 | 6.383%
15 Walpole Park South | MA | 104153 | 111395.48 | -7242.48 | -6.502% | 89228.88 | 14924.12 | 16.73%
19 Walpole Park South | MA | 61188.5 | 65174.61 | -3986.11 | -6.116% | 58354.98 | 2833.52 | 4.856%
23 Walpole Park South | MA | 88157 | 87482.7 | 674.3 | 0.7708% | 75130.85 | 13026.15 | 17.34%
24 Walpole Park South | MA | 112616.97 | 86238.408 | 26378.562 | 30.59% | 115699.48 | -3082.51 | -2.664%
25 Walpole Park South | MA | 119037.6137 | 129136.33 | -10098.7163 | -7.82% | 117695.56 | 1342.0537 | 1.14%
3 Walpole Park South | MA | 153431.6725 | 166914.2 | -13482.5275 | -8.078% | 139025.42 | 14406.2525 | 10.36%
4 Walpole Park South | MA | 88539 | 98734.25 | -10195.25 | -10.33% | 79463.04 | 9075.96 | 11.42%
Brockton | MA | 151426.5 | 141471.67 | 9954.83 | 7.037% | 135036.58 | 16389.92 | 12.14%
Canton | MA | 135913.25 | 141481.84 | -5568.59 | -3.936% | 131716.83 | 4196.42 | 3.186%
Chelsea | MA | 239688 | 254259.74 | -14571.74 | -5.731% | 209890.17 | 29797.83 | 14.2%
Hamilton Landfill | MA | 211029.231 | 265860.5 | -54831.269 | -20.62% | 0 | 211029.231
Holliston | MA | 345558 | 323947.65 | 21610.35 | 6.671% | 342519.75 | 3038.25 | 0.887%
Natick HS - Carports | MA | 109428.2 | 139584.601 | -30156.401 | -21.6% | 0 | 109428.2
Norton | MA | 0 | 0 | 0 |  | 0 | 0
Palmer - Boston Rd. | MA | 149896 | 175194.37 | -25298.37 | -14.44% | 138243 | 11653 | 8.429%
Shirley Bartkus | MA | 229712.0556 | 0 | 229712.0556 |  | 219334 | 10378.0556 | 4.732%
Stoughton | MA | 175631 | 116742.08 | 58888.92 | 50.44% | 148538.62 | 27092.38 | 18.24%
Wellfleet Landfill | MA | 207650.8 | 225057.9 | -17407.1 | -7.734% | 0 | 207650.8
Wilmington Garage & Building 7 | MA | 219257 | 245268.96 | -26011.96 | -10.61% | 214987.19 | 4269.81 | 1.986%
Woburn | MA | 356648 | 432008.2 | -75360.2 | -17.44% | 315481.21 | 41166.79 | 13.05%
Friendship Solar 1 | MD | 880006 | 899711.9 | -19705.9 | -2.19% | 797518.6 | 82487.4 | 10.34%
Friendship Solar 2 | MD | 866580 | 934069.4 | -67489.4 | -7.225% | 823977.8 | 42602.2 | 5.17%
101 Carnegie Center | NJ | 288438.4 | 378611.92 | -90173.52 | -23.82% | 0 | 288438.4
302 Carnegie Center | NJ | 129921 | 158111.2 | -28190.2 | -17.83% | 0 | 129921
510 Carnegie Center | NJ | 316076.7 | 409599 | -93522.3 | -22.83% | 0 | 316076.7
701 Carnegie Center | NJ | 266363.4055 | 308935.82 | -42572.4145 | -13.78% | 72312.8 | 194050.6055 | 268.3%
Hudson County Correction | NJ | 331087.1665 | 222581.8 | 108505.3665 | 48.75% | 313015 | 18072.1665 | 5.774%
ER Bison Solar | PA | 476066.5 | 0 | 476066.5 |  | 261395 | 214671.5 | 82.13%
Danville | IL | 526083.014 | 0 | 526083.014 |  | 0

## Jan
Greenbacker Capital |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1255667.4659 | 1584905.264 | -329237.7981 | -20.77% | 1501477.323 | -245809.8571 | -16.37%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 3478.8125 | 6181.574 | -2702.7615 | -43.72% | 6823.253 | -3344.4405 | -49.02%
15 Walpole Park South | MA | 12517 | 22722.47 | -10205.47 | -44.91% | 21603.71 | -9086.71 | -42.06%
19 Walpole Park South | MA | 7105.375 | 13704.15 | -6598.775 | -48.15% | 14450.27 | -7344.895 | -50.83%
23 Walpole Park South | MA | 10190.25 | 16832.77 | -6642.52 | -39.46% | 18563.55 | -8373.3 | -45.11%
24 Walpole Park South | MA | 15037 | 14267.73 | 769.27 | 5.392% | 28642.02 | -13605.02 | -47.5% | 1. Inverter 8 was offline on 01/15/24 7 and back online on 01/17/2024. | 1.SR080248
25 Walpole Park South | MA | 15224.5 | 26799 | -11574.5 | -43.19% | 29130.79 | -13906.29 | -47.74%
3 Walpole Park South | MA | 19881.5 | 35122.52 | -15241.02 | -43.39% | 34800.55 | -14919.05 | -42.87%
4 Walpole Park South | MA | 10678.25 | 19843.16 | -9164.91 | -46.19% | 19687.72 | -9009.47 | -45.76%
Brockton | MA | 21358 | 29225.2 | -7867.2 | -26.92% | 35891.12 | -14533.12 | -40.49%
Canton | MA | 17412.25 | 31213.29 | -13801.04 | -44.22% | 30904.81 | -13492.56 | -43.66% | 1. Inverter 4 tripped offline on 01/12/2024 at 08:30 & back online on 01/17/2024 at 14:30. | 1.SR080166
Chelsea | MA | 38716 | 54336.05 | -15620.05 | -28.75% | 55003.46 | -16287.46 | -29.61%
Hamilton Landfill | MA | 30221 | 58716 | -28495 | -48.53% | 0 | 30221
Holliston | MA | 37423.5 | 60597.82 | -23174.32 | -38.24% | 84734.92 | -47311.42 | -55.83% | 1.Site tripped offline on 01/13/2024 at 03:30 & back on 01/16/2024 mid day. | 1. SR080182
Natick HS - Carports | MA | 13924 | 29010 | -15086 | -52% | 0 | 13924
Norton | MA | 93336 | 144118.9 | -50782.9 | -35.24% | 162736.5 | -69400.5 | -42.65% | 1. Inverter 1 was tripped offline on 01/02/2024 at 8:45 & back online on 01/03/2024 at 11:30. 2. Site was offline tripped offline on 01/21/2024 at 11:45 & back online on 01/22/2024 at 10:30. | 1. SR079865 2. SR080375
Palmer - Boston Rd. | MA | 18016.0475 | 31872.06 | -13856.0125 | -43.47% | 45090 | -27073.9525 | -60.04%
Shirley Bartkus | MA | 24169.8712 | 47290.29 | -23120.4188 | -48.89% | 65151 | -40981.1288 | -62.9%
Stoughton | MA | 22398.5 | 29378.29 | -6979.79 | -23.76% | 35608.12 | -13209.62 | -37.1%
Wellfleet Landfill | MA | 40023 | 57476 | -17453 | -30.37% | 0 | 40023 |  | 1. Site was tripped offline on 01/07 at 18:15 and back online on 01/08 at 12:00 | 1. SR080033
Wilmington Garage & Building 7 | MA | 28124.62 | 53740.59 | -25615.97 | -47.67% | 51473.44 | -23348.82 | -45.36%
Woburn | MA | 47752.5 | 99772.07 | -52019.57 | -52.14% | 69636.91 | -21884.41 | -31.43% | 1. Inverter 17 tripped offline on 01/23/2024 at 12:00 & back online at 16:30. | 1. SR079023
Friendship Solar 1 | MD | 185310 | 198138.4 | -12828.4 | -6.474% | 253076.2 | -67766.2 | -26.78%
Friendship Solar 2 | MD | 183527 | 204402.5 | -20875.5 | -10.21% | 250422.2 | -66895.2 | -26.71%
101 Carnegie Center | NJ | 42576 | 72136 | -29560 | -40.98% | 0 | 42576 |  | 1.Inverters 14 and 18 tripped offline on 01/23/2024 at 13:45 & back online on 01/24/2024. | 1. SR080417
302 Carnegie Center | NJ | 18853 | 28852 | -9999 | -34.66% | 0 | 18853
510 Carnegie Center | NJ | 40883 | 79791 | -38908 | -48.76% | 0 | 40883 |  | 1. Inverter 7 tripped offline at 12/05/2023 at 13:00 & back online at 01/24 at 12:15. 2. Inverters 2, 5, and 24 tripped offline on 01/23/2024 & back online on 01/24/2024. | 1.SR078798 2. SR080419
701 Carnegie Center | NJ | 36140 | 59926 | -23786 | -39.69% | 0 | 36140
Hudson County Correction | NJ | 52029.4897 | 59439.43 | -7409.9403 | -12.47% | 87395.78 | -35366.2903 | -40.47%
ER Bison Solar | PA | 50310 | 0 | 50310 |  | 100651 | -50341 | -50.02%
Danville | IL | 119051 | 0 | 119051 |  | 0 | 119051

## Feb
Greenbacker Capital |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2964055.2715 | 2754884.14 | 209171.1315 | 7.593% | 2036870.179 | 927185.0925 | 45.52%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 10004.8125 | 10663.78 | -658.9675 | -6.179% | 9487.909 | 516.9035 | 5.448%
15 Walpole Park South | MA | 37374.75 | 41176.83 | -3802.08 | -9.234% | 32724.01 | 4650.74 | 14.21%
19 Walpole Park South | MA | 21676.1706 | 24933.68 | -3257.5094 | -13.06% | 20845.28 | 830.8906 | 3.986%
23 Walpole Park South | MA | 31445.5 | 31659.04 | -213.54 | -0.6745% | 26978.49 | 4467.01 | 16.56%
24 Walpole Park South | MA | 44947 | 41665.05 | 3281.95 | 7.877% | 41430.21 | 3516.79 | 8.488% | 1. Inverter 8 is offline on 02/16 and back online on 02/17 | 1. SR080248
25 Walpole Park South | MA | 45891 | 48624.34 | -2733.34 | -5.621% | 42368.25 | 3522.75 | 8.315%
3 Walpole Park South | MA | 52732 | 63086.7 | -10354.7 | -16.41% | 49247.23 | 3484.77 | 7.076%
4 Walpole Park South | MA | 32263.5 | 35638.16 | -3374.66 | -9.469% | 28453.96 | 3809.54 | 13.39%
Brockton | MA | 50932.5 | 50100.46 | 832.04 | 1.661% | 45403.86 | 5528.64 | 12.18%
Canton | MA | 54122.75 | 55077.24 | -954.49 | -1.733% | 48151.77 | 5970.98 | 12.4% | 1.Site tripped offline on 02/15 at 21:30 and back online at 02/16 at 10:30AM
Chelsea | MA | 100779.5 | 97636.57 | 3142.93 | 3.219% | 77108.57 | 23670.93 | 30.7%
Hamilton Landfill | MA | 81955.2665 | 92578 | -10622.7335 | -11.47% | 0 | 81955.2665
Holliston | MA | 129951.5 | 123734.8 | 6216.7 | 5.024% | 123168 | 6783.5 | 5.508%
Natick HS - Carports | MA | 41947 | 54546.6 | -12599.6 | -23.1% | 0 | 41947
Norton | MA | 208382 | 259599.2 | -51217.2 | -19.73% | 233294 | -24912 | -10.68% | 1. CB 1.1 is offline for whole month. | 1. SR079865
Palmer - Boston Rd. | MA | 58605.5 | 62468.96 | -3863.46 | -6.185% | 62743 | -4137.5 | -6.594%
Shirley Bartkus | MA | 27056.1288 | 36741.23 | -9685.1012 | -26.36% | 77292 | -50235.8712 | -64.99%
Stoughton | MA | 58669.5 | 44175.05 | 14494.45 | 32.81% | 49499.52 | 9169.98 | 18.53% | 1. Except inverter 13 all other inverters tripped offline on 02/16/2024 at 09:00AM and later back online on 02/16/2024 at 14:00. | 1. SR081055
Wellfleet Landfill | MA | 65995 | 82038 | -16043 | -19.56% | 0 | 65995
Wilmington Garage & Building 7 | MA | 92593.62 | 97217.95 | -4624.33 | -4.757% | 78728.72 | 13864.9 | 17.61%
Woburn | MA | 146359 | 163940.8 | -17581.8 | -10.72% | 112139.6 | 34219.4 | 30.52%
Friendship Solar 1 | MD | 322297 | 332843.8 | -10546.8 | -3.169% | 310998.2 | 11298.8 | 3.633%
Friendship Solar 2 | MD | 322955 | 339690.4 | -16735.4 | -4.927% | 322799.2 | 155.8 | 0.04827%
101 Carnegie Center | NJ | 107727 | 136195.6 | -28468.6 | -20.9% | 0 | 107727
302 Carnegie Center | NJ | 47965.6 | 57063.5 | -9097.9 | -15.94% | 0 | 47965.6
510 Carnegie Center | NJ | 119003 | 146361 | -27358 | -18.69% | 0 | 119003
701 Carnegie Center | NJ | 90283 | 115418 | -25135 | -21.78% | 0 | 90283
Hudson County Correction | NJ | 110854.6731 | 110009.4 | 845.2731 | 0.7684% | 105210.4 | 5644.2731 | 5.365%
ER Bison Solar | PA | 162625 | 0 | 162625 |  | 138798 | 23827 | 17.17%
Danville | IL | 286661 | 0 | 286661 |  | 0 | 286661

## Mar
Greenbacker Capital |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3886716.6375 | 3315526.8 | 571189.8375 | 17.23% | 3004280.57 | 882436.0675 | 29.37%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 13795.5625 | 12505.45 | 1290.1125 | 10.32% | 14738.99 | -943.4275 | -6.401%
15 Walpole Park South | MA | 50765.75 | 48451.57 | 2314.18 | 4.776% | 51542.51 | -776.76 | -1.507%
19 Walpole Park South | MA | 31449.4544 | 29167.38 | 2282.0744 | 7.824% | 32813.61 | -1364.1556 | -4.157%
23 Walpole Park South | MA | 43350 | 37112.66 | 6237.34 | 16.81% | 43035.11 | 314.89 | 0.7317% | 1. Inverter 3 is derating about 20kW during peak hours on 03/01 and later the inverter was powercycled by technician. | 1. SR081496
24 Walpole Park South | MA | 63743 | 52087.96 | 11655.04 | 22.38% | 66261.96 | -2518.96 | -3.802%
25 Walpole Park South | MA | 63904 | 58135.71 | 5768.29 | 9.922% | 67228.94 | -3324.94 | -4.946%
3 Walpole Park South | MA | 78101.2025 | 74536.98 | 3564.2225 | 4.782% | 78725.15 | -623.9475 | -0.7926% | 1. Inverter 13 derated on 03/21 & resolved next day. | 1.SR082332
4 Walpole Park South | MA | 44218.5 | 41454.25 | 2764.25 | 6.668% | 44666.27 | -447.77 | -1.002%
Brockton | MA | 69705 | 61459.27 | 8245.73 | 13.42% | 73083.76 | -3378.76 | -4.623%
Canton | MA | 67688.5112 | 63572.7 | 4115.8112 | 6.474% | 69209 | -1520.4888 | -2.197% | 1. Inverter 3 tripped offline on 03/08 at 18:00 & back online 03/11 at 15:30. | 1. SR081715
Chelsea | MA | 119463.5 | 113528.8 | 5934.7 | 5.227% | 116445.1 | 3018.4 | 2.592%
Hamilton Landfill | MA | 94311 | 100982 | -6671 | -6.606% | 0 | 94311
Holliston | MA | 168578 | 169929 | -1351 | -0.795% | 186094.3 | -17516.3 | -9.413% | 1. Site tripped offline on 03/31 at 9:30am and back online on 04/01 at 11:00am | 1. SR082943
Natick HS - Carports | MA | 58955 | 67346 | -8391 | -12.46% | 0 | 58955
Norton | MA | 363540 | 340343.2 | 23196.8 | 6.816% | 391581.6 | -28041.6 | -7.161% | 1. Site is offline at 8:00am on 03/20 and back online at 15:00 on 03/20. | 1. SR082234
Palmer - Boston Rd. | MA | 63920 | 63679.51 | 240.49 | 0.3777% | 69178 | -5258 | -7.601%
Shirley Bartkus | MA | 49078.5 | 44285.39 | 4793.11 | 10.82% | 98185 | -49106.5 | -50.01% | 1. Inverter 12 was offline on 03/31 | 1. SR082945
Stoughton | MA | 81146.0129 | 47074.77 | 34071.2429 | 72.38% | 78642.77 | 2503.2429 | 3.183%
Wellfleet Landfill | MA | 91566 | 77465 | 14101 | 18.2% | 0 | 91566 |  | 1. Site was offline on 03/11 between 11:15 to 15:30 | 1. SR081753
Wilmington Garage & Building 7 | MA | 116108 | 114997.7 | 1110.3 | 0.9655% | 115101.6 | 1006.4 | 0.8744% | 1. Inverter 5 is offline on 03/23 dur ground fault | 1. SR082598
Woburn | MA | 170307.6076 | 177306.6 | -6998.9924 | -3.947% | 165239.2 | 5068.4076 | 3.067% | 1. Inverter 27 was offline due to arc fault on 03/03 and 03/31 | 1. SR082924
Friendship Solar 1 | MD | 374354 | 396615.6 | -22261.6 | -5.613% | 439682.5 | -65328.5 | -14.86% | 1. Inverters 1 to 6 are derating during 09:00am to 12:00pm on 03/10, 03/11, 03/18 & 03/21. | 1. SR082017
Friendship Solar 2 | MD | 376540 | 400544 | -24004 | -5.993% | 433389.1 | -56849.1 | -13.12% | 1. Inverters 07 to 12 are derating during 09:00am to 12:00pm on 03/10, 03/11, 03/18 & 03/21 | 1. SR082020
101 Carnegie Center | NJ | 157835 | 170880 | -13045 | -7.634% | 0 | 157835
302 Carnegie Center | NJ | 68012 | 72955 | -4943 | -6.775% | 0 | 68012
510 Carnegie Center | NJ | 170238 | 183976 | -13738 | -7.467% | 0 | 170238
701 Carnegie Center | NJ | 132910 | 149891 | -16981 | -11.33% | 0 | 132910
Hudson County Correction | NJ | 173643.0364 | 145243.3 | 28399.7364 | 19.55% | 173945.1 | -302.0636 | -0.1737% | 1. Inverter 5 is derating during sunny days throughout the month 2. Inverter 3 right unit, Inverter 2 left unit has multiple tripping events thorughtout the month 3. Inverter 2 left unit tripped offline on 03/16 and back online 03/21 | 1. SR081196 2. SR081401 3. SR082342
ER Bison Solar | PA | 193367 | 0 | 193367 |  | 195491 | -2124 | -1.086% | 1. Site was offline on 03/10 between 14:00 to 15:00 2. Technician took inverters 6, 7 and 11 offline about 1 hour on 03/13 3. Inverter 11 tripped offline on 03/29 at 10:55 and back online at 17:00 4. Inverters 9, 10 and 11 7 were offline during peak hours on 03/29, 03/30 and 03/31 | 1. SR081730 2. PM7645 3. SR082897 4. SR082904
Danville | IL | 336123 | 0 | 336123 |  | 0 | 336123 |  | 1. Inverters 11 & 16 are offline on 03/14 between 09:30 to 14:15 | 1. SR081897

## Apr
Greenbacker Capital |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 3974120.9402 | 3410905.017 | 563215.9232 | 16.51% | 3625289.15 | 348831.7902 | 9.622%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 16114.8125 | 14796.69 | 1318.1225 | 8.908% | 17954.59 | -1839.7775 | -10.25%
15 Walpole Park South | MA | 58626.75 | 55434.57 | 3192.18 | 5.758% | 63304.81 | -4678.06 | -7.39%
19 Walpole Park South | MA | 37188.75 | 34363.12 | 2825.63 | 8.223% | 40259.89 | -3071.14 | -7.628%
23 Walpole Park South | MA | 50682.25 | 43350.75 | 7331.5 | 16.91% | 52936.25 | -2254 | -4.258%
24 Walpole Park South | MA | 72883 | 62551.38 | 10331.62 | 16.52% | 81454.66 | -8571.66 | -10.52% | 1. Site tripped offline at 07:30AM on 04/04 and back online at 13:15 on 04/05. | 1. SR083068
25 Walpole Park South | MA | 72574.5 | 66839.05 | 5735.45 | 8.581% | 82509.09 | -9934.59 | -12.04% | 1. Site tripped offline at 07:15AM on 04/04 and back online at 13:15 on 04/05. | 1. SR083069
3 Walpole Park South | MA | 94905.7975 | 87738.4 | 7167.3975 | 8.169% | 98901.56 | -3995.7625 | -4.04%
4 Walpole Park South | MA | 51464.25 | 47241.47 | 4222.78 | 8.939% | 54449.55 | -2985.3 | -5.483%
Brockton | MA | 84611.5 | 74862.95 | 9748.55 | 13.02% | 90635.83 | -6024.33 | -6.647% | 1. Inverter 13 is underperformed 4kW down compared to its peers through out the month | 1. SR075675
Canton | MA | 45279.9888 | 43765.15 | 1514.8388 | 3.461% | 82505.94 | -37225.9512 | -45.12% | 1. Site tripped offline on 04/04 at 14:45 and back online at 15:30 on same day. 2. Site tripped offline on 04/05 at 16:10 and back online on 04/19 at 09:30. 3. Inverter 4 tripped offline on 04/27 at 07:10 and back online on 04/29 at 13:15. | 1. SR083106 2. SR083114 & SR083365 3. SR083878
Chelsea | MA | 139486 | 134564.2 | 4921.8 | 3.658% | 146687.6 | -7201.6 | -4.909% | 1. Site tripped offline on 04/12 at 08:30 and back online at 13:45 on same day. | 1. SR083363
Hamilton Landfill | MA | 109359.79 | 116691.9 | -7332.11 | -6.283% | 0 | 109359.79
Holliston | MA | 203202.5 | 217775.9 | -14573.4 | -6.692% | 223764.6 | -20562.1 | -9.189% | 1. Site tripped offline on 03/31 and back online on 04/01 at 11:00. 2. Inverter 5 right and left unit tripped offline on 04/15 at 13:00 and back online on 04/19 at 12:45. 3. Site tripped offline on 04/28 at 15:30 and back online on 04/29 at 10:45. | 1. SR082943 2. SR083523 3. SR083903
Natick HS - Carports | MA | 72728 | 80794.9 | -8066.9 | -9.984% | 0 | 72728
Norton | MA | 8585 | 8582.607 | 2.393 | 0.02788% | 497513.2 | -488928.2 | -98.27% | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 67555 | 61426.2 | 6128.8 | 9.978% | 75993 | -8438 | -11.1%
Shirley Bartkus | MA | 122856.5 | 103482.6 | 19373.9 | 18.72% | 124491 | -1634.5 | -1.313% | 1. Inverter 3 dropped 1 string on 4/23 and underproducing 5kW since then, some of the modules need to be replaced | 1. SR083810, SR081044
Stoughton | MA | 97464.4871 | 52017.09 | 45447.3971 | 87.37% | 99111.88 | -1647.3929 | -1.662%
Wellfleet Landfill | MA | 118025.8 | 105212.8 | 12813 | 12.18% | 0 | 118025.8 |  | 1. Inverters 3,4,5,6,7,8,9,10,11,12 tripped offline around 10am on 04/04 and back online on 04/05 | 1. SR083077
Wilmington Garage & Building 7 | MA | 142289.125 | 140358.4 | 1930.725 | 1.376% | 142807.7 | -518.575 | -0.3631%
Woburn | MA | 202155.8924 | 200972.2 | 1183.6924 | 0.589% | 201468.7 | 687.1924 | 0.3411% | 1. Inverter 27 tripped offline on 03/30 and back online on 04/01 at 12:15pm. 2. Inverter 27 tripped offline on 04/08 at 07:45am and back online on 04/09 at 14:15. | 1. SR082924 2. SR083176
Friendship Solar 1 | MD | 393254 | 412712.7 | -19458.7 | -4.715% | 516949.9 | -123695.9 | -23.93%
Friendship Solar 2 | MD | 394264 | 413111.8 | -18847.8 | -4.562% | 503238.6 | -108974.6 | -21.65%
101 Carnegie Center | NJ | 176267.28 | 199303.32 | -23036.04 | -11.56% | 0 | 176267.28 |  | 1. Inverter 8 is underperforming 5kW compared to its peers for whole month. | 1. SR087088
302 Carnegie Center | NJ | 75863.2 | 80034.5 | -4171.3 | -5.212% | 0 | 75863.2
510 Carnegie Center | NJ | 191960 | 208228.6 | -16268.6 | -7.813% | 0 | 191960 |  | 1. Inverter 17 was underproduced 5kW compared to its peers for whole month. | 1. SR083972
701 Carnegie Center | NJ | 150226.1 | 170131.47 | -19905.37 | -11.7% | 0 | 150226.1
Hudson County Correction | NJ | 202450.2869 | 174560.3 | 27889.9869 | 15.98% | 212251.8 | -9801.5131 | -4.618% | 1. Inverter 5 has multiple trip events during high irradiance days. | 1. SR084029
ER Bison Solar | PA | 195894 | 0 | 195894 |  | 216099 | -20205 | -9.35% | 1. Inverter 11 tripped offline on 04/07 at 11:15 am and later back online at 16:30 pm on same day. | 1. SR083158
Danville | IL | 325902.38 | 0 | 325902.38 |  | 0 | 325902.38

## May
Greenbacker Capital |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 4473317.8996 | 3869725.676 | 603592.2236 | 15.6% | 6372815.65 | -1899497.7504 | -29.81%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 18870.1875 | 17653.89 | 1216.2975 | 6.89% | 20152.78 | -1282.5925 | -6.364%
15 Walpole Park South | MA | 68494.5 | 65531.46 | 2963.04 | 4.522% | 71515.53 | -3021.03 | -4.224%
19 Walpole Park South | MA | 43511.625 | 40299.69 | 3211.935 | 7.97% | 45357.92 | -1846.295 | -4.071%
23 Walpole Park South | MA | 59620.5 | 52342.5 | 7278 | 13.9% | 59960.62 | -340.12 | -0.5672%
24 Walpole Park South | MA | 84188.5 | 74470.68 | 9717.82 | 13.05% | 92156.27 | -7967.77 | -8.646% | 1. Inverter 11 is offline from 05/13. Inverter being RMA'D. | 1. SR084606
25 Walpole Park South | MA | 88315 | 79615.64 | 8699.36 | 10.93% | 93376.17 | -5061.17 | -5.42%
3 Walpole Park South | MA | 111481.5 | 100346.7 | 11134.8 | 11.1% | 111938.2 | -456.7 | -0.408% | 1. Inverter 2 was offline on 05/23 and later back online on 05/24 and started late on 05/27. | 1. SR085060
4 Walpole Park South | MA | 60084 | 55362.13 | 4721.87 | 8.529% | 61121.96 | -1037.96 | -1.698%
Brockton | MA | 93219 | 84494.77 | 8724.23 | 10.33% | 103804.7 | -10585.7 | -10.2% | 1. Site tripped offline on 05/19 at 06:35 and back online on 05/20 at 07:00. 2. Inverter 13 is underperformed 4kW down compared to its peers through out the month | 1. SR084834 2. SR075675
Canton | MA | 95888 | 88179.36 | 7708.64 | 8.742% | 102551.3 | -6663.3 | -6.498%
Chelsea | MA | 166159.5 | 161097.1 | 5062.4 | 3.142% | 164347.2 | 1812.3 | 1.103%
Hamilton Landfill | MA | 127791.3 | 134449.6 | -6658.3 | -4.952% | 0 | 127791.3
Holliston | MA | 238773 | 271207.1 | -32434.1 | -11.96% | 281565.2 | -42792.2 | -15.2% | 1. Inverter 5 right unit tripped offline on 05/02 at 15:14 & left unit tripped offline on 05/11 at 12:15 and back online on 05/20 at 17:30. | 1. SR084220
Natick HS - Carports | MA | 85420.7 | 95687.9 | -10267.2 | -10.73% | 0 | 85420.7
Norton | MA | 0 | 0 | 0 |  | 595612.5 | -595612.5 | -100% | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 82642.5 | 71216.7 | 11425.8 | 16.04% | 81652 | 990.5 | 1.213% | 1. Inverter 9 derated about 3kW during high irradiance days from 05/25 to 06/13 | 1. SR085423
Shirley Bartkus | MA | 133913 | 102417.7 | 31495.3 | 30.75% | 135175 | -1262 | -0.9336% | 1. Inverter 3 dropped 1 string on 4/23 and underproducing 5kW since then, some of the modules need to be replaced | 1. SR083810, SR081044
Stoughton | MA | 111148 | 61788.73 | 49359.27 | 79.88% | 113543.2 | -2395.2 | -2.11%
Wellfleet Landfill | MA | 136743.9 | 126581.05 | 10162.85 | 8.029% | 0 | 136743.9
Wilmington Garage & Building 7 | MA | 161283.625 | 159042.9 | 2240.725 | 1.409% | 180417.1 | -19133.475 | -10.61% | 1. Site was offline from 07:15 AM to 11:30 AM on 05/11 due to utility planned outage | 1. SR084574
Woburn | MA | 227766 | 220793.8 | 6972.2 | 3.158% | 256809 | -29043 | -11.31% | 1. Site tripped offline on 05/28 at 09:56am and back online at 13:00 on same day | 1. SR085214
Friendship Solar 1 | MD | 406608 | 438724.1 | -32116.1 | -7.32% | 577160.7 | -170552.7 | -29.55% | 1. Site tripped offline on 05/30 at 09:00am and back online at 18:00 on same day. | 1. SR085302
Friendship Solar 2 | MD | 408961 | 437754.2 | -28793.2 | -6.577% | 566911.3 | -157950.3 | -27.86% | 1. Site tripped offline on 05/30 at 09:00am and back online at 18:00 on same day. | 1. SR085303
101 Carnegie Center | NJ | 178862.68 | 220273.64 | -41410.96 | -18.8% | 0 | 178862.68 |  | 1. Inverter 8 is underperforming 5kW compared to its peers for whole month. 2. Site was offline from 12:00pm to 13:45pm on 05/20. | 1. SR087088 2. SR084908
302 Carnegie Center | NJ | 78094.21 | 81733.02 | -3638.81 | -4.452% | 0 | 78094.21
510 Carnegie Center | NJ | 199654.939 | 233678.216 | -34023.277 | -14.56% | 0 | 199654.939 |  | 1. Inverter 25 was tripped offline at 8:30am on 05/01 and back online on 05/02 at 14:00. | 1. SR084041
701 Carnegie Center | NJ | 156416.95 | 187294.8 | -30877.85 | -16.49% | 0 | 156416.95
Hudson County Correction | NJ | 235685.4831 | 207688.3 | 27997.1831 | 13.48% | 2418859 | -2183173.5169 | -90.26% | 1.Inverter 5 has multiple trip events throughout the day during high irradiance days observed on 05/01, 05/02, 05/07, 05/11 & 05/20 to 05/22. | 1. SR084029
ER Bison Solar | PA | 230092 | 0 | 230092 |  | 238828 | -8736 | -3.658% | 1. Inverter 1 is underperforming by 16kW, inverter 2 is underperforming by 24kW, inverter 3 is underperforming by 15kW, inverter 4 is underperforming by 8kW, inverter 5 is underperforming by 9kW, inverter 9 is underperforming by 6kW for whole month. | 1. SR087390
Danville | IL | 383628.3 | 0 | 383628.3 |  | 0 | 383628.3

## Jun
Greenbacker Capital |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 5183678.4319 | 4659686.068 | 523992.3639 | 11.25% | 4255622.6 | 928055.8319 | 21.81%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 20676.875 | 19674.22 | 1002.655 | 5.096% | 20719.76 | -42.885 | -0.207%
15 Walpole Park South | MA | 75447.75 | 72325.17 | 3122.58 | 4.317% | 73270.29 | 2177.46 | 2.972%
19 Walpole Park South | MA | 47897.375 | 44710.36 | 3187.015 | 7.128% | 46636.25 | 1261.125 | 2.704%
23 Walpole Park South | MA | 65316.5 | 58630.35 | 6686.15 | 11.4% | 61447.15 | 3869.35 | 6.297%
24 Walpole Park South | MA | 91752 | 85667.4 | 6084.6 | 7.103% | 94419.27 | -2667.27 | -2.825% | 1. Inverter 11 is offline from 05/13 and back online at 12:45PM on 06/11. 2. Inverter 10 tripped offline at 16:30 on 06/18. Inverter is being RMA'd | 1. SR084606 2. SR086410
25 Walpole Park South | MA | 91678.25 | 87385.38 | 4292.87 | 4.913% | 95628.9 | -3950.65 | -4.131% | 1. Site tripped offline at 14:15 on 06/13 and back online at 12:00PM on 06/14. 2. Inverter 9 is underperforming approximately 20kW from 06/15 to 06/18 and Inverter 13 is underperforming approximately 6kW from 06/15. | 1. SR086178 2. SR086279
3 Walpole Park South | MA | 121846.5 | 112902.8 | 8943.7 | 7.922% | 115500 | 6346.5 | 5.495% | 1. Inverter 2 was offline on 06/03 and back online on 06/04 and started late on 06/06 and 06/07. 2. Inverter 15 underproduced about 28 kW from 06/08 to 06/11. 3. Inverter 8 was started late on 06/18, 06/23, 06/24, 06/25, 06/27 & was offline on 06/22, again tripped offline on 06/28 at 14:15 and back online on 06/29 and was offline on 06/30. 4. Inverter 9 tripped offline on 06/20 at 06:30 and back online at 14:45 on same day . | 1. SR085060 2. SR085845 3. SR086354 4. SR086479
4 Walpole Park South | MA | 66215.25 | 61895.68 | 4319.57 | 6.979% | 62939.68 | 3275.57 | 5.204%
Brockton | MA | 109928.5 | 97642.95 | 12285.55 | 12.58% | 106090.1 | 3838.4 | 3.618% | 1. Inverter 13 is underperformed 4kW down compared to its peers through out the month | 1. SR075675
Canton | MA | 102749.123 | 96131.38 | 6617.743 | 6.884% | 101430.7 | 1318.423 | 1.3% | 1. Site tripped offline on 06/23 at 10:00 and back online on 06/24 at 09:15. | 1. SR086759
Chelsea | MA | 177136.5 | 175855.2 | 1281.3 | 0.7286% | 168267.4 | 8869.1 | 5.271% | 1. Site tripped offline on 06/09 at 08:45 and back online on 06/10 at 08:30. | 1. SR085784
Hamilton Landfill | MA | 131991.3 | 142585.8 | -10594.5 | -7.43% | 0 | 131991.3 |  | 1. Site was offline on 06/18 from 05:00 to 12:30. 2. Site was offline on 06/28 from 05:00 to 15:15. | 1. SR086350 2. SR087062
Holliston | MA | 250689.5 | 308244.8 | -57555.3 | -18.67% | 283046.1 | -32356.6 | -11.43% | 1. Inverter 2 primary unit tripped offline on 06/02 at 11:39 and back online on 06/25 at 15:30. 2. Site tripped offlline on 06/22 at 16:30 and back online on 06/24 at 07:30 | 1. SR085537 2. SR086659
Natick HS - Carports | MA | 95065.9 | 108597.8 | -13531.9 | -12.46% | 0 | 95065.9
Norton | MA | 0 | 0 | 0 |  | 602812.2 | -602812.2 | -100% | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 81554 | 69072.1 | 12481.9 | 18.07% | 84844 | -3290 | -3.878% | 1. Site was offline on 06/03 from 06:45 to 16:30. 2. Site tripped offline on 06/14 at 12:15 and back online on 06/15 at 11:30. 3. Inverter 9 derated about 3kW during high irradiance days from 05/25 to 06/13 | 1. SR085464 2. SR086251 3. SR085423
Shirley Bartkus | MA | 143257.5 | 111757.1 | 31500.4 | 28.19% | 145881 | -2623.5 | -1.798% | 1. Inverter 3 dropped 1 string on 4/23 and underproducing 5kW since then, some of the modules need to be replaced | 1. SR083810, SR081044
Stoughton | MA | 125646 | 70073.36 | 55572.64 | 79.31% | 112524.1 | 13121.9 | 11.66%
Wellfleet Landfill | MA | 153068.9 | 157080.25 | -4011.35 | -2.554% | 0 | 153068.9 |  | 1. Site was offline from 00:15 to 12:30 on 06/09 | 1. SR085770
Wilmington Garage & Building 7 | MA | 180680.625 | 180584 | 96.625 | 0.05351% | 177507.4 | 3173.225 | 1.788%
Woburn | MA | 258268 | 246417.7 | 11850.3 | 4.809% | 249757.7 | 8510.3 | 3.407%
Friendship Solar 1 | MD | 568811 | 606807.3 | -37996.3 | -6.262% | 579285 | -10474 | -1.808%
Friendship Solar 2 | MD | 572191 | 606266.8 | -34075.8 | -5.621% | 574494.1 | -2303.1 | -0.4009%
101 Carnegie Center | NJ | 214712.21 | 272074.49 | -57362.28 | -21.08% | 0 | 214712.21 |  | 1. Site is offline from 08:45AM to 19:45 on 06/22 due to planned outage. 2. Inverter 8 is underperforming approximately 5kW from 10/21/23. | 1. SR086633 2. SR087088
302 Carnegie Center | NJ | 96003.48 | 100373.678 | -4370.198 | -4.354% | 0 | 96003.48
510 Carnegie Center | NJ | 245994 | 293443.4 | -47449.4 | -16.17% | 0 | 245994 |  | 1. Inverter 25 tripped offline at 07:30AM on 06/09 and back online at 13:30 on 06/10. | 1. SR085777
701 Carnegie Center | NJ | 191178.74 | 234499.9 | -43321.16 | -18.47% | 0 | 191178.74 |  | 1. Inverter 6 is offline from 07:45AM to 14:15 on 06/03. | 1. SR085476
Hudson County Correction | NJ | 272727.7539 | 238986.7 | 33741.0539 | 14.12% | 248851.5 | 23876.2539 | 9.595%
ER Bison Solar | PA | 247759 | 0 | 247759 |  | 250270 | -2511 | -1.003% | 1. Inverter 9 tripped offline on 06/09 at 16:00 and back online on 06/12 at 07:00. 2. Inverter 5 tripped offline on 06/14 at 15:00 and back online and back online on 06/15 at 05:30 am. 3. Inverter 1 is underperforming by 16kW, inverter 2 is underperforming by 24kW, inverter 3 is underperforming by 15kW, inverter 4 is underperforming by 8kW, inverter 5 is underperforming by 9kW, inverter 9 is underperforming by 6kW for whole month. | 1. SR085790 2. SR086252 3. SR087390
Danville | IL | 383434.9 | 0 | 383434.9 |  | 0 | 383434.9 |  | 1. Site tripped offline at 4:45PM on 06/02 and back online at 11:15am on 06/03 | 1. SR085426

## Jul
Greenbacker Capital |  |  | 205961.173 |  |  | July Actual v. Forecasted
Total |  | 4928677.4122 | 4244198.5996 | 684478.8126 | 16.13% | 3834432.21 | 1094245.2022 | 28.54%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 19091.4375 | 17829.29 | 1262.1475 | 7.079% | 21735.09 | -2643.6525 | -12.16%
15 Walpole Park South | MA | 69736 | 66155.9 | 3580.1 | 5.412% | 76574.98 | -6838.98 | -8.931%
19 Walpole Park South | MA | 44155.25 | 40683.95 | 3471.3 | 8.532% | 48879.64 | -4724.39 | -9.665%
23 Walpole Park South | MA | 60236.25 | 54067.47 | 6168.78 | 11.41% | 64298.42 | -4062.17 | -6.318%
24 Walpole Park South | MA | 82594.5 | 76286.25 | 6308.25 | 8.269% | 98729.37 | -16134.87 | -16.34% | 1.Inverter 10 tripped offline at 16:30 from 06/18. Inverter is being RMA'd | 1.SR086410,SR089997
25 Walpole Park South | MA | 85519.25 | 81530.64 | 3988.61 | 4.892% | 99850.74 | -14331.49 | -14.35% | 1.Inverter 13 tripped offline at 12:15 from 7/16. Inverter power head RMA'd | 1.SR087756
3 Walpole Park South | MA | 113422.5 | 102295.1 | 11127.4 | 10.88% | 120718 | -7295.5 | -6.043% | 1.Inverter 8 tripped offline on 7/7 back online on 7/8 again offline at 07:30 on 7/10 back online at 12:15 | 1. SR087444
4 Walpole Park South | MA | 60974.5 | 56227.14 | 4747.36 | 8.443% | 66160.87 | -5186.37 | -7.839%
Brockton | MA | 101131 | 87786.84 | 13344.16 | 15.2% | 110218.4 | -9087.4 | -8.245%
Canton | MA | 91329.877 | 83469.73 | 7860.147 | 9.417% | 108826.7 | -17496.823 | -16.08% | 1. Inverters 7 and 11 are derating from 09:14AM from 7/1 | 1. SR087210
Chelsea | MA | 165811.5 | 160275.2 | 5536.3 | 3.454% | 174521.4 | -8709.9 | -4.991%
Hamilton Landfill | MA | 137045.289 | 144810.045 | -7764.756 | -5.362% | 0 | 137045.289
Holliston | MA | 247839.5 | 288374.2 | -40534.7 | -14.06% | 290634.9 | -42795.4 | -14.72% | 1.Inverter 6 primary unit is offline from 06:00 to 11:44 on 7/10 2.nverter 6 primary unit is offline and reporting isolation fault. Inverter 10 primary unit tripping on & off from 07/11 Inverter 1 right unit having multiple tripping from 02/03 Inverter 11 left unit & 9 right unit tripping on & off from 07/26 | 1.SR087550 2.SR089086
Natick HS - Carports | MA | 88406.8865 | 100367.912 | -11961.0255 | -11.92% | 0 | 88406.8865
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 86465 | 73107.22 | 13357.78 | 18.27% | 89737 | -3272 | -3.646% | 1.Site offline from 03:15 to 08:30 on 7/12 | 1.SR087608
Shirley Bartkus | MA | 136715 | 9635.973 | 127079.027 | 1319% | 156687 | -19972 | -12.75% | 1.Weather Station (Standard) (RMA9664) lost communication from 7/5 2.Inverter 12 tripped offline at 13:00 on 7/3 3.Inverter 3 tripped offline at 13:00 on 7/14 4.Inverter 26 offline from 7/15 resolved on 7/26 5.Inverter 31 offline from 7/15 resolved on 7/26 | 1. SR087248 2.SR087360 3.SR087660 4. SR087825 5.SR087826
Stoughton | MA | 113672 | 64863.27 | 48808.73 | 75.25% | 118688.8 | -5016.8 | -4.227%
Wellfleet Landfill | MA | 139921.972 | 158770.903 | -18848.931 | -11.87% | 0 | 139921.972
Wilmington Garage & Building 7 | MA | 174159 | 170814.7 | 3344.3 | 1.958% | 191642.4 | -17483.4 | -9.123%
Woburn | MA | 245398 | 232784.8 | 12613.2 | 5.418% | 273136.8 | -27738.8 | -10.16%
Friendship Solar 1 | MD | 528542 | 561993.3 | -33451.3 | -5.952% | 609693.3 | -81151.3 | -13.31%
Friendship Solar 2 | MD | 531127 | 560757.9 | -29630.9 | -5.284% | 594201.4 | -63074.4 | -10.61%
101 Carnegie Center | NJ | 205961.173 | 249801 | -43839.827 | -17.55% | 0 | 205961.173 |  | 1.Inverter 8 underperforming by 5kW since 10/21/23. | 1.SR087088
302 Carnegie Center | NJ | 89551.0416 | 91839.8236 | -2288.782 | -2.492% | 0 | 89551.0416
510 Carnegie Center | NJ | 231135.421 | 267595.589 | -36460.168 | -13.63% | 0 | 231135.421
701 Carnegie Center | NJ | 177506.875 | 211282.054 | -33775.179 | -15.99% | 0 | 177506.875
Hudson County Correction | NJ | 265275.9416 | 230792.4 | 34483.5416 | 14.94% | 254490 | 10785.9416 | 4.238% | 1.inverter 1 is underperforming by 16kW. inverter 2 is underperforming by 24kW. inverter 3 is underperforming by 15kW. inverter 4 is underperforming by 8kW. inverter 5 is underperforming by 9kW. inverter 9 is underperforming by 6kW. 2.Inverter 5 tripped offline at 15:45 on 7/8 | 1. SR087390 2.SR087483
ER Bison Solar | PA | 247793 | 0 | 247793 |  | 265007 | -17214 | -6.496%
Danville | IL | 388160.248 | 0 | 388160.248 |  | 0 | 388160.248

## Aug
Greenbacker Capital |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 4410666.1471 | 3798667.9682 | 611998.1789 | 16.11% | 3469680.92 | 940985.2271 | 27.12% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 17857.4375 | 16787.54 | 1069.8975 | 6.373% | 20029.88 | -2172.4425 | -10.85%
15 Walpole Park South | MA | 65125 | 61341.47 | 3783.53 | 6.168% | 70499.34 | -5374.34 | -7.623%
19 Walpole Park South | MA | 41042.25 | 38018.07 | 3024.18 | 7.955% | 44969.24 | -3926.99 | -8.733%
23 Walpole Park South | MA | 55914.5 | 50585.49 | 5329.01 | 10.53% | 59319.64 | -3405.14 | -5.74%
24 Walpole Park South | MA | 76628.5 | 70634.44 | 5994.06 | 8.486% | 91162.77 | -14534.27 | -15.94% | 1.Inverter 10 tripped offline at 16:30 from 06/18. Inverter is being RMA'd | 1.SR086410,SR089997
25 Walpole Park South | MA | 75523.5 | 75766.92 | -243.42 | -0.3213% | 92176.45 | -16652.95 | -18.07% | 1.Inverter 13 tripped offline at 12:15 from 7/16. Inverter power head RMA'd 2. Inverters 9, 10, 11 & 12 tripped offline from 8/16 and back online on 8/20 | 1.SR087756 2.SR089170
3 Walpole Park South | MA | 104716 | 96742.95 | 7973.05 | 8.241% | 109945 | -5229 | -4.756% | 1. Inverters 1 and 9 tripped offline 12:45 to 18:30 on 8/26 and again inverter tripped offline from 09:00 to 15:00 on 8/30 | 1.SR089564
4 Walpole Park South | MA | 57269.5 | 53014.98 | 4254.52 | 8.025% | 61015.6 | -3746.1 | -6.14%
Brockton | MA | 95309 | 83349.84 | 11959.16 | 14.35% | 100764.3 | -5455.3 | -5.414% | 1.Inverter 5 is underperforming approximately 3-4kW compared to inverter 4 since 08/13. | 1. SR089336
Canton | MA | 91571.5 | 82805.97 | 8765.53 | 10.59% | 100465.4 | -8893.9 | -8.853%
Chelsea | MA | 154403.5 | 150065.9 | 4337.6 | 2.89% | 162292.2 | -7888.7 | -4.861%
Hamilton Landfill | MA | 122906.611 | 132969.01 | -10062.399 | -7.567% | 0 | 122906.611 |  | 1.Inverters 10 and 12 are being RMA'd from 8/28 | 1.SR089813
Holliston | MA | 224205.9347 | 253866.2 | -29660.2653 | -11.68% | 266159 | -41953.0653 | -15.76% | 1.Inverter 2 right unit offline from 8/13 and back online on 8/15 2.nverter 6 primary unit is offline and reporting isolation fault. Inverter 10 primary unit tripping on & off from 07/11 Inverter 1 right unit having multiple tripping from 02/03 Inverter 11 left unit & 9 right unit tripping on & off from 07/26 resloved on 8/23 3.Inverter 6 right unit tripped offline at 16:25 from 8/23 | 1.SR089084 2.SR089086 3. SR090028
Natick HS - Carports | MA | 78591.845 | 89392.6255 | -10800.7805 | -12.08% | 0 | 78591.845
Norton | MA | [7 empty] | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 75293.5 | 68533.02 | 6760.48 | 9.865% | 80844 | -5550.5 | -6.866%
Shirley Bartkus | MA | 124543 |  |  |  | 138832 | -14289 | -10.29% | 1.Inverter 03 under preforming compared to its peer 2.Weather Station (Standard) (RMA9664) lost communication from 7/5 | 1.SR089560 2.SR087248
Stoughton | MA | 107686.5 | 59376.27 | 48310.23 | 81.36% | 110489.8 | -2803.3 | -2.537%
Wellfleet Landfill | MA | 138314.825 | 158181.489 | -19866.664 | -12.56% | 0 | 138314.825
Wilmington Garage & Building 7 | MA | 151451.75 | 148980.7 | 2471.05 | 1.659% | 171021.8 | -19570.05 | -11.44% | 1.Inverter 4 offline on 8/17 2.Inverter 1 tripped offline from 8/22 and back online on 8/26 at 13:45 | 1.SR089193 2.SR089410
Woburn | MA | 220309 | 212165.6 | 8143.4 | 3.838% | 249057.6 | -28748.6 | -11.54%
Friendship Solar 1 | MD | 425879 | 489395.6 | -63516.6 | -12.98% | 537272.2 | -111393.2 | -20.73% | 1.Site offline from 8/10 at from 20:15 and back online on 8/13 2. All inverters have tripped offline from 07:00 to 09:45 on 8/19 | 1. SR088888 2.SR089251
Friendship Solar 2 | MD | 426758 | 489129.2 | -62371.2 | -12.75% | 534863.4 | -108105.4 | -20.21% | 1.Site offline from 8/10 at from 20:15 and back online on 8/13 2. All inverters have tripped offline from 07:00 to 09:45 on 8/19 | 1.SR088887 2.SR089251
101 Carnegie Center | NJ | 188238 | 223715 | -35477 | -15.86% | 0 | 188237.967 |  | 1.Inverter 8 underperforming by 5kW since 10/21/23. | 1.SR087088
302 Carnegie Center | NJ | 81616.8418 | 85471.8377 | -3854.9959 | -4.51% | 0 | 81616.8418
510 Carnegie Center | NJ | 207380.217 | 234190.6 | -26810.383 | -11.45% | 0 | 207380.217
701 Carnegie Center | NJ | 160176.685 | 188370.346 | -28193.661 | -14.97% | 0 | 160176.685
Hudson County Correction | NJ | 218796.2191 | 185816.9 | 32979.3191 | 17.75% | 227257.3 | -8461.0809 | -3.723%
ER Bison Solar | PA | 218165 | 0 | 218165 |  | 241244 | -23079 | -9.567% | 1.inverter 2 is underperforming by 6 kW. | 1.SR089719
Danville | IL | 404992.531 | 0 | 404992.531 |  | 0 | 404992.531 |  | 1.Inverter 16 tripped offline multiple days at 08:30AM on 9/3 | 1.SR089440

## Sep
Greenbacker Capital |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 3642435.1936 | 3048091.4931 | 594343.7005 | 19.5% | 2829061.93 | 813373.2636 | 28.75%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 14863.75 | 13281.19 | 1582.56 | 11.92% | 16932.91 | -2069.16 | -12.22%
15 Walpole Park South | MA | 54408.5 | 50967.48 | 3441.02 | 6.751% | 59450.29 | -5041.79 | -8.481%
19 Walpole Park South | MA | 33685.375 | 30977.28 | 2708.095 | 8.742% | 37895.3 | -4209.925 | -11.11%
23 Walpole Park South | MA | 46212.5 | 41125.52 | 5086.98 | 12.37% | 49688.05 | -3475.55 | -6.995% | 1.Inverters 1,5 tripped offline at 10:00 on 9/6 and back onlin eon 9/7 | 1. SR090045, SR090046
24 Walpole Park South | MA | 63072.28 | 55740.7 | 7331.58 | 13.15% | 76431.91 | -13359.63 | -17.48% | 1.Inverter 10 tripped offline at 16:30 from 06/18. Inverter is being RMA'd | 1.SR086410,SR089997
25 Walpole Park South | MA | 64038.8863 | 62358.55 | 1680.3363 | 2.695% | 77406.2 | -13367.3137 | -17.27% | 1.Inverter 13 tripped offline at 12:15 from 7/16. Inverter power head RMA'd | 1.SR087756
3 Walpole Park South | MA | 84852.14 | 77923.67 | 6928.47 | 8.891% | 91581.91 | -6729.77 | -7.348% | 1.Inverters 1,9 are tripped offline from 13:30 to 17:40 on 9/3 | 1.SR089564
4 Walpole Park South | MA | 47370 | 43897.53 | 3472.47 | 7.91% | 51480.72 | -4110.72 | -7.985%
Brockton | MA | 78192 | 66932.96 | 11259.04 | 16.82% | 82302.7 | -4110.7 | -4.995% | 1.Inverter 5 is underperforming approximately 3-4kW compared to inverter 4 since 08/13. | 1. SR089336
Canton | MA | 75471.5 | 68742.17 | 6729.33 | 9.789% | 82235.1 | -6763.6 | -8.225% | 1.Inverters 7 and 11 are derating from 09:14AM from 7/1 2.Inverter 3 offline from 9/29 | 1. SR087210 2. SR091356
Chelsea | MA | 132514 | 129038.8 | 3475.2 | 2.693% | 134327.4 | -1813.4 | -1.35%
Hamilton Landfill | MA | 109243.283 | 116698.858 | -7455.575 | -6.389% | 0 | 109243.283 |  | 1.Inverters 10 and 12 are being RMA'd from 8/28 | 1.SR089813
Holliston | MA | 179111.0653 | 200400.5 | -21289.4347 | -10.62% | 210212.1 | -31101.0347 | -14.8% | 1.Inverter 6 right unit back online on 9/9 at 16:34 2.Site offline from 9/7 at 07:15 and back online on 9/8 at 09:00 3.Inverter 10 primary unit is tripping on and off. Inverter 11 left unit is tripping on and off. Inverter 9 right unit is derating | 1. SR090028 2. SR090086 3.SR090413,SR089086
Natick HS - Carports | MA | 64629.2353 | 74301.6463 | -9672.411 | -13.02% | 0 | 64629.2353
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 70383.5 | 68190.97 | 2192.53 | 3.215% | 71143 | -759.5 | -1.068%
Shirley Bartkus | MA | 114572.3866 |  |  |  | 107941 | 6631.3866 | 6.144% | 1.Inverter 27 offline from 9/5 2.Weather station back online on 9/8 | 1. SR089983 2.SR087248
Stoughton | MA | 86346 | 49438.1 | 36907.9 | 74.65% | 91922.54 | -5576.54 | -6.067%
Wellfleet Landfill | MA | 107157.577 | 120207.977 | -13050.4 | -10.86% | 0 | 107157.577 |  | 1.Site offline due to utility outage from 9/25 at 08:00 back online on 9/26 at 11:15 | 1.SR091176
Wilmington Garage & Building 7 | MA | 128423.875 | 128471.8 | -47.925 | -0.0373% | 135273.1 | -6849.225 | -5.063%
Woburn | MA | 190326 | 187777.4 | 2548.6 | 1.357% | 203205.8 | -12879.8 | -6.338%
Friendship Solar 1 | MD | 348185 | 367263.5 | -19078.5 | -5.195% | 450070.8 | -101885.8 | -22.64% | 1.Inverter 16 started late to start frequent days | 1.SR090156,SR091498
Friendship Solar 2 | MD | 349504 | 368615.3 | -19111.3 | -5.185% | 418145.8 | -68641.8 | -16.42%
101 Carnegie Center | NJ | 147023.477 | 170510 | -23486.523 | -13.77% | 0 | 147023.477 |  | 1.Inverter 8 underperforming by 5kW since 10/21/23. | 1.SR087088
302 Carnegie Center | NJ | 64135.9171 | 67835.3478 | -3699.4307 | -5.454% | 0 | 64135.9171
510 Carnegie Center | NJ | 162577.486 | 185052.04 | -22474.554 | -12.14% | 0 | 162577.486
701 Carnegie Center | NJ | 125488.172 | 148684.304 | -23196.132 | -15.6% | 0 | 125488.172
Hudson County Correction | NJ | 178555.541 | 153657.9 | 24897.641 | 16.2% | 186443.3 | -7887.759 | -4.231%
ER Bison Solar | PA | 183969 | 0 | 183969 |  | 194972 | -11003 | -5.643% | 1.inverter 1 down a string from 9/9/24 | 1.SR091298
Danville | IL | 338122.747 | 0 | 338122.747 |  | 0 | 338122.747 |  | 1.Inverter 16 tripped offline multiple days at 08:30AM on 9/3 2.Inverters 3. 5, 11, 12 are underperforming 15kW down each compared to its peers Inverters 9, 10, 15, 13 are underperforming 8kW down each compared to its peers Inverters 8 is underperforming 23kW compared to its peers Inverters 14 is underperforming 30kW compared to its peers. 3.Site tripped offline. UPS is discharging on 9/24 later Remotely closed | 1.SR089848 2.SR090300 3. SR091120

## Oct
Greenbacker Capital |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 3632522.3684 | 3073267.94 | 559254.4284 | 18.2% | 2216750.67 | 1415771.6984 | 63.87%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 14023 | 12414.51 | 1608.49 | 12.96% | 12504.55 | 1518.45 | 12.14%
15 Walpole Park South | MA | 51644.4808 | 48913.33 | 2731.1508 | 5.584% | 43473.76 | 8170.7208 | 18.79%
19 Walpole Park South | MA | 30950.625 | 29759.26 | 1191.365 | 4.003% | 27701.17 | 3249.455 | 11.73%
23 Walpole Park South | MA | 43257.2667 | 38990.8 | 4266.4667 | 10.94% | 35974.93 | 7282.3367 | 20.24%
24 Walpole Park South | MA | 56027.97 | 51542.75 | 4485.22 | 8.702% | 55092.08 | 935.89 | 1.699% | 1. Inverter 10 tripped offline at 16:30 from 06/18. Inverter is being RMA'd | 1.SR086410,SR089997
25 Walpole Park South | MA | 58890.1137 | 59847.1 | -956.9863 | -1.599% | 56143.87 | 2746.2437 | 4.891% | 1. Inverter 13 tripped offline at 12:15 from 7/16. Inverter power head is being RMA'd | 1.SR087756, SR089170
3 Walpole Park South | MA | 77435.3998 | 74933.85 | 2501.5498 | 3.338% | 65249.59 | 12185.8098 | 18.68% | 1. Inverter 9 tripped offline at 7:00AM and back online at 11:30AM on 10/07/2024 | 1. SR089564
4 Walpole Park South | MA | 44496.5 | 42861.65 | 1634.85 | 3.814% | 37815.55 | 6680.95 | 17.67%
Brockton | MA | 71270.5 | 62179.72 | 9090.78 | 14.62% | 61822.74 | 9447.76 | 15.28% | 1. Inverter 5 is underperforming approximately 3-4kW compared to inverter 4 since 08/13. 2. Inverter 1 is underperforming approximately 5KW from 09/16. Inverter 13 is underperforming approximately 5KW from 09/30. 3. Inverter 1 tripped offline at 14:45 on 10/31 and back online at 9:15 on 11/01. | 1. SR089336 2. SR091976 3. SR092851, SR091976
Canton | MA | 66871.75 | 64774.27 | 2097.48 | 3.238% | 64314.41 | 2557.34 | 3.976% | 1. Inverter 3 tripped offline at 17:15 from 09/29 and back online at 11:45 on 10/04. | 1. SR091356
Chelsea | MA | 110221.5 | 108777.2 | 1444.3 | 1.328% | 96186.27 | 14035.23 | 14.59% | 1. Inverter A4 is offline on 10/24/2024 and back online on 10/25/2024. 2. The site was offline from 8:30 AM to 10:45 AM on 10/23. However, inverters B6 and C1 remained offline and came back online on 10/24.. | 1. SR092522 2. SR092475
Hamilton Landfill | MA | 99744.931 | 109771.1 | -10026.169 | -9.134% | 0 | 99744.931 |  | 1. Inverter 10 is back online on 10/08/2024 2. Inverter 12 is back online on 10/08/2024 | 1. SR089813 2. SR089674
Holliston | MA | 165820 | 157542.4 | 8277.6 | 5.254% | 162647.8 | 3172.2 | 1.95% | 1. Inverter 10 primary unit is tripping on and off and back to normal on 10/23/2024 Inverter 11 left unit is tripping on and off back to normal on 10/23/2024 Inverter 9 right unit is derating back to normal on 10/23/2024 2. Inverter 11 primary unit tripped offline from 10/26/2024 3. Inverter 2 right unit offline on 10/29/2024 and back online on 10/30/2024 | 1. SR090413 2. SR092625 3. SR092758
Natick HS - Carports | MA | 52924.9 | 62779.5 | -9854.6 | -15.7% | 0 | 52924.9
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 68250 | 73054.99 | -4804.99 | -6.577% | 62250 | 6000 | 9.639%
Shirley Bartkus | MA | 102182.1134 | 0 | 102182.1134 |  | 101613 | 569.1134 | 0.5601% | 1.Inverter 27 offline from 9/5 | 1. SR089983
Stoughton | MA | 83200 | 48593.09 | 34606.91 | 71.22% | 69398.15 | 13801.85 | 19.89%
Wellfleet Landfill | MA | 97015.1 | 114624.6 | -17609.5 | -15.36% | 0 | 97015.1
Wilmington Garage & Building 7 | MA | 104351.125 | 108112.1 | -3760.975 | -3.479% | 102511.6 | 1839.525 | 1.794%
Woburn | MA | 164724.5 | 177345 | -12620.5 | -7.116% | 155138.2 | 9586.3 | 6.179% | 1. Inverter 17 is underperforming 4kW compared to its peers | 1. SR092567
Friendship Solar 1 | MD | 420994 | 438486.9 | -17492.9 | -3.989% | 337101.5 | 83892.5 | 24.89% | 1. Inverter 16 started late to start frequent days. 2. Inverter 2 underproducing 4kW down compared to peers. | 1.SR091498 2. SR09182
Friendship Solar 2 | MD | 419963 | 448792.8 | -28829.8 | -6.424% | 370407.4 | 49555.6 | 13.38% | 1. Inverters from 1, 6 to 16 and underproducing 10kW each during peak production hours. Possibly due to seasonal shading. | 1. SR092109
101 Carnegie Center | NJ | 143361.6 | 178996.42 | -35634.82 | -19.91% | 0 | 143361.6 |  | 1. Inv 8 is underperforming by 5kW down compared to its peers since 10/21/23. | 1. SR087088
302 Carnegie Center | NJ | 64265.4 | 76063.8 | -11798.4 | -15.51% | 0 | 64265.4
510 Carnegie Center | NJ | 160818.8 | 195840.8 | -35022 | -17.88% | 0 | 160818.8 |  | 1. Inverter 07 tripped offline at 16:30 on 10/18 and back online at 10:00 on 10/22. | 1. SR092323
701 Carnegie Center | NJ | 121714.1 | 152234.3 | -30520.2 | -20.05% | 0 | 121714.1
Hudson County Correction | NJ | 169975.893 | 136035.7 | 33940.193 | 24.95% | 141559.1 | 28416.793 | 20.07%
ER Bison Solar | PA | 208020 | 0 | 208020 |  | 157845 | 50175 | 31.79% | 1. Inverter 1 is underperforming by 6 kW down from 9/9 to 10/29. 2. Inverter 2 is offline from 10/27 to throughout the month. | 1. SR091298 2. SR092627
Danville | IL | 360107.8 | 0 | 360107.8 |  | 0 | 360107.8 |  | 1. Inverter 3 underperforming by 13 kW from 10/16 to 10/22. Inverter 6 underperforming by 5 kW from 10/16 to 10/22. Inverter 8 underperforming by 5 kW from 10/16 to 10/22. Inverter 9 underperforming by 13 kW from 10/16 to 10/22. Inverter 10 underperforming by 13 kW from 10/16 to 10/22. Inverter 11 underperforming by 16 kW from 10/16 to 10/22. Inverter 12 underperforming by 4 kW from 10/16 to 10/22. Inverter 13 underperforming by 4 kW from 10/16 to 10/22. Inverter 14 underperforming by 12 kW from 10/16 to 10/22. 2. Site tripped offline at 10:45AM on 10/31 and back online at 12PM on 10/31. | 1. SR092204 2. SR092831

## Nov
Greenbacker Capital |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 2279259.2774 | 2031084.739 | 248174.5384 | 12.22% | 1532089.867 | 747169.4104 | 48.77%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 9569.3125 | 9245.219 | 324.0935 | 3.506% | 8517.777 | 1051.5355 | 12.35%
15 Walpole Park South | MA | 34951.5192 | 35438.58 | -487.0608 | -1.374% | 28152.47 | 6799.0492 | 24.15%
19 Walpole Park South | MA | 20245.875 | 21343.67 | -1097.795 | -5.143% | 18313.55 | 1932.325 | 10.55%
23 Walpole Park South | MA | 29424.2333 | 28537.26 | 886.9733 | 3.108% | 23645.35 | 5778.8833 | 24.44%
24 Walpole Park South | MA | 36985.25 | 25616.24 | 11369.01 | 44.38% | 36397.68 | 587.57 | 1.614% | 1.Inverter 10 tripped offline at 16:30 on 06/18 and was being RMA'd from 10/17 2. Weather station is reporting erroneous values. Observed from Nov 2023. | 1.SR089997 2.SR080044
25 Walpole Park South | MA | 39494.25 | 43289.23 | -3794.98 | -8.767% | 37410.08 | 2084.17 | 5.571% | 1. Inverter 13 tripped offline at 12:15 from 7/16. Inverter power head is being RMA'd | 1.SR087756, SR089170
3 Walpole Park South | MA | 49096.1343 | 52686.58 | -3590.4457 | -6.815% | 43513.68 | 5582.4543 | 12.83% | 1.Inverter 9 tripped offline at 10:00AM on 11/02/2024 and Inverter is being RMA'd | 1. SR089564
4 Walpole Park South | MA | 29528.75 | 31439.16 | -1910.41 | -6.077% | 24959.52 | 4569.23 | 18.31%
Brockton | MA | 50153.5 | 44422.29 | 5731.21 | 12.9% | 43974.27 | 6179.23 | 14.05% | 1. Site tripped offline at 10:00AM and back online at 12:15PM on 11/27/24. 2. Inverter 1 tripped offline at 14:45 on 10/31 and back online at 9:15 on 11/01. | 1. SR093661 2. SR091976, SR092851
Canton | MA | 45921.25 | 48489.28 | -2568.03 | -5.296% | 40545.79 | 5375.46 | 13.26%
Chelsea | MA | 77336.5 | 82258.34 | -4921.84 | -5.983% | 66233.47 | 11103.03 | 16.76% | 1. Inverter A4 is offline from 11/04/2024 and Inverter is being RMA'd. 2. Inverter D1 is offline on 11/13 and back online on 11/14 but inverter starts consistently late everyday. 3. Invverter B6 is offline on 11/19 and back online on 11/20 | 1. SR092522, SR092971 2. SR093218 3. SR093420
Hamilton Landfill | MA | 72413.4 | 86509.6 | -14096.2 | -16.29% | 0 | 72413.4
Holliston | MA | 112291 | 97652.94 | 14638.06 | 14.99% | 102832.9 | 9458.1 | 9.198% | 1. Inverter 11 primary unit tripped offline from 10/26/2024 and back online at 14:20 on 11/01/2024 | 1. SR092625
Natick HS - Carports | MA | 34070.6 | 42921 | -8850.4 | -20.62% | 0 | 34070.6
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 50293.5 | 56229.06 | -5935.56 | -10.56% | 38805 | 11488.5 | 29.61%
Shirley Bartkus | MA | 78004.5 | 0 | 78004.5 |  | 72691 | 5313.5 | 7.31% | 1.Inverter 27 offline from 9/5 | 1.SR089983
Stoughton | MA | 59576.94 | 35072.6 | 24504.34 | 69.87% | 46600.99 | 12975.95 | 27.84%
Wellfleet Landfill | MA | 67904.3 | 64534.7 | 3369.6 | 5.221% | 0 | 67904.3
Wilmington Garage & Building 7 | MA | 68019.75 | 77126.07 | -9106.32 | -11.81% | 66156.64 | 1863.11 | 2.816%
Woburn | MA | 118114.1255 | 141082.1 | -22967.9745 | -16.28% | 97594.5 | 20519.6255 | 21.03% | 1. Inverter 17 is offline on 11/26 and back online at 09:45AM on 11/27/24 2.Inverter 17 is underperforming 4kW compared to its peers | 1. SR093631 2.SR092567
Friendship Solar 1 | MD | 264558 | 269203.6 | -4645.6 | -1.726% | 269440.6 | -4882.6 | -1.812%
Friendship Solar 2 | MD | 256387 | 280553.8 | -24166.8 | -8.614% | 265739.7 | -9352.7 | -3.519% | 1.Inverter 2.6 was offline on 11/15/24 and back online at 07:00 on 11/16/24 .And Inverter 2.6 delayed for production at 10:30 on 11/20/24.Inverter 2.6 was offline on 11/22, 11/23 , /11/24 and back online at 14:45 on 11/25. 2. Inverters from 1, 6 to 16 and underproducing 10kW each during peak production hours. Possibly due to seasonal shading. | 1.SR093284 2. SR092109
101 Carnegie Center | NJ | 85991.6 | 112281.6 | -26290 | -23.41% | 0 | 85991.6 |  | 1. Inverter 8 is underperforming by 5kW down compared to its peers since 10/21/23. | 1. SR087088
302 Carnegie Center | NJ | 38817.1 | 46559.5 | -7742.4 | -16.63% | 0 | 38817.1
510 Carnegie Center | NJ | 94643.3 | 120387 | -25743.7 | -21.38% | 0 | 94643.3 |  | 1. Inverter 7 tripped offline at 15:30 on 11/03 and back online at 15:00 on 11/04. | 1. SR092925
701 Carnegie Center | NJ | 73386.1 | 91659.22 | -18273.12 | -19.94% | 0 | 73386.1
Hudson County Correction | NJ | 99282.2735 | 86546.1 | 12736.1735 | 14.72% | 97014.9 | 2267.3735 | 2.337% | 1. Site tripped offline at 16:00 EST on 11/28 to throughout the month. | 1. SR093712
ER Bison Solar | PA | 116824 | 0 | 116824 |  | 103550 | 13274 | 12.82% | 1. Inverter 2 is offline from 10/27 and back online at 12:30 EST on 11/15. | 1. SR092627
Danville | IL | 165975.214 | 0 | 165975.214 |  | 0 | 165975.214 |  | 1. Inverter 10 underperforming. Inverter 12 underperforming. Inverter 11 underperforming. 2. Inverter 11 offline on 11/18 and back online at 09:45 AM on 11/19 ,again went offline in 11/20 and back online at 11:00 AM on 11/20 and again went offline on 11/21 and back online at 10:45AM on 11/21. 3. Inverter 3 tripped offline at 10:15AM on 11/16 and back online on 11/18. | 1. SR092997 2. SR092997,SR093368 3. SR093341,SR092997

## Dec
Greenbacker Capital |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 1509733.4706 | 1510622.451 | -888.9804 | -0.05885% | 1076691.944 | 433041.5266 | 40.22%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 5096.625 | 6414.972 | -1318.347 | -20.55% | 5945.394 | -848.769 | -14.28%
15 Walpole Park South | MA | 17557 | 27043.57 | -9486.57 | -35.08% | 17602.65 | -45.65 | -0.2593%
19 Walpole Park South | MA | 9992 | 14071.68 | -4079.68 | -28.99% | 12340.26 | -2348.26 | -19.03%
23 Walpole Park South | MA | 15475.5 | 19954.64 | -4479.14 | -22.45% | 15510.57 | -35.07 | -0.2261%
24 Walpole Park South | MA | 19603.75 | 9079.418 | 10524.332 | 115.9% | 24209.72 | -4605.97 | -19.03% |  | 1.SR089997 2.SR080044
25 Walpole Park South | MA | 20653.25 | 26000 | -5346.75 | -20.56% | 24141.61 | -3488.36 | -14.45% | 1.Inverter 13 being RMA'd from 08/20 | 1.SR095220
3 Walpole Park South | MA | 26900.1384 | 39293.77 | -12393.6316 | -31.54% | 30262.15 | -3362.0116 | -11.11% | 1.Inverter 1 tripped offline at 12:23 on 12/31 and back online at 14:30 on 12/31. 2.Inverter 9 being RMA'D from 11/19. | 1.SR095197 2.SR093404
4 Walpole Park South | MA | 14513.75 | 24433.44 | -9919.69 | -40.6% | 16687.97 | -2174.22 | -13.03%
Brockton | MA | 30002.5 | 34869.66 | -4867.16 | -13.96% | 29239.57 | 762.93 | 2.609%
Canton | MA | 23120.25 | 28218.29 | -5098.04 | -18.07% | 26856.63 | -3736.38 | -13.91%
Chelsea | MA | 52130 | 63224.2 | -11094.2 | -17.55% | 47470.43 | 4659.57 | 9.816% | 1.Inverter A4 was offline from 06:35 on 12/01 and Inverter A4 being RMA'd from 12/02 and the Inverter was back online at 11:00 on 12/04. 2.Inverter B6 being RMA'd from 12/04 and the Inverter was producing as expected from 12/17. 3.Inverter B3 was not starting up in the morning and it turns on by noon and the Inverter has a hwastory of intermittent communication. Inverter B3 being RMA'd from 12/19 4.While technician wass on site Inverter C1 was offline from 10:15 to 12:00 on 12/04 5.While technician wass on site Inverter D2 was offline from 09:15 to 10:15on 12/04 6.Inverter D1 was offline on 12/06 and back online at 06:45 on 12/7 | 1.SR092971 2.SR094027 3.SR093500 4.SR094028 5.SR094024 6.SR093218
Hamilton Landfill | MA | 38870.9 | 69579.8 | -30708.9 | -44.13% | 0 | 38870.9
Holliston | MA | 67447 | 68752.31 | -1305.31 | -1.899% | 77039.05 | -9592.05 | -12.45% | 1. Inverter 6 right unit was tripped offline at 12:1PM on 12/17 and remains offline throughout the month. 2. Inverter 10 started communicating from 12/14. | 1.SR095142 2.SR092545
Natick HS - Carports | MA | 22432.7 | 33884.101 | -11451.401 | -33.8% | 0 | 22432.7
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site tripped offline on 04/01 at 16:00 and still offline. | 1. SR082974, SR084822
Palmer - Boston Rd. | MA | 31352.5 | 45910.32 | -14557.82 | -31.71% | 37188 | -5835.5 | -15.69%
Shirley Bartkus | MA | 49525.4422 | 0 | 49525.4422 |  | 45030 | 4495.4422 | 9.983% | 1.Inverter 34 was offline on 12/01 and back online at 12:15 on 12/03 and again tripped offline at 15:00 on 12/05 and back online at 14:30 on 12/17. 2.Inverter 31 tripped offline at 15:30 on 12/01 and back online at 12PM on 12/03. 3.Site tripped offline at 12:03AM and back online at 12:24PM on 12/23. 4.Inverter 12 was being RMA'D from 12/24. 5.Inverter 27 offline from 09/05. | 1.SR093749, SR094606 2.SR093783 3.SR095027 4.SR095058 5.SR089983
Stoughton | MA | 32854.06 | 33076.39 | -222.33 | -0.6722% | 32539.48 | 314.58 | 0.9668%
Wellfleet Landfill | MA | 42731.4 | 45898.6 | -3167.2 | -6.9% | 0 | 42731.4
Wilmington Garage & Building 7 | MA | 46886.125 | 60030.79 | -13144.665 | -21.9% | 46318.95 | 567.175 | 1.224% | 1. Inverter 12 was offline on 12/15 and back online on 12/16. Inverter again offline on 12/18 and remains offline throughtout the month. | 1.SR094678
Woburn | MA | 73809.3745 | 113581.1 | -39771.7255 | -35.02% | 62748.51 | 11060.8645 | 17.63% | 1.Site tripped offline at 16:30 on 12/11 and back online at 9:45 on 12/12. 2.Inverter 17 tripped offline at 8:30AM on 12/25 and remains offline through out the month. | 1.SR094441 2.SR095079
Friendship Solar 1 | MD | 194454 | 192021.4 | 2432.6 | 1.267% | 190976.5 | 3477.5 | 1.821%
Friendship Solar 2 | MD | 190230 | 204722.8 | -14492.8 | -7.079% | 187830.7 | 2399.3 | 1.277%
101 Carnegie Center | NJ | 59085.2 | 87333.9 | -28248.7 | -32.35% | 0 | 59085.2
302 Carnegie Center | NJ | 26838.5 | 35487.9 | -8649.4 | -24.37% | 0 | 26838.5
510 Carnegie Center | NJ | 60614.6 | 93371.2 | -32756.6 | -35.08% | 0 | 60614.6
701 Carnegie Center | NJ | 53242.2 | 69325.9 | -16083.7 | -23.2% | 0 | 53242.2
Hudson County Correction | NJ | 71263.2055 | 65042.3 | 6220.9055 | 9.564% | 72312.8 | -1049.5945 | -1.451% | 1. Site tripped offline at 16:00 EST on 11/28 and back online at 12:45 on 12/02. | 1.SR093712
ER Bison Solar | PA | 61829 | 0 | 61829 |  | 74441 | -12612 | -16.94%
Danville | IL | 151222.5 | 0 | 151222.5 |  | 0 | 151222.5

## Sites
Portfolio: | Greenbacker Capital
Site DAS Name | Site | State | Update | DAS
10 Walpole Park South [0664] | 10 Walpole Park South | MA | AEF | PowerTrack
15 Walpole Park South [0668] | 15 Walpole Park South | MA | AEF | PowerTrack
19 Walpole Park South [0670] | 19 Walpole Park South | MA | AEF | PowerTrack
23 Walpole Park South [0676] | 23 Walpole Park South | MA | AEF | PowerTrack
24 Walpole Park South [0667] | 24 Walpole Park South | MA | AEF | PowerTrack
25 Walpole Park South [0665] | 25 Walpole Park South | MA | AEF | PowerTrack
3 Walpole Park South [0666] | 3 Walpole Park South | MA | AEF | PowerTrack
4 Walpole Park South [0669] | 4 Walpole Park South | MA | AEF | PowerTrack
Brockton [0662] | Brockton | MA | AEF | PowerTrack
Canton [0672] | Canton | MA | AEF | PowerTrack
Chelsea [0663] | Chelsea | MA | AEF | PowerTrack
Hamilton MA Landfill | Hamilton Landfill | MA |  | InAccess
Holliston [0674] | Holliston | MA | AEF | PowerTrack
MA: Natick HS - Carports | Natick HS - Carports | MA |  | InAccess
Norton [0671] | Norton | MA | AEF | PowerTrack
Palmer - Boston Rd. [0637] | Palmer - Boston Rd. | MA | AEF | PowerTrack
Shirley Bartkus [0632] | Shirley Bartkus | MA | AEF | PowerTrack
Stoughton [0661] | Stoughton | MA | AEF | PowerTrack
MA: Wellfleet Landfill | Wellfleet Landfill | MA |  | InAccess
Wilmington Garage & Building 7 [0675] | Wilmington Garage & Building 7 | MA | AEF | PowerTrack
Woburn [0673] | Woburn | MA | AEF | PowerTrack
Friendship Solar 1 [0569] | Friendship Solar 1 | MD | AEF | PowerTrack
Friendship Solar 2 [0570] | Friendship Solar 2 | MD | AEF | PowerTrack
101 Carnegie Center | 101 Carnegie Center | NJ |  | InAccess
302 Carnegie Center | 302 Carnegie Center | NJ |  | InAccess
510 Carnegie Center | 510 Carnegie Center | NJ |  | InAccess
701 Carnegie Center | 701 Carnegie Center | NJ |  | InAccess
Hudson County Correction [0470] | Hudson County Correction | NJ | AEF | PowerTrack
ER Bison Solar [0371] | ER Bison Solar | PA | AEF | PowerTrack
Danville | Danville | IL |  | InAccess