## Year to Date
Wells Fargo |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total | 13849749.3751 | 13886968.5442 | -37219.1691 | -0.268% | 16558193.0611 | -2708443.686 | -16.36%
Site | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 720206.5403 | 748185.92 | -27979.3797 | -3.74% | 788763.208 | -68556.6677 | -8.692%
CO | 272608.7315 | 0 | 272608.7315 |  | 275553.832 | -2945.1005 | -1.069%
CT | 13674.214 | 13020.1656 | 654.0484 | 5.023% | 17642.1848 | -3967.9708 | -22.49%
FL | 15977.256 | 41822.958 | -25845.702 | -61.8% | 54424.661 | -38447.405 | -70.64%
IA | 2819486.6875 | 2839873.334 | -20386.6465 | -0.7179% | 2905887.257 | -86400.5695 | -2.973%
NC | 2528419.25 | 2336528.376 | 191890.874 | 8.213% | 3379722.225 | -851302.975 | -25.19%
NJ | 845128.1957 | 838020.5366 | 7107.6591 | 0.8481% | 915113.1513 | -69984.9556 | -7.648%
TX | 6634248.5002 | 7069517.254 | -435268.7538 | -6.157% | 8221086.542 | -1586838.0418 | -19.3%

## 1st Qtr
Wells Fargo |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total | 2022284.6486 | 2259425.2583 | -237140.6097 | -10.5% | 3056274.5468 | -1033989.8982 | -33.83%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 96460.8742 | 98630.98 | -2170.1058 | -2.2% | 92937.79 | 3523.0842 | 3.791%
CO | 49254.6004 | 0 | 49254.6004 |  | 58983.135 | -9728.5346 | -16.49%
CT | 1437.1503 | 3198.4033 | -1761.253 | -55.07% | 2904.6053 | -1467.455 | -50.52%
FL | 3427.8035 | 9472.91 | -6045.1065 | -63.81% | 12229.661 | -8801.8575 | -71.97%
IA | 600256.9375 | 573354.794 | 26902.1435 | 4.692% | 641026.387 | -40769.4495 | -6.36%
NC | 102107 | 266710 | -164603 | -61.72% | 336745 | -234638 | -69.68%
NJ | 152779.9028 | 157231.971 | -4452.0682 | -2.832% | 166141.6225 | -13361.7197 | -8.042%
TX | 1016560.38 | 1150826.2 | -134265.82 | -11.67% | 1745306.346 | -728745.966 | -41.75%

## 2nd Qtr
Wells Fargo |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total | 4061976.2103 | 3842359.1285 | 219617.0818 | 5.716% | 4722056.4858 | -660080.2755 | -13.98%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 179169.75 | 147873.06 | 31296.69 | 21.16% | 157791.785 | 21377.965 | 13.55%
CO | 90952.0029 | 0 | 90952.0029 |  | 87739.817 | 3212.1859 | 3.661%
CT | 5041.9727 | 5037.0564 | 4.9163 | 0.0976% | 6033.0028 | -991.0301 | -16.43%
FL | 2375.5373 | 12898.605 | -10523.0677 | -81.58% | 16185 | -13809.4627 | -85.32%
IA | 840017.0825 | 818172.78 | 21844.3025 | 2.67% | 857847.64 | -17830.5575 | -2.079%
NC | 1016205 | 859577.364 | 156627.636 | 18.22% | 1180909.1 | -164704.1 | -13.95%
NJ | 277465.6772 | 273716.5151 | 3749.1621 | 1.37% | 297775.533 | -20309.8558 | -6.821%
TX | 1650749.1877 | 1725083.748 | -74334.5603 | -4.309% | 2117774.608 | -467025.4203 | -22.05%

## 3rd Qtr
Wells Fargo |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total | 4472304.015 | 4198626.6533 | 273677.3617 | 6.518% | 5239646.6991 | -767342.6841 | -14.64%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 246974.5089 | 261203.812 | -14229.3031 | -5.448% | 288419.592 | -41445.0831 | -14.37%
CO | 84559.8182 | 0 | 84559.8182 |  | 78898.843 | 5660.9752 | 7.175%
CT | 4907.1703 | 2248.3949 | 2658.7754 | 118.3% | 5993.1526 | -1085.9823 | -18.12%
FL | 2909.5079 | 10996.864 | -8087.3561 | -73.54% | 15389 | -12479.4921 | -81.09%
IA | 838363.4175 | 853856.56 | -15493.1425 | -1.814% | 873758.3 | -35394.8825 | -4.051%
NC | 707923.75 | 467700.341 | 240223.409 | 51.36% | 1080129.075 | -372205.325 | -34.46%
NJ | 256720.4039 | 251646.4114 | 5073.9925 | 2.016% | 296221.9405 | -39501.5366 | -13.34%
TX | 2329945.4382 | 2350974.27 | -21028.8318 | -0.8945% | 2600836.796 | -270891.3578 | -10.42%

## 4th Qtr
Wells Fargo |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total | 3293184.5012 | 3586557.5041 | -293373.0029 | -8.18% | 3540215.3294 | -247030.8282 | -6.978%
State | Actual | Expected | Delta | % | Forecasted | Delta | %
CA | 197601.4072 | 240478.068 | -42876.6608 | -17.83% | 249614.041 | -52012.6338 | -20.84%
CO | 47842.31 | 0 | 47842.31 |  | 49932.037 | -2089.727 | -4.185%
CT | 2287.9206 | 2536.311 | -248.3903 | -9.793% | 2711.4241 | -423.5035 | -15.62%
FL | 7264.4073 | 8454.579 | -1190.1717 | -14.08% | 10621 | -3356.5927 | -31.6%
IA | 540849.25 | 594489.2 | -53639.95 | -9.023% | 533254.93 | 7594.32 | 1.424%
NC | 702183.5 | 742540.671 | -40357.171 | -5.435% | 781939.05 | -79755.55 | -10.2%
NJ | 158162.2117 | 155425.6391 | 2736.5726 | 1.761% | 154974.0553 | 3188.1564 | 2.057%
TX | 1636993.4943 | 1842633.036 | -205639.5417 | -11.16% | 1757168.792 | -120175.2977 | -6.839%

## Jan
Wells Fargo |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 434853.6353 | 405850.9266 | 29002.7087 | 7.146% | 698800.05 | -263946.4147 | -37.77% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 668.5 | 0 | 668.5 |  | 660.258 | 8.242 | 1.248%
Otay Mesa | CA | 37.789 | 0 | 37.789 |  | 0 | 37.789
San Leandro | CA | 18587.375 | 25565.67 | -6978.295 | -27.3% | 22910.168 | -4322.793 | -18.87% | 1. Inverter 4 was replaced on 01/31 | 1. SR079901
Van Nuys | CA | 1267.6979 | 0 | 1267.6979 |  | 1339.747 | -72.0491 | -5.378%
98th & Grant | CO | 724.2 | 0 | 724.2 |  | 1165.016 | -440.816 | -37.84%
Arapahoe Crossings | CO | 2121.2004 | 0 | 2121.2004 |  | 2132.967 | -11.7666 | -0.5517%
Aurora City Center | CO | 1077.5 | 0 | 1077.5 |  | 1040.516 | 36.984 | 3.554%
Dry Creek | CO | -0.40201 | 0 | -0.40201 |  | 1258.016 | -1258.418 | -100% | 1. Site is offline from 05/12/2023 | 1. SR078942
Highlands Ranch S. | CO | 1000.7 | 0 | 1000.7 |  | 1110.774 | -110.074 | -9.91%
Lone Tree | CO | 2395.4 | 0 | 2395.4 |  | 2590.419 | -195.019 | -7.528%
Meridian | CO | 1646.1 | 0 | 1646.1 |  | 1355.097 | 291.003 | 21.47%
Southglenn | CO | 1513 | 0 | 1513 |  | 1611.403 | -98.403 | -6.107%
Standley Lake | CO | 2051.1 | 0 | 2051.1 |  | 2170.403 | -119.303 | -5.497%
Havana Gardens | CO | 1739.8 | 0 | 1739.8 |  | 846.258 | 893.542 | 105.6% | 03/01/2023 Per Kate - Do Not Pursue Weather Station
East Hartford | CT | 119.7 | 246.8964 | -127.1964 | -51.52% | 273.275 | -153.575 | -56.2%
Norwalk | CT | 117.7406 | 417.3167 | -299.5761 | -71.79% | 376.757 | -259.0164 | -68.75%
Hialeah Gardens | FL | 1428.4985 | 2582.073 | -1153.5745 | -44.68% | 3451.661 | -2023.1625 | -58.61%
West Des Moines - HMHQ | IA | 12390.9375 | 16455.02 | -4064.0825 | -24.7% | 23956.604 | -11565.6665 | -48.28%
W. Des Moines Campus EAST | IA | 62192.5 | 8477.248 | 53715.252 | 633.6% | 105997.32 | -43804.82 | -41.33% | 1. Expected energy was not available till 01/30 | 1. SR080333
W. Des Moines Campus SW | IA | 25312.5 | 4681.486 | 20631.014 | 440.7% | 55952.783 | -30640.283 | -54.76% | 1. Inverter 4 tripped offline on 01/31 2. Expected energy was not available till 01/30 | 1. SR080633 2. SR080334
WF - CIC | NC | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site de-energized 06/02/2023 due to TIGO investigation. | 1. SR078172
Charlotte - Wells Fargo - DUC | NC | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site de-energized 06/02/2023 due to TIGO investigation. | 1. SR078173
East Windsor | NJ | 234.4 | 395.1954 | -160.7954 | -40.69% | 408.178 | -173.778 | -42.57%
Burlington | NJ | 720 | 848.942 | -128.942 | -15.19% | 1105.296 | -385.296 | -34.86%
Bayonne | NJ | 792.7 | 1075.812 | -283.112 | -26.32% | 2010.779 | -1218.079 | -60.58%
Clifton | NJ | 824.2969 | 1479.194 | -654.8971 | -44.27% | 2566.102 | -1741.8051 | -67.88%
North Elizabeth | NJ | 784.1 | 751.989 | 32.111 | 4.27% | 1413.128 | -629.028 | -44.51%
Haddon Westmont Plaza | NJ | 494.2 | 789.4208 | -295.2208 | -37.4% | 999.193 | -504.993 | -50.54%
Parsippany | NJ | 583.8 | 1291.575 | -707.775 | -54.8% | 1156.298 | -572.498 | -49.51%
Clark | NJ | 559.8 | 806.6296 | -246.8296 | -30.6% | 953.546 | -393.746 | -41.29%
Closter | NJ | 144.2 | 202.6485 | -58.4485 | -28.84% | 494.769 | -350.569 | -70.86%
Holmdel | NJ | 450.3 | 643.0844 | -192.7844 | -29.98% | 809.704 | -359.404 | -44.39%
Ellisburg Circle Center | NJ | 241 | 385.1902 | -144.1902 | -37.43% | 451.606 | -210.606 | -46.63%
Nutley | NJ | 770.9 | 1199.326 | -428.426 | -35.72% | 1734.511 | -963.611 | -55.56%
Marlton | NJ | 1016.6 | 1055.635 | -39.035 | -3.698% | 1680.262 | -663.662 | -39.5%
Middletown | NJ | 994.1 | 964.945 | 29.155 | 3.021% | 1643.936 | -649.836 | -39.53%
Whiting Crestwood | NJ | 1524.9 | 1991.186 | -466.286 | -23.42% | 2510.996 | -986.096 | -39.27%
Barnegat | NJ | 1678.6484 | 1609.744 | 68.9044 | 4.28% | 2100.114 | -421.4656 | -20.07%
Manchester | NJ | 1243.7 | 1242.431 | 1.269 | 0.1021% | 2172.929 | -929.229 | -42.76%
West Deptford - Woodbury | NJ | 1385.9 | 1614.307 | -228.407 | -14.15% | 1978.362 | -592.462 | -29.95%
Edison | NJ | 923 | 960.8481 | -37.8481 | -3.939% | 1532.135 | -609.135 | -39.76%
Flemington | NJ | 745.8 | 1052.367 | -306.567 | -29.13% | 1315.785 | -569.985 | -43.32%
Route 22 | NJ | 933.7 | 1153.66 | -219.96 | -19.07% | 1296.399 | -362.699 | -27.98%
Laurelton | NJ | 799.4 | 861.1401 | -61.7401 | -7.17% | 1207.299 | -407.899 | -33.79%
Mahwah | NJ | 530.1 | 950.6528 | -420.5528 | -44.24% | 1061.701 | -531.601 | -50.07%
Franklin Township WF | NJ | 643.1 | 924.3221 | -281.2221 | -30.42% | 1767.34 | -1124.24 | -63.61%
Bordentown | NJ | 705.7 | 734.3849 | -28.6849 | -3.906% | 1121.351 | -415.651 | -37.07%
South Plainfield | NJ | 440.8 | 493.0951 | -52.2951 | -10.61% | 750.996 | -310.196 | -41.3%
Somerset | NJ | 0 | 0 | 0 |  | 0 | 0 |  | No data available
Clinton Main Relo | NJ | 611.7383 | 1001.651 | -389.9127 | -38.93% | 1153.765 | -542.0267 | -46.98%
North Brunswick | NJ | 740.1 | 851.9058 | -111.8058 | -13.12% | 1435.025 | -694.925 | -48.43%
Cherry Hill | NJ | 566.7148 | 844.154 | -277.4392 | -32.87% | 928.459 | -361.7442 | -38.96%
Hainesport | NJ | 701.1 | 866.3807 | -165.2807 | -19.08% | 998.585 | -297.485 | -29.79%
San Antonio - Ops Ctr (Bldg 106) | TX | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site's de-energized 06/02/2023 due to TIGO investigation
San Antonio - Ops Ctr GM | TX | 275677 | 318383.4 | -42706.4 | -13.41% | 289610.834 | -13933.834 | -4.811% | 1. Inverter 17 was offline from morning and back online at 14:00 on 01/24 | 1. SR080443
San Antonio - Ctr (Bldg 201) | TX | 0 | 0 | 0 |  | 35803.38 | -35803.38 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078159
San Antonio - Ops Ctr (Bldg 203) | TX | 0 | 0 | 0 |  |  |  |  | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078164
San Antonio - Ops Ctr (Bldg 205) | TX | 0 | 0 | 0 |  | 33517.699 | -33517.699 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078165
San Antonio - Ops Ctr (Bldg 307) | TX | 0 | 0 | 0 |  | 34698.845 | -34698.845 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078166
San Antonio - Ctr (Bldg 308) | TX | 0 | 0 | 0 |  | 34211.301 | -34211.301 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078160
San Antonio - Ops Ctr (Bldg 104) | TX | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078162
San Antonio - Ops Ctr (Bldg 102) | TX | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078161
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA

## Feb
Wells Fargo |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 650956.6095 | 702151.3317 | -51194.7222 | -7.291% | 903765.6888 | -252809.0793 | -27.97% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 675.2 | 0 | 675.2 |  | 746.37 | -71.17 | -9.535%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0
San Leandro | CA | 27875.8125 | 31129.31 | -3253.4975 | -10.45% | 25298.6 | 2577.2125 | 10.19% | 1. Inverter 4 tripped offline on 02/12 and 02/24. Inverter being RMA'd | 1. SR080945
Van Nuys | CA | 1221.4997 | 0 | 1221.4997 |  | 1486.647 | -265.1473 | -17.84%
98th & Grant | CO | 884 | 0 | 884 |  | 1280 | -396 | -30.94%
Arapahoe Crossings | CO | 2267.1002 | 0 | 2267.1002 |  | 2339.458 | -72.3578 | -3.093%
Aurora City Center | CO | 1176.7 | 0 | 1176.7 |  | 1140 | 36.7 | 3.219%
Dry Creek | CO | -3.902 | 0 | -3.902 |  | 1386 | -1389.902 | -100.3% | 1. Site not reporting prodcution from 05/12/2023 | 1. SR078942
Highlands Ranch S. | CO | 1075.3 | 0 | 1075.3 |  | 1265 | -189.7 | -15%
Lone Tree | CO | 1922.5 | 0 | 1922.5 |  | 2891 | -968.5 | -33.5%
Meridian | CO | 1964.8 | 0 | 1964.8 |  | 1699 | 265.8 | 15.64%
Southglenn | CO | 1800.9 | 0 | 1800.9 |  | 1778 | 22.9 | 1.288%
Standley Lake | CO | 2393.1 | 0 | 2393.1 |  | 2371 | 22.1 | 0.9321%
Havana Gardens | CO | 2062.1 | 0 | 2062.1 |  | 926 | 1136.1 | 122.7% | 03/01/2023 Per Kate - Do Not Pursue Weather Station
East Hartford | CT | 277.7 | 420.284 | -142.584 | -33.93% | 431.1858 | -153 | -35.48%
Norwalk | CT | 212.0097 | 641.9062 | -429.8965 | -66.97% | 490.3875 | -278 | -56.69%
Hialeah Gardens | FL | 1245.3049 | 3165.837 | -1920.5321 | -60.66% | 3739 | -2493.6951 | -66.69% | 1. Daily drop in production due to inverter fan failure. | 1. SR081410
West Des Moines - HMHQ | IA | 33641.5 | 34557.14 | -915.64 | -2.65% | 29114.09 | 4527.41 | 15.55%
W. Des Moines Campus EAST | IA | 154786 | 162400.1 | -7614.1 | -4.688% | 124800 | 29986 | 24.03%
W. Des Moines Campus SW | IA | 63016.5 | 89106.8 | -26090.3 | -29.28% | 63174.59 | -158.09 | -0.2502% | 1. Inverter 4 back online on 02/21 after replacement | 1. SR080633
WF - CIC | NC | 0 | 0 | 0 |  | 0 | 0
Charlotte - Wells Fargo - DUC | NC | 0 | 0 | 0 |  | 0 | 0
East Windsor | NJ | 616.9 | 728.9626 | -112.0626 | -15.37% | 481.6708 | 135.2292 | 28.08%
Burlington | NJ | 1843.1 | 1626.606 | 216.494 | 13.31% | 1364.992 | 478.108 | 35.03%
Bayonne | NJ | 1770 | 2142.025 | -372.025 | -17.37% | 2322.581 | -552.581 | -23.79%
Clifton | NJ | 2043.2812 | 2654.534 | -611.2528 | -23.03% | 3038.303 | -995.0217 | -32.75%
North Elizabeth | NJ | 1566.5 | 1603.561 | -37.061 | -2.311% | 1917.395 | -350.895 | -18.3%
Haddon Westmont Plaza | NJ | 1473.6 | 1550.355 | -76.755 | -4.951% | 1328.679 | 144.921 | 10.91%
Parsippany | NJ | 1595.4 | 2384.318 | -788.918 | -33.09% | 1729.456 | -134.056 | -7.751%
Clark | NJ | 1274.5 | 1502.578 | -228.078 | -15.18% | 1380.123 | -105.623 | -7.653%
Closter | NJ | 304.9 | 446.6089 | -141.7089 | -31.73% | 770.4244 | -465.5244 | -60.42%
Holmdel | NJ | 1149.5 | 1236.095 | -86.595 | -7.006% | 1001 | 148.5 | 14.84%
Ellisburg Circle Center | NJ | 662.6 | 734.0975 | -71.4975 | -9.74% | 615 | 47.6 | 7.74%
Nutley | NJ | 1637.7 | 2148.254 | -510.554 | -23.77% | 2500.109 | -862.409 | -34.49%
Marlton | NJ | 2616.5 | 1996.437 | 620.063 | 31.06% | 2216.347 | 400.153 | 18.05%
Middletown | NJ | 2120.4 | 1811.757 | 308.643 | 17.04% | 1910.473 | 209.927 | 10.99%
Whiting Crestwood | NJ | 3314.8 | 3360.472 | -45.672 | -1.359% | 2967.669 | 347.131 | 11.7%
Barnegat | NJ | 3450.6484 | 2871.162 | 579.4864 | 20.18% | 2744.481 | 706.1674 | 25.73%
Manchester | NJ | 2231.9 | 2113.042 | 118.858 | 5.625% | 2378.861 | -146.961 | -6.178%
West Deptford - Woodbury | NJ | 3009.1 | 2738.82 | 270.28 | 9.868% | 2354.187 | 654.913 | 27.82%
Edison | NJ | 2238.1 | 1936.849 | 301.251 | 15.55% | 2090.041 | 148.059 | 7.084%
Flemington | NJ | 1635.7 | 1878.609 | -242.909 | -12.93% | 1856.084 | -220.384 | -11.87%
Route 22 | NJ | 1838.9 | 2501.375 | -662.475 | -26.48% | 1744.93 | 93.97 | 5.385%
Laurelton | NJ | 1846.9 | 1545.61 | 301.29 | 19.49% | 1514.129 | 332.771 | 21.98%
Mahwah | NJ | 1409 | 1801.931 | -392.931 | -21.81% | 1471.531 | -62.531 | -4.249%
Franklin Township WF | NJ | 1710.6 | 1659.973 | 50.627 | 3.05% | 2156.48 | -445.88 | -20.68%
Bordentown | NJ | 1752.8 | 1349.719 | 403.081 | 29.86% | 1259.502 | 493.298 | 39.17%
South Plainfield | NJ | 1060 | 954.5605 | 105.4395 | 11.05% | 943.8813 | 116.1187 | 12.3%
Somerset | NJ | 1459 | 2436.757 | -977.757 | -40.13% | 1447.482 | 11.518 | 0.7957%
Clinton Main Relo | NJ | 1706.6641 | 1993.052 | -286.3879 | -14.37% | 1675.408 | 31.2561 | 1.866%
North Brunswick | NJ | 1841.8 | 1726.46 | 115.34 | 6.681% | 1852.114 | -10.314 | -0.5569%
Cherry Hill | NJ | 1352.2106 | 1529.766 | -177.5554 | -11.61% | 1197.873 | 154.3376 | 12.88%
Hainesport | NJ | 1647.1 | 1596.808 | 50.292 | 3.15% | 1161.867 | 485.233 | 41.76%
San Antonio - Ops Ctr (Bldg 106) | TX | 2887 | 0 | 2887 |  | 38409 | -35522 | -92.48% | 1. Site reenergized on 02/27 after TIGO investigation | 1. SR078163
San Antonio - Ops Ctr GM | TX | 285995.75 | 324168.8 | -38173.05 | -11.78% | 305642 | -19646.25 | -6.428%
San Antonio - Ctr (Bldg 201) | TX | 0 | 0 | 0 |  | 38321 | -38321 | -100% | 1. Site's de-energized on 06/02/2023 due to TIGO investigation and renergized on 03/05/2024 | 1. SR078159
San Antonio - Ops Ctr (Bldg 203) | TX | 0 | 0 | 0 |  | 39375.26 | -39375.26 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078164
San Antonio - Ops Ctr (Bldg 205) | TX | 0 | 0 | 0 |  | 36456.78 | -36456.78 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078165
San Antonio - Ops Ctr (Bldg 307) | TX | 0 | 0 | 0 |  | 37489.763 | -37489.763 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078166
San Antonio - Ctr (Bldg 308) | TX | 0 | 0 | 0 |  | 36430.224 | -36430.224 | -100% | 1. Site's de-energized 06/02/2023 due to TIGO investigation | 1. SR078160
San Antonio - Ops Ctr (Bldg 104) | TX | 3498.63 | 0 | 3498.63 |  | 11154.26 | -7655.63 | -68.63% | 1. Site reenergized on 02/20 after TIGO investigation | 1. SR078162
San Antonio - Ops Ctr (Bldg 102) | TX | 5901 | 0 | 5901 |  | 40738 | -34837 | -85.51% | 1. Site reenergized on 02/23, but inverters 2, 3 & 5 are still underproducing | 1. SR078161
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA

## Mar
Wells Fargo |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 936474.4038 | 1151423 | -214948.5962 | -18.67% | 1453708.808 | -517234.4042 | -35.58% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1138 | 0 | 1138 |  | 1060 | 78 | 7.358%
Otay Mesa | CA |  | 0
San Leandro | CA | 43042 | 41936 | 1106 | 2.637% | 37309 | 5733 | 15.37% | 1. Inverter 4 offline on 03/02, 03/04, 03/05, 03/06, 03/08, 03/10 | 1. SR080945
Van Nuys | CA | 1947 | 0 | 1947 |  | 2127 | -180 | -8.463%
98th & Grant | CO | 1216 | 0 | 1216 |  | 1984 | -768 | -38.71%
Arapahoe Crossings | CO | 3183.3998 | 0 | 3183.3998 |  | 3628.808 | -445.4082 | -12.27%
Aurora City Center | CO | 1628 | 0 | 1628 |  | 1727 | -99 | -5.732%
Dry Creek | CO | -2.996 | 0 | -2.996 |  | 2153 | -2155.996 | -100.1% | 1. Site stopped communicating since 03/22 | 1. SR078942
Highlands Ranch S. | CO | 1464 | 0 | 1464 |  | 2006 | -542 | -27.02%
Lone Tree | CO | 2352 | 0 | 2352 |  | 4580 | -2228 | -48.65%
Meridian | CO | 2687 | 0 | 2687 |  | 2667 | 20 | 0.7499%
Southglenn | CO | 2486 | 0 | 2486 |  | 2762 | -276 | -9.993%
Standley Lake | CO | 1464 | 0 | 1464 |  | 3683 | -2219 | -60.25%
Havana Gardens | CO | 2966 | 0 | 2966 |  | 1436 | 1530 | 106.5%
East Hartford | CT |  | 609 |  |  | 599
Norwalk | CT | 710 | 863 | -153 | -17.73% | 734 | -24 | -3.27%
Hialeah Gardens | FL | 754 | 3725 | -2971 | -79.76% | 5039 | -4285 | -85.04% | 1. Daily drop in production due to inverter fan failure | 1. SR081410
West Des Moines - HMHQ | IA | 0 | 0 | 0 |  | 0 | 0
W. Des Moines Campus EAST | IA | 168562 | 169387 | -825 | -0.4871% | 159000 | 9562 | 6.014%
W. Des Moines Campus SW | IA | 80355 | 88290 | -7935 | -8.987% | 79031 | 1324 | 1.675%
WF - CIC | NC | 101088 | 111466 | -10378 | -9.31% | 171329 | -70241 | -41% | 1. Site back online on 03/12. Inverter 1 to 4 are back online since 03/13, Inverters 13 to 17 are back online on 03/14, Inverters 6, 7 and 09 to 12 are back online on 03/15 | 1. SR078172
Charlotte - Wells Fargo - DUC | NC | 1019 | 155244 | -154225 | -99.34% | 165416 | -164397 | -99.38% | 1. Site back online on 03/16 but since then all the inverters are producing constantly around 0.8kW throughout the day | 1. SR078173
East Windsor | NJ | 868 | 899 | -31 | -3.448% | 758 | 110 | 14.51%
Burlington | NJ | 2271 | 2117 | 154 | 7.274% | 1975 | 296 | 14.99%
Bayonne | NJ | 2808 | 2774 | 34 | 1.226% | 3084 | -276 | -8.949%
Clifton | NJ | 3452 | 3504 | -52 | -1.484% | 3881 | -429 | -11.05%
North Elizabeth | NJ | 2955 | 2135 | 820 | 38.41% | 2680 | 275 | 10.26%
Haddon Westmont Plaza | NJ | 2120 | 2028 | 92 | 4.536% | 1901 | 219 | 11.52%
Parsippany | NJ | 2545 | 2776 | -231 | -8.321% | 2545 | 0 | 0%
Clark | NJ | 2177 | 1988 | 189 | 9.507% | 1843 | 334 | 18.12%
Closter | NJ | 817 | 763 | 54 | 7.077% | 1041 | -224 | -21.52%
Holmdel | NJ | 1858 | 1620 | 238 | 14.69% | 1596 | 262 | 16.42%
Ellisburg Circle Center | NJ | 940 | 929 | 11 | 1.184% | 874 | 66 | 7.551%
Nutley | NJ | 2974 | 2777 | 197 | 7.094% | 3135 | -161 | -5.136%
Marlton | NJ | 3496 | 2962 | 534 | 18.03% | 3142 | 354 | 11.27%
Middletown | NJ | 2867 | 2409 | 458 | 19.01% | 2632 | 235 | 8.929%
Whiting Crestwood | NJ | 3856 | 3757 | 99 | 2.635% | 3766 | 90 | 2.39%
Barnegat | NJ | 4807 | 4116 | 691 | 16.79% | 4404 | 403 | 9.151%
Manchester | NJ | 2722 | 2531 | 191 | 7.546% | 3173 | -451 | -14.21%
West Deptford - Woodbury | NJ | 3319 | 3314 | 5 | 0.1509% | 2972 | 347 | 11.68%
Edison | NJ | 2928 | 2567 | 361 | 14.06% | 2499 | 429 | 17.17%
Flemington | NJ | 2630 | 2285 | 345 | 15.1% | 2337 | 293 | 12.54%
Route 22 | NJ | 2658 | 2719 | -61 | -2.243% | 2240 | 418 | 18.66%
Laurelton | NJ | 2040 | 2082 | -42 | -2.017% | 2166 | -126 | -5.817%
Mahwah | NJ | 2064 | 2044 | 20 | 0.9785% | 1905 | 159 | 8.346%
Franklin Township WF | NJ | 2433 | 2215 | 218 | 9.842% | 2742 | -309 | -11.27%
Bordentown | NJ | 1983 | 1664 | 319 | 19.17% | 1717 | 266 | 15.49%
South Plainfield | NJ | 1416 | 1280 | 136 | 10.62% | 1227 | 189 | 15.4%
Somerset | NJ | 2146 | 2895 | -749 | -25.87% | 1893 | 253 | 13.37%
Clinton Main Relo | NJ | 2481 | 2488 | -7 | -0.2814% | 2163 | 318 | 14.7%
North Brunswick | NJ | 2516 | 2256 | 260 | 11.52% | 2428 | 88 | 3.624%
Cherry Hill | NJ | 1739 | 1729 | 10 | 0.5784% | 1658 | 81 | 4.885%
Hainesport | NJ | 1929 | 2006 | -77 | -3.838% | 1613 | 316 | 19.59%
San Antonio - Ops Ctr (Bldg 106) | TX | 39844 | 24128 | 15716 | 65.14% | 50913 | -11069 | -21.74%
San Antonio - Ops Ctr GM | TX | 298274 | 337304 | -39030 | -11.57% | 366154 | -67880 | -18.54%
San Antonio - Ctr (Bldg 201) | TX | 31737 | 23935 | 7802 | 32.6% | 50950 | -19213 | -37.71% | 1. Site was re-energized on 03/05 and inverter 3 is underproducing ~16kW | 1. SR078159
San Antonio - Ops Ctr (Bldg 203) | TX | 23760 | 24509 | -749 | -3.056% | 51537 | -27777 | -53.9% | 1. Site was re-energized on 03/12 at 13:45 | 1. SR078164
San Antonio - Ops Ctr (Bldg 205) | TX | 0 | 21809 | -21809 | -100% | 48185 | -48185 | -100% | 1. Site de-energized 06/02/2023 due to TIGO investigation | 1. SR078165
San Antonio - Ops Ctr (Bldg 307) | TX | 0 | 23708 | -23708 | -100% | 49346 | -49346 | -100% | 1. Site de-energized 06/02/2023 due to TIGO investigation | 1. SR078166
San Antonio - Ctr (Bldg 308) | TX | 0 | 23168 | -23168 | -100% | 47944 | -47944 | -100% | 1. Site de-energized 06/02/2023 due to TIGO investigation | 1. SR078160
San Antonio - Ops Ctr (Bldg 104) | TX | 10721 | 7259 | 3462 | 47.69% | 14772 | -4051 | -27.42%
San Antonio - Ops Ctr (Bldg 102) | TX | 38265 | 22454 | 15811 | 70.42% | 53647 | -15382 | -28.67% | 1. Inverters 2, 3 & 5 are underperforming throughout the month | 1. SR078161
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA

## Apr
Wells Fargo |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 967630.937 | 1046571.4263 | -78940.4893 | -7.543% | 1235173.484 | -267542.547 | -21.66% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1295.8 | 0 | 1295.8 |  | 1189 | 106.8 | 8.982%
Otay Mesa | CA |  | 0
San Leandro | CA | 52633.125 | 47100.36 | 5532.765 | 11.75% | 44943.77 | 7689.355 | 17.11%
Van Nuys | CA | 2145.5 | 0 | 2145.5 |  | 2383.032 | -237.532 | -9.968%
98th & Grant | CO | 1577.4 | 0 | 1577.4 |  | 2136 | -558.6 | -26.15%
Arapahoe Crossings | CO | 4133.5045 | 0 | 4133.5045 |  | 3918.467 | 215.0375 | 5.488%
Aurora City Center | CO | 1935.5 | 0 | 1935.5 |  | 1830 | 105.5 | 5.765%
Dry Creek | CO | 256.1 | 0 | 256.1 |  | 2326 | -2069.9 | -88.99% | 1. Site is offline from 04/01 & back online at 04/26 at 15:00. | 1. SR078942
Highlands Ranch S. | CO | 2045.9 | 0 | 2045.9 |  | 2208 | -162.1 | -7.341%
Lone Tree | CO | 3089.5 | 0 | 3089.5 |  | 5022 | -1932.5 | -38.48%
Meridian | CO | 3105.7 | 0 | 3105.7 |  | 2914 | 191.7 | 6.579%
Southglenn | CO | 3252.2 | 0 | 3252.2 |  | 2987 | 265.2 | 8.878%
Standley Lake | CO | [7 empty] | 1. Site stopped communicating on 03/14 at 07:00. Cannot verify production | 1. SR081942
Havana Gardens | CO | 3662.8 |  |  |  | 1550 | 2112.8 | 136.3%
East Hartford | CT | 684.8 | 607.3737 | 77.4263 | 12.75% | 800.537 | -115.737 | -14.46%
Norwalk | CT | 807.5727 | 875.3109 | -67.7382 | -7.739% | 993.77 | -186.1973 | -18.74%
Hialeah Gardens | FL | 869.938 | 4597.807 | -3727.869 | -81.08% | 5532 | -4662.062 | -84.27% | 1. Site production is droping consistently from the mid of the day. | 1.SR081410
West Des Moines - HMHQ | IA
W. Des Moines Campus EAST | IA | 180086.75 | 177234.7 | 2852.05 | 1.609% | 177300 | 2786.75 | 1.572%
W. Des Moines Campus SW | IA | 85747.5 | 89118.94 | -3371.44 | -3.783% | 88010.12 | -2262.62 | -2.571%
WF - CIC | NC | 178890 | 129343.5 | 49546.5 | 38.31% | 194273 | -15383 | -7.918%
Charlotte - Wells Fargo - DUC | NC | 73190 | 171337.2 | -98147.2 | -57.28% | 173188 | -99998 | -57.74% | 1. Utill 04/19 all inverters were producing 0.8 kW except 2, which began operating at rated capacity from 04/18 and Inverter 10 is offline since 04/27 | 1.SR078173
East Windsor | NJ | 952.4 | 959.2463 | -6.8463 | -0.7137% | 1088.314 | -135.914 | -12.49%
Burlington | NJ | 2447.5 | 2421.409 | 26.091 | 1.078% | 2751.473 | -303.973 | -11.05%
Bayonne | NJ | 3186.9 | 3081.743 | 105.157 | 3.412% | 3318.21 | -131.31 | -3.957%
Clifton | NJ | 3670.4531 | 3807.622 | -137.1689 | -3.602% | 4401.765 | -731.3119 | -16.61%
North Elizabeth | NJ | 3363.6 | 2506.891 | 856.709 | 34.17% | 3662.329 | -298.729 | -8.157%
Haddon Westmont Plaza | NJ | 2326.4 | 2294.151 | 32.249 | 1.406% | 2665.607 | -339.207 | -12.73%
Parsippany | NJ | 2697.5 | 2760.886 | -63.386 | -2.296% | 3034.207 | -336.707 | -11.1%
Clark | NJ | 2421.6 | 2316.562 | 105.038 | 4.534% | 2537.376 | -115.776 | -4.563%
Closter | NJ | 1220.5 | 959.8124 | 260.6876 | 27.16% | 1509.897 | -289.397 | -19.17%
Holmdel | NJ | 2017.6 | 1842.106 | 175.494 | 9.527% | 2190.279 | -172.679 | -7.884%
Ellisburg Circle Center | NJ | 1052.5 | 1031.004 | 21.496 | 2.085% | 1221.8 | -169.3 | -13.86%
Nutley | NJ | 3239.2 | 3139.521 | 99.679 | 3.175% | 4284.495 | -1045.295 | -24.4%
Marlton | NJ | 3663.8 | 3352.921 | 310.879 | 9.272% | 4197.603 | -533.803 | -12.72%
Middletown | NJ | 2967.5 | 2619.169 | 348.331 | 13.3% | 3501.3 | -533.8 | -15.25%
Whiting Crestwood | NJ | 3911.8 | 3669.987 | 241.813 | 6.589% | 4703.77 | -791.97 | -16.84%
Barnegat | NJ | 5506.8169 | 4964.311 | 542.5059 | 10.93% | 6090.859 | -584.0421 | -9.589%
Manchester | NJ | 2850.7 | 2600.038 | 250.662 | 9.641% | 3965.795 | -1115.095 | -28.12%
West Deptford - Woodbury | NJ | 3342.7 | 3514.023 | -171.323 | -4.875% | 3793.855 | -451.155 | -11.89%
Edison | NJ | 3057.9 | 2972.998 | 84.902 | 2.856% | 3326.064 | -268.164 | -8.063%
Flemington | NJ | 2860.7 | 2705.1 | 155.6 | 5.752% | 3300.397 | -439.697 | -13.32%
Route 22 | NJ | 2803.4 | 2968.078 | -164.678 | -5.548% | 3059.282 | -255.882 | -8.364%
Laurelton | NJ | 2089 | 2447.617 | -358.617 | -14.65% | 2858.875 | -769.875 | -26.93% | 1. Production meter reporting less than actual production due to phase A voltage dropping to zero throughout the month | 1. SR075812
Mahwah | NJ | 2236.3 | 2020.069 | 216.231 | 10.7% | 2605.216 | -368.916 | -14.16%
Franklin Township WF | NJ | 2627.4 | 2556.795 | 70.605 | 2.761% | 3147.511 | -520.111 | -16.52%
Bordentown | NJ | 2017.5 | 1816.225 | 201.275 | 11.08% | 2256.149 | -238.649 | -10.58%
South Plainfield | NJ | 1495.1 | 1454.835 | 40.265 | 2.768% | 1595.567 | -100.467 | -6.297%
Somerset | NJ | 1716.5 | 2166.354 | -449.854 | -20.77% | 1719.093 | -2.593 | -0.1508%
Clinton Main Relo | NJ | 2811.176 | 2787.123 | 24.053 | 0.863% | 3006.942 | -195.766 | -6.51%
North Brunswick | NJ | 2769.7 | 2582.647 | 187.053 | 7.243% | 3330.864 | -561.164 | -16.85%
Cherry Hill | NJ | 1831.4453 | 1826.987 | 4.4583 | 0.244% | 2170.223 | -338.7777 | -15.61%
Hainesport | NJ | 1967.5 | 2178.004 | -210.504 | -9.665% | 2189.541 | -222.041 | -10.14%
San Antonio - Ops Ctr (Bldg 106) | TX | 40699.3125 | 42002.4 | -1303.0875 | -3.102% | 54117.97 | -13418.6575 | -24.8% | 1. Inverter 2 tripped offline on 04/11 at 12:30, came back online at 15:00, and started derating untill 04/29. | 1.SR078163
San Antonio - Ops Ctr GM | TX | 52633.125 | 47100.36 | 5532.765 | 11.75% | 44943.77 | 7689.355 | 17.11%
San Antonio - Ctr (Bldg 201) | TX | 42554.875 | 41679.99 | 874.885 | 2.099% | 52156.83 | -9601.955 | -18.41% | 1. Inverter 3 is underperforming ~16kW till 04/14. | 1. SR078159
San Antonio - Ops Ctr (Bldg 203) | TX | 44657.0333 | 45221.17 | -564.1367 | -1.248% | 53254.52 | -8597.4866 | -16.14%
San Antonio - Ops Ctr (Bldg 205) | TX | 8224.3438 | 37986.76 | -29762.4163 | -78.35% | 51076.02 | -42851.6762 | -83.9% | 1.Site was offline from 06/02/2023 to 04/16/2024, but inverters 1 & 2 remainied offline even after the site resumed. | 1. SR078165
San Antonio - Ops Ctr (Bldg 307) | TX | 34702.4688 | 41309.93 | -6607.4613 | -15.99% | 51882.91 | -17180.4413 | -33.11% | 1. Site was offline from 06/02/2023 to 04/02/2024, but inverters 4 remainied offline till 04/17 & started underproducing till 04/28. | 1. SR078166
San Antonio - Ctr (Bldg 308) | TX | 14864.1253 | 40358.8 | -25494.6747 | -63.17% | 49286.58 | -34422.4547 | -69.84% | 1. Site was offline from 06/02/2023 to 04/10/2024. But Inverters 1, 3 & 5 remained offline till 04/18 and came online on 04/19 at 11:00 am & inverter 4 tripped offline on 04/19 at 10:00 am & continued. | 1.SR078160
San Antonio - Ops Ctr (Bldg 104) | TX | 10116.2664 | 12644.16 | -2527.8936 | -19.99% | 15675.24 | -5558.9736 | -35.46%
San Antonio - Ops Ctr (Bldg 102) | TX | 38646.7053 | 39728.43 | -1081.7247 | -2.723% | 55790.29 | -17143.5847 | -30.73% | 1. Inverter 2,3 & 5 are underperforming throughout the month. | 1. SR078161
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA

## May
Wells Fargo |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 1446903.5275 | 1318940.0186 | 127963.5089 | 9.702% | 1703692.745 | -256789.2175 | -15.07% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1168.1 | 0 | 1168.1 |  | 1376 | -207.9 | -15.11%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0
San Leandro | CA | 60879.625 | 52276.36 | 8603.265 | 16.46% | 49505.85 | 11373.775 | 22.97% | 1. Inverters 2,4 & 9 are underperforming approximately 4kW each compared to peers possibly string down from 05/13 | 1. SR084620
Van Nuys | CA | 2108.1 | 0 | 2108.1 |  | 2808.835 | -700.735 | -24.95%
98th & Grant | CO | 1849.3 | 0 | 1849.3 |  | 2339 | -489.7 | -20.94%
Arapahoe Crossings | CO | 4776.0048 | 0 | 4776.0048 |  | 4285.177 | 490.8278 | 11.45%
Aurora City Center | CO | 2316.4 | 0 | 2316.4 |  | 1972 | 344.4 | 17.46%
Dry Creek | CO | 2142.5 | 0 | 2142.5 |  | 2551 | -408.5 | -16.01%
Highlands Ranch S. | CO | 2464.9 | 0 | 2464.9 |  | 2417 | 47.9 | 1.982%
Lone Tree | CO | 3854 | 0 | 3854 |  | 5500 | -1646 | -29.93%
Meridian | CO | 3791.4 | 0 | 3791.4 |  | 3150 | 641.4 | 20.36%
Southglenn | CO | 3690.9 | 0 | 3690.9 |  | 3267 | 423.9 | 12.98%
Standley Lake | CO | 5029.7 | 0 | 5029.7 |  | 4357 | 672.7 | 15.44%
Havana Gardens | CO | 4375.3 | 0 | 4375.3 |  | 1695 | 2680.3 | 158.1%
East Hartford | CT | 845 | 680.5051 | 164.4949 | 24.17% | 1052.49 | -207.49 | -19.71%
Norwalk | CT | 844.8899 | 991.6151 | -146.7252 | -14.8% | 1241.701 | -396.8111 | -31.96% | 1. Intermittent meter phase C/power factor issue slightly impacting reported energy production | 1. SR077700
Hialeah Gardens | FL | 771.3982 | 4721.588 | -3950.1898 | -83.66% | 5552 | -4780.6018 | -86.11% | 1. Site production is dropping consistently from the mid of the day due to fan fault. | 1. SR081410
West Des Moines - HMHQ | IA | 0 | 0 | 0 |  | 0 | 0
W. Des Moines Campus EAST | IA | 195594.75 | 188012.9 | 7581.85 | 4.033% | 192800 | 2794.75 | 1.45%
W. Des Moines Campus SW | IA | 92136 | 92247.49 | -111.49 | -0.1209% | 95417.42 | -3281.42 | -3.439%
WF - CIC | NC | 187961 | 137400.2 | 50560.8 | 36.8% | 205438 | -17477 | -8.507%
Charlotte - Wells Fargo - DUC | NC | 180424 | 134257.7 | 46166.3 | 34.39% | 186177.1 | -5753.1 | -3.09% | 1. Inverter 10 is offline from 04/27 to 05/17 and inverter 2 is offline since 05/16 | 1. SR078173
East Windsor | NJ | 1017 | 997.2594 | 19.7406 | 1.979% | 1301.677 | -284.677 | -21.87%
Burlington | NJ | 2570 | 2598.016 | -28.016 | -1.078% | 3348.455 | -778.455 | -23.25%
Bayonne | NJ | 3563.8 | 3409.604 | 154.196 | 4.522% | 3794.636 | -230.836 | -6.083%
Clifton | NJ | 4377.5078 | 4537.442 | -159.9342 | -3.525% | 4475.149 | -97.6412 | -2.182%
North Elizabeth | NJ | 3763.2 | 3321.67 | 441.53 | 13.29% | 4156.65 | -393.45 | -9.466%
Haddon Westmont Plaza | NJ | 2500.9 | 2470.426 | 30.474 | 1.234% | 3078.087 | -577.187 | -18.75%
Parsippany | NJ | 3162.7 | 3126.6 | 36.1 | 1.155% | 3553.629 | -390.929 | -11%
Clark | NJ | 2667.4 | 2624.083 | 43.317 | 1.651% | 2892.308 | -224.908 | -7.776%
Closter | NJ | 1489.1 | 1192.224 | 296.876 | 24.9% | 1810.933 | -321.833 | -17.77%
Holmdel | NJ | 2282.9 | 2123.976 | 158.924 | 7.482% | 2552.46 | -269.56 | -10.56%
Ellisburg Circle Center | NJ | 1111.1 | 1130.588 | -19.488 | -1.724% | 1424.187 | -313.087 | -21.98%
Nutley | NJ | 3783.2 | 3705.649 | 77.551 | 2.093% | 4989.1 | -1205.9 | -24.17%
Marlton | NJ | 3893.5 | 3640.529 | 252.971 | 6.949% | 4973.951 | -1080.451 | -21.72%
Middletown | NJ | 3290.1 | 3124.739 | 165.361 | 5.292% | 4046.587 | -756.487 | -18.69%
Whiting Crestwood | NJ | 3860.8 | 3742.763 | 118.037 | 3.154% | 5333.231 | -1472.431 | -27.61%
Barnegat | NJ | 5918.2812 | 5428.35 | 489.9312 | 9.025% | 7703.145 | -1784.8638 | -23.17%
Manchester | NJ | 2815.7 | 2545.564 | 270.136 | 10.61% | 4420.348 | -1604.648 | -36.3%
West Deptford - Woodbury | NJ | 3435.5 | 3699.739 | -264.239 | -7.142% | 4225.189 | -789.689 | -18.69%
Edison | NJ | 3262.9 | 3317.666 | -54.766 | -1.651% | 3805.732 | -542.832 | -14.26%
Flemington | NJ | 3109 | 3288.516 | -179.516 | -5.459% | 3804.528 | -695.528 | -18.28%
Route 22 | NJ | 3052.9 | 3180.358 | -127.458 | -4.008% | 3412.318 | -359.418 | -10.53%
Laurelton | NJ | 1861.2 | 2660.09 | -798.89 | -30.03% | 3345.333 | -1484.133 | -44.36% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 | 1. SR075812
Mahwah | NJ | 2674.8 | 2324.243 | 350.557 | 15.08% | 3214.382 | -539.582 | -16.79%
Franklin Township WF | NJ | 2824.6 | 2835.99 | -11.39 | -0.4016% | 3311.285 | -486.685 | -14.7%
Bordentown | NJ | 2062.6 | 1936.258 | 126.342 | 6.525% | 2575.138 | -512.538 | -19.9%
South Plainfield | NJ | 1623.1 | 1653.081 | -29.981 | -1.814% | 1813.296 | -190.196 | -10.49%
Somerset | NJ | 2620.3 | 3245.099 | -624.799 | -19.25% | 3057.936 | -437.636 | -14.31%
Clinton Main Relo | NJ | 3059.1758 | 3061.227 | -2.0512 | -0.06701% | 3516.182 | -457.0062 | -13%
North Brunswick | NJ | 3053.3 | 2935.113 | 118.187 | 4.027% | 3929.651 | -876.351 | -22.3%
Cherry Hill | NJ | 1960.7305 | 1948.25 | 12.4805 | 0.6406% | 2574.719 | -613.9885 | -23.85%
Hainesport | NJ | 2028.9 | 2349.998 | -321.098 | -13.66% | 2603.08 | -574.18 | -22.06%
San Antonio - Ops Ctr (Bldg 106) | TX | 43079.125 | 39823.29 | 3255.835 | 8.176% | 57607.63 | -14528.505 | -25.22%
San Antonio - Ops Ctr GM | TX | 293021.375 | 332845.6 | -39824.225 | -11.96% | 414100 | -121078.625 | -29.24% | 1. Inverter 2 is derating by 25kW from 05/11/2024. Inverter 8 is underperforming approximately 50kW compared to its peers from 05/10/2024. 2. Inverter 17 is derating by 75kW from 05/28/2024. | 1. SR084558 2. SR085239
San Antonio - Ctr (Bldg 201) | TX | 45121.9688 | 39532.5 | 5589.4688 | 14.14% | 55911.19 | -10789.2213 | -19.3%
San Antonio - Ops Ctr (Bldg 203) | TX | 45701.2934 | 44197.59 | 1503.7034 | 3.402% | 56492.54 | -10791.2466 | -19.1%
San Antonio - Ops Ctr (Bldg 205) | TX | 32914.4375 | 36023.38 | -3108.9425 | -8.63% | 54301.05 | -21386.6125 | -39.39% | 1. Inverters 1 and 2 are offline from 05/01 to 05/20. | 1. SR078165
San Antonio - Ops Ctr (Bldg 307) | TX | 45272.5927 | 39178.58 | 6094.0127 | 15.55% | 55047.09 | -9774.4973 | -17.76%
San Antonio - Ctr (Bldg 308) | TX | 37331.4684 | 38282.52 | -951.0516 | -2.484% | 52423.06 | -15091.5916 | -28.79% | 1. Inverter 4 is offline from 04/19 to 05/21. | 1. SR078160
San Antonio - Ops Ctr (Bldg 104) | TX | 12444.6026 | 11998.25 | 446.3526 | 3.72% | 16668.79 | -4224.1874 | -25.34%
San Antonio - Ops Ctr (Bldg 102) | TX | 46297.2009 | 38314.84 | 7982.3609 | 20.83% | 59195.52 | -12898.3191 | -21.79%
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA

## Jun
Wells Fargo |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 1647441.7458 | 1476847.6836 | 170594.0622 | 11.55% | 1783190.2568 | -135748.511 | -7.613% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1302.5 | 0 | 1302.5 |  | 1338 | -35.5 | -2.653%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0
San Leandro | CA | 55493.5 | 48496.34 | 6997.16 | 14.43% | 51502.16 | 3991.34 | 7.75% | 1. Site offline from 14:45 on 06/28 due to fire accident 2. Inverters 2,4 & 9 are underperforming approximately 4kW each compared to peers possibly string down from 05/13 | 1. SR087113 2. SR084620
Van Nuys | CA | 2143.5 | 0 | 2143.5 |  | 2745.138 | -601.638 | -21.92%
98th & Grant | CO | 1802.6 | 0 | 1802.6 |  | 2315 | -512.4 | -22.13%
Arapahoe Crossings | CO | 4794.0936 | 0 | 4794.0936 |  | 4259.673 | 534.4206 | 12.55%
Aurora City Center | CO | 2301.8 | 0 | 2301.8 |  | 1950 | 351.8 | 18.04%
Dry Creek | CO | 2299.4 | 0 | 2299.4 |  | 2528 | -228.6 | -9.043%
Highlands Ranch S. | CO | 2328.4 | 0 | 2328.4 |  | 2420 | -91.6 | -3.785%
Lone Tree | CO | 4014.3 | 0 | 4014.3 |  | 5490 | -1475.7 | -26.88%
Meridian | CO | 3774.1 | 0 | 3774.1 |  | 3132 | 642.1 | 20.5%
Southglenn | CO | 3726.1 | 0 | 3726.1 |  | 3205.5 | 520.6 | 16.24%
Standley Lake | CO | 4128 | 0 | 4128 |  | 4331 | -203 | -4.687%
Havana Gardens | CO | 4434.2 | 0 | 4434.2 |  | 1684 | 2750.2 | 163.3%
East Hartford | CT | 951.1 | 773.5046 | 177.5954 | 22.96% | 896.4028 | 54.6972 | 6.102%
Norwalk | CT | 908.6101 | 1108.747 | -200.1369 | -18.05% | 1048.102 | -139.4919 | -13.31% | 1. Intermittent meter phase C/power factor issue slightly impacting reported energy production | 1. SR077700
Hialeah Gardens | FL | 734.2011 | 3579.21 | -2845.0089 | -79.49% | 5101 | -4366.7989 | -85.61% | 1. Site production is dropping consistently from the mid of the day due to fan fault. | 1. SR081410
West Des Moines - HMHQ | IA | 0 | 0 | 0 |  | 0 | 0
W. Des Moines Campus EAST | IA | 194184.5 | 182837.9 | 11346.6 | 6.206% | 203700 | -9515.5 | -4.671%
W. Des Moines Campus SW | IA | 92267.5825 | 88720.85 | 3546.7325 | 3.998% | 100620.1 | -8352.5175 | -8.301%
WF - CIC | NC | 197870 | 143619.364 | 54250.636 | 37.77% | 209637 | -11767 | -5.613%
Charlotte - Wells Fargo - DUC | NC | 197870 | 143619.4 | 54250.6 | 37.77% | 212196 | -14326 | -6.751% | 1. Inverter 13 is underperforming by 5kW compared to peers possibly string down 2. Weather station reporting zero value from 05/24 due to that expected value is reporting zero | 1. SR086520 2. SR087337
East Windsor | NJ | 1294.2 | 1231.601 | 62.599 | 5.083% | 1076.519 | 217.681 | 20.22%
Burlington | NJ | 3286.9 | 3285.284 | 1.616 | 0.04919% | 2804.51 | 482.39 | 17.2%
Bayonne | NJ | 4088.4 | 3857.13 | 231.27 | 5.996% | 3847.406 | 240.994 | 6.264%
Clifton | NJ | 4932.4071 | 5090.931 | -158.5239 | -3.114% | 4897.527 | 34.8801 | 0.7122%
North Elizabeth | NJ | 4334.1 | 4034.583 | 299.517 | 7.424% | 3606.833 | 727.267 | 20.16%
Haddon Westmont Plaza | NJ | 3187.2 | 3169.668 | 17.532 | 0.5531% | 2654.475 | 532.725 | 20.07%
Parsippany | NJ | 3725.6 | 3610.257 | 115.343 | 3.195% | 2929.755 | 795.845 | 27.16%
Clark | NJ | 3139 | 3101.724 | 37.276 | 1.202% | 2505.601 | 633.399 | 25.28%
Closter | NJ | 1760.8 | 1378.245 | 382.555 | 27.76% | 1551.144 | 209.656 | 13.52%
Holmdel | NJ | 2733.1 | 2546.924 | 186.176 | 7.31% | 2188.446 | 544.654 | 24.89%
Ellisburg Circle Center | NJ | 1398.9 | 1433.891 | -34.991 | -2.44% | 1220.777 | 178.123 | 14.59%
Nutley | NJ | 4337.6 | 4256.489 | 81.111 | 1.906% | 4351.121 | -13.521 | -0.3107%
Marlton | NJ | 4968.1 | 4743.054 | 225.046 | 4.745% | 4288.961 | 679.139 | 15.83%
Middletown | NJ | 3857.2 | 3735.696 | 121.504 | 3.253% | 3432.157 | 425.043 | 12.38%
Whiting Crestwood | NJ | 4889.2 | 4682.134 | 207.066 | 4.422% | 4595.965 | 293.235 | 6.38%
Barnegat | NJ | 7614.8125 | 6775.413 | 839.3995 | 12.39% | 6492.996 | 1121.8165 | 17.28%
Manchester | NJ | 3599.4 | 3201.31 | 398.09 | 12.44% | 3846.748 | -247.348 | -6.43%
West Deptford - Woodbury | NJ | 4323.6 | 4638.197 | -314.597 | -6.783% | 3641.503 | 682.097 | 18.73%
Edison | NJ | 3855.2 | 3981.41 | -126.21 | -3.17% | 3168.94 | 686.26 | 21.66%
Flemington | NJ | 3795.7 | 4159.794 | -364.094 | -8.753% | 3308.512 | 487.188 | 14.73%
Route 22 | NJ | 3628.9 | 4007.815 | -378.915 | -9.454% | 2937.025 | 691.875 | 23.56%
Laurelton | NJ | 2283.9 | 3274.799 | -990.899 | -30.26% | 2916.671 | -632.771 | -21.69% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 | 1. SR075812
Mahwah | NJ | 3024.6 | 2587.571 | 437.029 | 16.89% | 2702.886 | 321.714 | 11.9%
Franklin Township WF | NJ | 3408.3 | 3488.055 | -79.755 | -2.287% | 3345.446 | 62.854 | 1.879%
Bordentown | NJ | 2535.4 | 2418.319 | 117.081 | 4.841% | 2080.553 | 454.847 | 21.86%
South Plainfield | NJ | 1893.4 | 1943.485 | -50.085 | -2.577% | 1536.942 | 356.458 | 23.19%
Somerset | NJ | 3129 | 3804.641 | -675.641 | -17.76% | 2561.151 | 567.849 | 22.17%
Clinton Main Relo | NJ | 3663.078 | 3656.995 | 6.083 | 0.1663% | 3087.542 | 575.536 | 18.64%
North Brunswick | NJ | 3776.8 | 3598.601 | 178.199 | 4.952% | 3328.077 | 448.723 | 13.48%
Cherry Hill | NJ | 2581.293 | 2467.991 | 113.302 | 4.591% | 2200.033 | 381.26 | 17.33%
Hainesport | NJ | 2600.3 | 3075.163 | -474.863 | -15.44% | 2141.351 | 458.949 | 21.43%
San Antonio - Ops Ctr (Bldg 106) | TX | 52290.486 | 47834.573 | 4455.913 | 9.315% | 60655.494 | -8365.008 | -13.79% | 1. Inverter 5 is underperforming approximately 20kW compared to peers possibly string down | 1. SR085492
San Antonio - Ops Ctr GM | TX | 355521.5 | 409610.431 | -54088.931 | -13.2% | 435826 | -80304.5 | -18.43% | 1. Inverter 2 is derating by 25kW from 05/11/2024. Inverter 8 is underperforming approximately 50kW compared to its peers from 05/10/2024. 2. Inverter 17 is derating by 75kW from 05/28/2024. | 1. SR084558 2. SR085239
San Antonio - Ctr (Bldg 201) | TX | 56524.156 | 47478.758 | 9045.398 | 19.05% | 59706.662 | -3182.506 | -5.33%
San Antonio - Ops Ctr (Bldg 203) | TX | 57061.374 | 54811.429 | 2249.945 | 4.105% | 60005.59 | -2944.216 | -4.907%
San Antonio - Ops Ctr (Bldg 205) | TX | 55028.281 | 43263.522 | 11764.759 | 27.19% | 57390.643 | -2362.362 | -4.116%
San Antonio - Ops Ctr (Bldg 307) | TX | 56682.751 | 47055.499 | 9627.252 | 20.46% | 58213.548 | -1530.797 | -2.63%
San Antonio - Ctr (Bldg 308) | TX | 53308.844 | 45977.633 | 7331.211 | 15.95% | 55434.508 | -2125.664 | -3.835%
San Antonio - Ops Ctr (Bldg 104) | TX | 16120.163 | 14406.903 | 1713.26 | 11.89% | 17588.343 | -1468.18 | -8.347%
San Antonio - Ops Ctr (Bldg 102) | TX | 59929.313 | 46416.45 | 13512.863 | 29.11% | 63022.82 | -3093.507 | -4.909%
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA

## Jul
Wells Fargo |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 1488980.0487 | 1268527.9116 | 220452.1371 | 17.38% | 1757021.1966 | -268041.1479 | -15.26% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1411.6 | 0 | 1411.6 |  | 1364 | 47.6 | 3.49%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0
San Leandro | CA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site offline from 14:45 on 06/28 due to fire accident. Inverter 9 being RMA'd 2. Inverter 3 is being RMA'd | 1. SR087113 2. SR088261
Van Nuys | CA | 2214.9 | 0 | 2214.9 |  | 2748.967 | -534.067 | -19.43%
98th & Grant | CO | 1669.2 | 0 | 1669.2 |  | 2218 | -548.8 | -24.74%
Arapahoe Crossings | CO | 4848.4111 | 0 | 4848.4111 |  | 4164.246 | 684.1651 | 16.43%
Aurora City Center | CO | 2353.4 | 0 | 2353.4 |  | 1923 | 430.4 | 22.38%
Dry Creek | CO | 2784.7 | 0 | 2784.7 |  | 2426 | 358.7 | 14.79%
Highlands Ranch S. | CO | 2403.1 | 0 | 2403.1 |  | 2380 | 23.1 | 0.9706%
Lone Tree | CO | 3800.6 | 0 | 3800.6 |  | 5432 | -1631.4 | -30.03%
Meridian | CO | 3794.9 | 0 | 3794.9 |  | 3145 | 649.9 | 20.66%
Southglenn | CO | 3845.4 | 0 | 3845.4 |  | 3163.129 | 682.271 | 21.57%
Standley Lake | CO | 3929.6 | 0 | 3929.6 |  | 4231 | -301.4 | -7.124%
Havana Gardens | CO | 4528.7 | 0 | 4528.7 |  | 1646 | 2882.7 | 175.1%
East Hartford | CT | 888.1 | 734.2972 | 153.8028 | 20.95% | 933.4506 | -45.3506 | -4.858%
Norwalk | CT | 990.3 | 257.4814 | 732.8186 | 284.6% | 1148.105 | -157.805 | -13.74% | 1. Intermittent meter phase C/power factor issue slightly impacting reported energy production. 2. Weather station reporting erroneous values from 07/04 due to that expected values are low | 1. SR077700. 2. SR088667
Hialeah Gardens | FL | 729.7035 | 4075.184 | -3345.4805 | -82.09% | 5675 | -4945.2965 | -87.14% | 1. Site production is dropping consistently from the mid of the day due to fan fault. | 1. SR081410
West Des Moines - HMHQ | IA | 0 | 0 | 0 |  | 0 | 0
W. Des Moines Campus EAST | IA | 192946.5 | 186007 | 6939.5 | 3.731% | 204900 | -11953.5 | -5.834%
W. Des Moines Campus SW | IA | 91996.6675 | 90625.73 | 1370.9375 | 1.513% | 101023.9 | -9027.2325 | -8.936%
WF - CIC | NC | 175064 | 145225.441 | 29838.559 | 20.55% | 210055.387 | -34991.387 | -16.66% | 1. Inverter 13 tripped offline at 14:00 on 07/05. Inverter 13 back online on 07/24 at 15:15 but faulted string #10 is isolated | 1. SR087433
Charlotte - Wells Fargo - DUC | NC | 150418.75 | 0 | 150418.75 |  | 180448.388 | -30029.638 | -16.64% | 1. Inverter 13 was underperforming till technician troubleshoot it on 07/25 2. Weather station reporting zero value from 05/24 due to that expected value is reporting zero. Parts being RMA'd 3. Inverter 4 tripped offline at 14:30 on 07/01 and back online on 07/05 4. All inverters reporting 0.8kW from 07/26 due to utility power sent is being curtailed | 1. SR086520 2. SR087337 3. SR087215 4. SR088287
East Windsor | NJ | 1155.3 | 1095.469 | 59.831 | 5.462% | 1208.607 | -53.307 | -4.411%
Burlington | NJ | 2993.8 | 2912.818 | 80.982 | 2.78% | 3087.839 | -94.039 | -3.045%
Bayonne | NJ | 3964.1 | 3750.517 | 213.583 | 5.695% | 3894.253 | 69.847 | 1.794%
Clifton | NJ | 4677.3351 | 4815.889 | -138.5539 | -2.877% | 5116.956 | -439.6209 | -8.591%
North Elizabeth | NJ | 4082.5 | 3901.668 | 180.832 | 4.635% | 3922.77 | 159.73 | 4.072%
Haddon Westmont Plaza | NJ | 2917.7 | 2873.323 | 44.377 | 1.544% | 2890.645 | 27.055 | 0.936%
Parsippany | NJ | 3537 | 3474.839 | 62.161 | 1.789% | 3456.696 | 80.304 | 2.323%
Clark | NJ | 2908.7 | 2884.707 | 23.993 | 0.8317% | 2822.704 | 85.996 | 3.047%
Closter | NJ | 1612.4 | 1281.922 | 330.478 | 25.78% | 1748.149 | -135.749 | -7.765%
Holmdel | NJ | 2535.6 | 2345.395 | 190.205 | 8.11% | 2343.728 | 191.872 | 8.187%
Ellisburg Circle Center | NJ | 1296 | 1296.314 | -0.314 | -0.02422% | 1338.94 | -42.94 | -3.207%
Nutley | NJ | 4083.8 | 3909.39 | 174.41 | 4.461% | 4942.42 | -858.62 | -17.37%
Marlton | NJ | 4588.3 | 4254.448 | 333.852 | 7.847% | 4606.266 | -17.966 | -0.39%
Middletown | NJ | 3657.5 | 3447.196 | 210.304 | 6.101% | 3697.459 | -39.959 | -1.081%
Whiting Crestwood | NJ | 4539.1 | 4486.699 | 52.401 | 1.168% | 4998.502 | -459.402 | -9.191%
Barnegat | NJ | 7034.7853 | 6283.319 | 751.4663 | 11.96% | 6906.281 | 128.5043 | 1.861%
Manchester | NJ | 2843.9 | 2905.58 | -61.68 | -2.123% | 4215.938 | -1372.038 | -32.54%
West Deptford - Woodbury | NJ | 4039.3 | 4290.577 | -251.277 | -5.856% | 3903.672 | 135.628 | 3.474%
Edison | NJ | 3549.5 | 3615.635 | -66.135 | -1.829% | 3626.513 | -77.013 | -2.124%
Flemington | NJ | 3569.2 | 3789.894 | -220.694 | -5.823% | 3749.948 | -180.748 | -4.82%
Route 22 | NJ | 3348.3 | 3747.618 | -399.318 | -10.66% | 3341.234 | 7.066 | 0.2115%
Laurelton | NJ | 2101.9 | 3004.435 | -902.535 | -30.04% | 3118.646 | -1016.746 | -32.6% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 2. Weather station reporting erroneous values throughout the month | 1. SR075812 2. Need to create SR
Mahwah | NJ | 2844.2 | 2158.717 | 685.483 | 31.75% | 3098.047 | -253.847 | -8.194%
Franklin Township WF | NJ | 3176.8 | 3187.578 | -10.778 | -0.3381% | 3470.484 | -293.684 | -8.462%
Bordentown | NJ | 2378.3 | 2222.15 | 156.15 | 7.027% | 2351.99 | 26.31 | 1.119%
South Plainfield | NJ | 1806.2 | 1844.113 | -37.913 | -2.056% | 1706.133 | 100.067 | 5.865%
Somerset | NJ | 2921.2 | 3517.632 | -596.432 | -16.96% | 2922.449 | -1.249 | -0.04274%
Clinton Main Relo | NJ | 3539.461 | 3562.142 | -22.681 | -0.6367% | 3451.412 | 88.049 | 2.551%
North Brunswick | NJ | 3458.9 | 3265.358 | 193.542 | 5.927% | 3756.723 | -297.823 | -7.928%
Cherry Hill | NJ | 2163.1211 | 2296.771 | -133.6499 | -5.819% | 2361.148 | -198.0269 | -8.387%
Hainesport | NJ | 2353 | 2793.045 | -440.045 | -15.76% | 2320.896 | 32.104 | 1.383%
San Antonio - Ops Ctr (Bldg 106) | TX | 49661.139 | 46930.806 | 2730.333 | 5.818% | 63389.421 | -13728.282 | -21.66% | 1. Inverter 5 is underperforming approximately 20kW compared to peers possibly string down | 1. SR085492
San Antonio - Ops Ctr GM | TX | 350704.5 | 402783.833 | -52079.333 | -12.93% | 461978.1 | -111273.6 | -24.09% | 1. Inverter 2 is derating by 25kW from 05/11/2024. Inverter 8 is underperforming approximately 50kW compared to its peers from 05/10/2024. 2. Inverter 17 is derating by 75kW from 05/28/2024. | 1. SR084558 2. SR085239
San Antonio - Ctr (Bldg 201) | TX | 54489.281 | 46578.779 | 7910.502 | 16.98% | 62615.616 | -8126.335 | -12.98%
San Antonio - Ops Ctr (Bldg 203) | TX | 54418.938 | 52813.016 | 1605.922 | 3.041% | 62892.113 | -8473.175 | -13.47%
San Antonio - Ops Ctr (Bldg 205) | TX | 52114.25 | 42443.104 | 9671.146 | 22.79% | 60005.89 | -7891.64 | -13.15%
San Antonio - Ops Ctr (Bldg 307) | TX | 53559.438 | 46159.535 | 7399.903 | 16.03% | 60930.061 | -7370.623 | -12.1%
San Antonio - Ctr (Bldg 308) | TX | 51207.063 | 45123.935 | 6083.128 | 13.48% | 58141.926 | -6934.863 | -11.93%
San Antonio - Ops Ctr (Bldg 104) | TX | 15240.455 | 14136.152 | 1104.303 | 7.812% | 18393.83 | -3153.375 | -17.14%
San Antonio - Ops Ctr (Bldg 102) | TX | 57289.25 | 45418.46 | 11870.79 | 26.14% | 65271.219 | -7981.969 | -12.23%
Lodi - Lodi Vineyard | CA
Arden Fair Mall | CA
Modesto - Modesto Main | CA
Stevens Creek | CA

## Aug
Wells Fargo |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 1566587.9435 | 1547343.9768 | 19243.9667 | 1.244% | 1863295.1633 | -296707.2198 | -15.92% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 1267.6 | 0 | 1267.6 |  | 1312 | -44.4 | -3.384%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0
San Leandro | CA | 34819.25 | 37068.39 | -2249.14 | -6.068% | 48909.82 | -14090.57 | -28.81% | 1. Site back online and reporting at 10:30 on 08/09 after the fire accident. Inverter 9 still offline and being RMA'd 2. Inverter 3 was replaced and back online on 08/09 | 1. SR087113,SR087742 2. SR088261
Van Nuys | CA | 1969.5 | 0 | 1969.5 |  | 2608.029 | -638.529 | -24.48%
98th & Grant | CO | 1183.8 | 0 | 1183.8 |  | 2124 | -940.2 | -44.27%
Arapahoe Crossings | CO | 2004.207 | 0 | 2004.207 |  | 3962.468 | -1958.261 | -49.42% | 1. Site stopped communicating at 09:20 PM on 08/17, production cannot be confirmed | 1. SR089204
Aurora City Center | CO | 2077.2 | 0 | 2077.2 |  | 1840 | 237.2 | 12.89%
Dry Creek | CO | 2326.9 | 0 | 2326.9 |  | 2319 | 7.9 | 0.3407%
Highlands Ranch S. | CO | 2007.8 | 0 | 2007.8 |  | 2235 | -227.2 | -10.17%
Lone Tree | CO | 3157 | 0 | 3157 |  | 5091 | -1934 | -37.99% | 1. Inverters stopped reporting from 06/13, technician confirmed one of the inverters is offline during PM4252 and needs to troubleshooted/replaced | 1. SR088671
Meridian | CO | 3324.4 | 0 | 3324.4 |  | 2948 | 376.4 | 12.77%
Southglenn | CO | 3334 | 0 | 3334
Standley Lake | CO | 3309.1 | 0 | 3309.1 |  | 4022 | -712.9 | -17.73%
Havana Gardens | CO | 3935.9 | 0 | 3935.9 |  | 1565 | 2370.9 | 151.5%
East Hartford | CT | 734.8 | 640.9022 | 93.8978 | 14.65% | 961.5963 | -226.7963 | -23.59%
Norwalk | CT | 870.3 | 16.0085 | 854.2915 | 5336% | 1230.292 | -359.992 | -29.26% | 1. Weather station reporting erroneous values from 07/04 due to that expected values are low. 2. Intermittent meter phase C/power factor issue slightly impacting reported energy production. | 1. SR088667 2. SR077700
Hialeah Gardens | FL | 743.3047 | 3420.608 | -2677.3033 | -78.27% | 5217 | -4473.6953 | -85.75%
West Des Moines - HMHQ | IA
W. Des Moines Campus EAST | IA | 186173.5 | 193027.8 | -6854.3 | -3.551% | 197900 | -11726.5 | -5.925% | 1. Inverter 6 is tripping on and off intermittently from 08/02 resulting in inverter being mostly offline. Issue occurring throughout the month | 1. SR088535
W. Des Moines Campus SW | IA | 96373.25 | 96472.78 | -99.53 | -0.1032% | 97637.28 | -1264.03 | -1.295%
WF - CIC | NC | 176476 | 186483 | -10007 | -5.366% | 192546 | -16070 | -8.346% | 1. Inverter 13 string #10 is isolated for further troubleshooting | 1. SR087433
Charlotte - Wells Fargo - DUC | NC | 5889 | 0 | 5889 |  | 174009 | -168120 | -96.62% | 1. Weather station reporting zero value from 05/24 due to that expected value is reporting zero. Parts being RMA'd by AlsoEnergy 2. Site was in curtailment throughout the month resulting in low site production | 1. SR088678, SR087337 2. SR088287
East Windsor | NJ | 1061.6 | 1022.334 | 39.266 | 3.841% | 1257.524 | -195.924 | -15.58%
Burlington | NJ | 2730.7 | 2582.508 | 148.192 | 5.738% | 3210.935 | -480.235 | -14.96%
Bayonne | NJ | 3307.6 | 3109.33 | 198.27 | 6.377% | 3672.28 | -364.68 | -9.931% | 1. Site stopped communicating at 09:45 PM on 08/30, production cannot be confirmed | 1. SR089791
Clifton | NJ | 4106.7891 | 4202.462 | -95.6729 | -2.277% | 4561.403 | -454.6139 | -9.967%
North Elizabeth | NJ | 3467 | 3220.966 | 246.034 | 7.639% | 4183.035 | -716.035 | -17.12%
Haddon Westmont Plaza | NJ | 2619.4 | 2534.839 | 84.561 | 3.336% | 3013.925 | -394.525 | -13.09%
Parsippany | NJ | 3032.1 | 3073.883 | -41.783 | -1.359% | 3492.794 | -460.694 | -13.19%
Clark | NJ | 2547.3 | 2460.185 | 87.115 | 3.541% | 2913.348 | -366.048 | -12.56% | 1. Site tripped offline at 04:35 PM on 08/14 due to meter phase B voltages dropped to zero and came back online on 08/15 | 1. SR089050
Closter | NJ | 1144.8 | 1032.165 | 112.635 | 10.91% | 1827.416 | -682.616 | -37.35%
Holmdel | NJ | 2176 | 1984.02 | 191.98 | 9.676% | 2536.394 | -360.394 | -14.21%
Ellisburg Circle Center | NJ | 1131 | 1143.687 | -12.687 | -1.109% | 1374.944 | -243.944 | -17.74%
Nutley | NJ | 3533 | 3341.516 | 191.484 | 5.73% | 5093.468 | -1560.468 | -30.64%
Marlton | NJ | 4137.1 | 3717.938 | 419.162 | 11.27% | 4774.142 | -637.042 | -13.34%
Middletown | NJ | 3217.9 | 2838.038 | 379.862 | 13.38% | 3968.413 | -750.513 | -18.91%
Whiting Crestwood | NJ | 4380.6 | 4353.65 | 26.95 | 0.619% | 5518.252 | -1137.652 | -20.62%
Barnegat | NJ | 6434.9803 | 5715.146 | 719.8343 | 12.6% | 6874.703 | -439.7227 | -6.396%
Manchester | NJ | 2518.1 | 2750.881 | -232.781 | -8.462% | 4727.076 | -2208.976 | -46.73%
West Deptford - Woodbury | NJ | 3770.7 | 3885.042 | -114.342 | -2.943% | 4121.148 | -350.448 | -8.504%
Edison | NJ | 3201.3 | 3106.009 | 95.291 | 3.068% | 3837.506 | -636.206 | -16.58%
Flemington | NJ | 3040.7 | 2887.549 | 153.151 | 5.304% | 3931.128 | -890.428 | -22.65%
Route 22 | NJ | 3055.9 | 3276.239 | -220.339 | -6.725% | 3522.667 | -466.767 | -13.25%
Laurelton | NJ | 1908.7 | 2640.474 | -731.774 | -27.71% | 3325.338 | -1416.638 | -42.6% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 | 1. SR075812
Mahwah | NJ | 2399.3 | 505.1301 | 1894.1699 | 375% | 3147.107 | -747.807 | -23.76%
Franklin Township WF | NJ | 2768.8 | 2721.068 | 47.732 | 1.754% | 3211.349 | -442.549 | -13.78%
Bordentown | NJ | 2181.3 | 1946.592 | 234.708 | 12.06% | 2540.332 | -359.032 | -14.13%
South Plainfield | NJ | 1573.8 | 1529.813 | 43.987 | 2.875% | 1799.165 | -225.365 | -12.53%
Somerset | NJ | 2549.6 | 3202.76 | -653.16 | -20.39% | 3004.865 | -455.265 | -15.15%
Clinton Main Relo | NJ | 2980 | 3021 | -41 | -1.357% | 3368 | -388 | -11.52%
North Brunswick | NJ | 2988.4 | 2780.64 | 207.76 | 7.472% | 3875.399 | -886.999 | -22.89%
Cherry Hill | NJ | 1970.4258 | 2061.014 | -90.5882 | -4.395% | 2446.057 | -475.6312 | -19.44%
Hainesport | NJ | 2161.7 | 2539.853 | -378.153 | -14.89% | 2483.505 | -321.805 | -12.96%
San Antonio - Ops Ctr (Bldg 106) | TX | 54566 | 52913 | 1653 | 3.124% | 63500 | -8934 | -14.07% | 1. Inverter 5 is underperforming approximately 20kW compared to peers thorughout the month due to issue with RSD unit, requires further troubleshooting | 1. SR085492
San Antonio - Ops Ctr GM | TX | 421456 | 465519 | -44063 | -9.465% | 451447 | -29991 | -6.643%
San Antonio - Ctr (Bldg 201) | TX | 61297 | 52526 | 8771 | 16.7% | 63191 | -1894 | -2.997%
San Antonio - Ops Ctr (Bldg 203) | TX | 61274 | 58279 | 2995 | 5.139% | 63558 | -2284 | -3.594%
San Antonio - Ops Ctr (Bldg 205) | TX | 57335 | 47863 | 9472 | 19.79% | 60140 | -2805 | -4.664%
San Antonio - Ops Ctr (Bldg 307) | TX | 59578 | 52055 | 7523 | 14.45% | 61282 | -1704 | -2.781%
San Antonio - Ctr (Bldg 308) | TX | 57583 | 50863 | 6720 | 13.21% | 58480 | -897 | -1.534%
San Antonio - Ops Ctr (Bldg 104) | TX | 16467 | 15938 | 529 | 3.319% | 18417 | -1950 | -10.59%
San Antonio - Ops Ctr (Bldg 102) | TX | 63523.393 | 50685.49 | 12837.903 | 25.33% | 65934.24 | -2410.847 | -3.656%
Lodi - Lodi Vineyard | CA | 47549.8414 | 51076.54 | -3526.6986 | -6.905% | 42061 | 5488.8414 | 13.05%
Arden Fair Mall | CA | 22460.9688 | 23630.99 | -1170.0213 | -4.951% | 27363 | -4902.0312 | -17.91%
Modesto - Modesto Main | CA | 17417.9283 | 17500.46 | -82.5317 | -0.4716% | 24836.82 | -7418.8917 | -29.87% | 1. Site was offline from 08/25 at 04:00 and back online at 08:00 on 08/25 | 1. SR089603
Stevens Creek | CA | 6006.4051 | 6178.277 | -171.8719 | -2.782% | 7034 | -1027.5949 | -14.61%

## Sep
Wells Fargo |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 1416736.0228 | 1382754.7649 | 33981.2579 | 2.458% | 1619330.3392 | -202594.3164 | -12.51% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 900 | 0 | 900 |  | 1067 | -167 | -15.65%
Otay Mesa | CA
San Leandro | CA | 37285.375 | 42375.51 | -5090.135 | -12.01% | 41155.66 | -3870.285 | -9.404% | 1.The site has been turned offline for maintenance at 10:15 PDT on 09/26/2024 and back online at 16:00 PDT on 09/27/2024 | 1.SR091313
Van Nuys | CA | 1536.6 | 0 | 1536.6 |  | 2147.166 | -610.566 | -28.44%
98th & Grant | CO | 1154.3 | 0 | 1154.3 |  | 1914 | -759.7 | -39.69%
Arapahoe Crossings | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site stopped communicating at 09:20 PM on 08/17, production cannot be confirmed | 1. SR089204
Aurora City Center | CO | 2026.4 | 0 | 2026.4 |  | 1642 | 384.4 | 23.41%
Dry Creek | CO | 2364.1 | 0 | 2364.1 |  | 2079 | 285.1 | 13.71%
Highlands Ranch S. | CO | 1974.2 | 0 | 1974.2 |  | 1934 | 40.2 | 2.079%
Lone Tree | CO | 3086.8 | 0 | 3086.8 |  | 4395 | -1308.2 | -29.77%
Meridian | CO | 3139.2 | 0 | 3139.2 |  | 2534 | 605.2 | 23.88%
Southglenn | CO | 3233.5 | 0 | 3233.5 |  | 2652 | 581.5 | 21.93%
Standley Lake | CO | 3244.8 | 0 | 3244.8 |  | 3536 | -291.2 | -8.235%
Havana Gardens | CO | 3718.2 | 0 | 3718.2 |  | 1378 | 2340.2 | 169.8%
East Hartford | CT | 643.6 | 585.9053 | 57.6947 | 9.847% | 786.0682 | -142.4682 | -18.12%
Norwalk | CT | 780.0703 | 13.8003 | 766.27 | 5553% | 933.6405 | -153.5702 | -16.45%
Hialeah Gardens | FL | 1436.4997 | 3501.072 | -2064.5723 | -58.97% | 4497 | -3060.5003 | -68.06% | 1. Site peaks at about 5kw, then around noon drops to 1.5KW on 09/17/2024 . Likely due to inverters offline and heat issues 2. Inverter stuck in start up and standby mode on 09/21/2024- Fronius will not RMA inv due to thermal issues on site | 1. SR091062 2. SR091062
West Des Moines - HMHQ | IA
W. Des Moines Campus EAST | IA | 178457 | 189582.3 | -11125.3 | -5.868% | 182300 | -3843 | -2.108%
W. Des Moines Campus SW | IA | 92416.5 | 98140.95 | -5724.45 | -5.833% | 89997.12 | 2419.38 | 2.688%
WF - CIC | NC | 116190 | 135991.9 | -19801.9 | -14.56% | 165450 | -49260 | -29.77% | 1. AlsoEnergy conducting an assessment/adjustment of the RTAC settings that interact with the Duke Energy RTU on 09/06/2024 and more over AE made changes on 09/09/2024 and site is producing full power 2. Inverter 13 is offline on 09/26/2024 and reporting an isolation fault. Weather related. | 1. SR090058 2. SR091286
Charlotte - Wells Fargo - DUC | NC | 83886 | 0 | 83886 |  | 157620.3 | -73734.3 | -46.78%
East Windsor | NJ | 818.1 | 825.9029 | -7.8029 | -0.9448% | 924.9545 | -106.8545 | -11.55%
Burlington | NJ | 2146.6 | 2008.808 | 137.792 | 6.859% | 2402.242 | -255.642 | -10.64%
Bayonne | NJ | 1858.7 | 1768.404 | 90.296 | 5.106% | 3042.637 | -1183.937 | -38.91%
Clifton | NJ | 3442.5156 | 3481.042 | -38.5264 | -1.107% | 3951.995 | -509.4794 | -12.89%
North Elizabeth | NJ | 2962.1 | 2436.091 | 526.009 | 21.59% | 3201.151 | -239.051 | -7.468%
Haddon Westmont Plaza | NJ | 2025.7 | 1971.989 | 53.711 | 2.724% | 2263.927 | -238.227 | -10.52%
Parsippany | NJ | 2610.9 | 2709.693 | -98.793 | -3.646% | 2853.919 | -243.019 | -8.515%
Clark | NJ | 2076.4 | 1978.445 | 97.955 | 4.951% | 2230.972 | -154.572 | -6.928%
Closter | NJ | 479.1 | 842.4615 | -363.3615 | -43.13% | 1441.564 | -962.464 | -66.77% | 1.Inverter is kept offline intentionally and is being rmad from 12:00 on 09/16/2024 | 1.SR090634
Holmdel | NJ | 1789.6 | 1617.319 | 172.281 | 10.65% | 1952.598 | -162.998 | -8.348%
Ellisburg Circle Center | NJ | 909.6 | 895.6295 | 13.9705 | 1.56% | 1045.343 | -135.743 | -12.99%
Nutley | NJ | 3011.1 | 2804.825 | 206.275 | 7.354% | 4042.425 | -1031.325 | -25.51%
Marlton | NJ | 3271.3 | 2842.605 | 428.695 | 15.08% | 3619.303 | -348.003 | -9.615%
Middletown | NJ | 2769.2 | 1957.095 | 812.105 | 41.5% | 3146.534 | -377.334 | -11.99%
Whiting Crestwood | NJ | 3470 | 3465.274 | 4.726 | 0.1364% | 4196.949 | -726.949 | -17.32%
Barnegat | NJ | 4588.3125 | 4168.44 | 419.8725 | 10.07% | 5027.721 | -439.4085 | -8.74%
Manchester | NJ | 1990.9 | 2216.2 | -225.3 | -10.17% | 3620.607 | -1629.707 | -45.01%
West Deptford - Woodbury | NJ | 3064.6 | 3070.614 | -6.014 | -0.1959% | 3363.597 | -298.997 | -8.889%
Edison | NJ | 2802.7 | 2509.302 | 293.398 | 11.69% | 3087.868 | -285.168 | -9.235%
Flemington | NJ | 2501.3 | 2221.212 | 280.088 | 12.61% | 2959.683 | -458.383 | -15.49%
Route 22 | NJ | 2492.3 | 3050.304 | -558.004 | -18.29% | 2711.023 | -218.723 | -8.068%
Laurelton | NJ | 1477 | 1986.796 | -509.796 | -25.66% | 2471.509 | -994.509 | -40.24% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 | 1. SR075812
Mahwah | NJ | 2033.2 | 551.5364 | 1481.6636 | 268.6% | 2409.188 | -375.988 | -15.61%
Franklin Township WF | NJ | 2316.7 | 2163.07 | 153.63 | 7.102% | 2815.273 | -498.573 | -17.71%
Bordentown | NJ | 1810.7 | 1551.235 | 259.465 | 16.73% | 2049.341 | -238.641 | -11.64%
South Plainfield | NJ | 1354.8 | 1217.938 | 136.862 | 11.24% | 1472.853 | -118.053 | -8.015%
Somerset | NJ | 2091 | 2689.127 | -598.127 | -22.24% | 2386.735 | -295.735 | -12.39%
Clinton Main Relo | NJ | 2455.2422 | 2492.929 | -37.6868 | -1.512% | 2742.876 | -287.6338 | -10.49%
North Brunswick | NJ | 1036.6 | 2172.238 | -1135.638 | -52.28% | 3003.611 | -1967.011 | -65.49% | 1. The PV inverter tripped offline from 09/10/2024, reporting an IsolationErr code | 1. SR090252
Cherry Hill | NJ | 1582.8359 | 1686.58 | -103.7441 | -6.151% | 1879.415 | -296.5791 | -15.78%
Hainesport | NJ | 1707.5 | 1891.417 | -183.917 | -9.724% | 1913.061 | -205.561 | -10.75%
San Antonio - Ops Ctr (Bldg 106) | TX | 49778.8125 | 49279.45 | 499.3625 | 1.013% | 56349.73 | -6570.9175 | -11.66%
San Antonio - Ops Ctr GM | TX | 367458 | 411610.8 | -44152.8 | -10.73% | 376464 | -9006 | -2.392%
San Antonio - Ctr (Bldg 201) | TX | 51428.0625 | 48918 | 2510.0625 | 5.131% | 55838.68 | -4410.6175 | -7.899%
San Antonio - Ops Ctr (Bldg 203) | TX | 52725.125 | 50731.52 | 1993.605 | 3.93% | 56750.84 | -4025.715 | -7.094%
San Antonio - Ops Ctr (Bldg 205) | TX | 48459.0625 | 44575.95 | 3883.1125 | 8.711% | 53363.67 | -4904.6075 | -9.191%
San Antonio - Ops Ctr (Bldg 307) | TX | 50566.625 | 48478.5 | 2088.125 | 4.307% | 54554.13 | -3987.505 | -7.309%
San Antonio - Ctr (Bldg 308) | TX | 49535.2641 | 47372.51 | 2162.7541 | 4.565% | 52593.14 | -3057.8759 | -5.814%
San Antonio - Ops Ctr (Bldg 104) | TX | 13377.2172 | 14845.64 | -1468.4228 | -9.891% | 16348.51 | -2971.2928 | -18.17%
San Antonio - Ops Ctr (Bldg 102) | TX | 54853.5625 | 46132.79 | 8720.7725 | 18.9% | 59006.68 | -4153.1175 | -7.038%
Lodi - Lodi Vineyard | CA | 36046.0312 | 42688.77 | -6642.7387 | -15.56% | 36116 | -69.9688 | -0.1937%
Arden Fair Mall | CA | 17602.2031 | 20817.29 | -3215.0869 | -15.44% | 22974 | -5371.7969 | -23.38%
Modesto - Modesto Main | CA | 13587.3158 | 14947.89 | -1360.5742 | -9.102% | 21215.13 | -7627.8142 | -35.95%
Stevens Creek | CA | 4898.9901 | 4919.695 | -20.7049 | -0.4209% | 5507 | -608.0099 | -11.04% | 1. Inverter 1 lost communication at 17:15 on 09/23,possibly offline | 1.SR091107

## Oct
Wells Fargo |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 1476085.2979 | 1553629.4537 | -77544.1558 | -4.991% | 1477232.1342 | -1146.8363 | -0.07763% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 680.4 |  |  |  | 864 | -183.6 | -21.25%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Weather station is started communicating from 10/15 | 1.SR092201
San Leandro | CA | 34820.75 | 41793.45 | -6972.7 | -16.68% | 34800.58 | 20.17 | 0.05796% | 1.Inverter 9 is re-energised on 10/04 at 13:30 PM 2.Inverter 4 is underperforming 8KW and Inverter 2,7 are underperforming by approximately 3KW down compared down to its peers. | 1.SR087742 2.SR091496
Van Nuys | CA | 1193.7 | 0 | 1193.7 |  | 1746.145 | -552.445 | -31.64%
98th & Grant | CO | 971.3 | 0 | 971.3 |  | 1610 | -638.7 | -39.67%
Arapahoe Crossings | CO | 2718.0946 | 0 | 2718.0946 |  | 2954.311 | -236.2164 | -7.996% | 1.Site is back online on 10/04 at 13:00 PM | 1.SR089204
Aurora City Center | CO | 1708.8 | 0 | 1708.8 |  | 1424 | 284.8 | 20%
Dry Creek | CO | 2041.9 | 0 | 2041.9 |  | 1742 | 299.9 | 17.22%
Highlands Ranch S. | CO | 1621.7 | 0 | 1621.7 |  | 1605 | 16.7 | 1.04%
Lone Tree | CO | 2526.1 | 0 | 2526.1 |  | 3663 | -1136.9 | -31.04%
Meridian | CO | 2562.7 | 0 | 2562.7 |  | 2150 | 412.7 | 19.2%
Southglenn | CO | 2662.8 | 0 | 2662.8 |  | 2239 | 423.8 | 18.93%
Standley Lake | CO | 2588.4 | 0 | 2588.4 |  | 2986 | -397.6 | -13.32%
Havana Gardens | CO | 3045.6 | 0 | 3045.6 |  | 1166 | 1879.6 | 161.2%
East Hartford | CT | 545.7 | 569.9687 | -24.2687 | -4.258% | 603.8138 | -58.1138 | -9.624%
Norwalk | CT | 675.6206 | 52.5238 | 623.0969 | 1186% | 717.8893 | -42.2687 | -5.888% | 1.Weather station is reporting erroneous values from 07/04/2024 | 1.SR088667
Hialeah Gardens | FL | 2492.9002 | 2776.394 | -283.4938 | -10.21% | 4137 | -1644.0998 | -39.74%
West Des Moines - HMHQ | IA
W. Des Moines Campus EAST | IA | 190907 | 191854.4 | -947.4 | -0.4938% | 154900 | 36007 | 23.25%
W. Des Moines Campus SW | IA | 91053 | 103986.3 | -12933.3 | -12.44% | 77012.73 | 14040.27 | 18.23% | 1.Meter is not capturing all inverters production due to drop in phase B current. Meter is reporting 30kW less than all inverters. B phase current is 60 amps lower than A and C currents. | 1.SR092064
WF - CIC | NC | 162259 | 165846.761 | -3587.761 | -2.163% | 163366.99 | -1107.99 | -0.6782%
Charlotte - Wells Fargo - DUC | NC | 161956.5 | 165938.6 | -3982.1 | -2.4% | 151539.16 | 10417.34 | 6.874%
East Windsor | NJ | 880.4 | 924.7235 | -44.3235 | -4.793% | 769.4904 | 110.9096 | 14.41%
Burlington | NJ | 2435.8 | 2039.797 | 396.003 | 19.41% | 1948.429 | 487.371 | 25.01%
Bayonne | NJ | 2844.7 | 2823.037 | 21.663 | 0.7674% | 2509.315 | 335.385 | 13.37%
Clifton | NJ | 3484.3281 | 3491.086 | -6.7579 | -0.1936% | 3276.999 | 207.3291 | 6.327%
North Elizabeth | NJ | 2628.9 | 2340.016 | 288.884 | 12.35% | 2680.354 | -51.454 | -1.92%
Haddon Westmont Plaza | NJ | 2056.9 | 1952.444 | 104.456 | 5.35% | 1870.032 | 186.868 | 9.993%
Parsippany | NJ | 2715.9 | 3143.237 | -427.337 | -13.6% | 2232.411 | 483.489 | 21.66%
Clark | NJ | 2129.2 | 1934.169 | 195.031 | 10.08% | 1818.579 | 310.621 | 17.08%
Closter | NJ | 319.9 | 535.6319 | -215.7319 | -40.28% | 1050.132 | -730.232 | -69.54% | 1.Inverter back online on 10/8 | 1.SR091644
Holmdel | NJ | 1878.2 | 1593.788 | 284.412 | 17.85% | 1540.111 | 338.089 | 21.95%
Ellisburg Circle Center | NJ | 911.8 | 920.3688 | -8.5688 | -0.931% | 857.2627 | 54.5373 | 6.362%
Nutley | NJ | 2875.9 | 2676.383 | 199.517 | 7.455% | 3242.086 | -366.186 | -11.29%
Marlton | NJ | 3564.7 | 2591.822 | 972.878 | 37.54% | 3019.942 | 544.758 | 18.04%
Middletown | NJ | 3115.8 | 2260.275 | 855.525 | 37.85% | 2632.213 | 483.587 | 18.37%
Whiting Crestwood | NJ | 4363.2 | 4624.792 | -261.592 | -5.656% | 3778.464 | 584.736 | 15.48%
Barnegat | NJ | 4731.2031 | 3816.909 | 914.2941 | 23.95% | 3906.647 | 824.5561 | 21.11%
Manchester | NJ | 2425.3 | 2729.621 | -304.321 | -11.15% | 3368.297 | -942.997 | -28%
West Deptford - Woodbury | NJ | 3865.6 | 3431.474 | 434.126 | 12.65% | 3102.823 | 762.777 | 24.58%
Edison | NJ | 3228.3 | 2499.333 | 728.967 | 29.17% | 2716.206 | 512.094 | 18.85%
Flemington | NJ | 2715.9 | 2287.201 | 428.699 | 18.74% | 2449.099 | 266.801 | 10.89%
Route 22 | NJ | 2834.7 | 3324.278 | -489.578 | -14.73% | 2313.89 | 520.81 | 22.51%
Laurelton | NJ | 1580.4 | 1955.651 | -375.251 | -19.19% | 2074.504 | -494.104 | -23.82% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 | 1.SR075812
Mahwah | NJ | 2013.4 | 1332.793 | 680.607 | 51.07% | 1915.701 | 97.699 | 5.1%
Franklin Township WF | NJ | 1892.8 | 1659.107 | 233.693 | 14.09% | 2197.633 | -304.833 | -13.87% | 1.Site offline from 10/19 on 13:45 and back online on 10/26 at 16:30. | 1. SR092402
Bordentown | NJ | 2269.2 | 1707.324 | 561.876 | 32.91% | 1813.99 | 455.21 | 25.09%
South Plainfield | NJ | 1526.1 | 1227.362 | 298.738 | 24.34% | 1246.43 | 279.67 | 22.44%
Somerset | NJ | 2296.2 | 3063.254 | -767.054 | -25.04% | 2006.157 | 290.043 | 14.46%
Clinton Main Relo | NJ | 2540.6641 | 2675.458 | -134.7939 | -5.038% | 2215.433 | 325.2311 | 14.68%
North Brunswick | NJ | 1687.7 | 2197.339 | -509.639 | -23.19% | 2472.428 | -784.728 | -31.74%
Cherry Hill | NJ | 1762.8828 | 1911.442 | -148.5592 | -7.772% | 1595.464 | 167.4188 | 10.49% | 1.Meter phase B current intermittently underreporting while inverter production unaffected. Reported energy loss may be retroactively corrected. | 1.SR077660
Hainesport | NJ | 2096.3 | 2076.671 | 19.629 | 0.9452% | 1701.55 | 394.75 | 23.2%
San Antonio - Ops Ctr (Bldg 106) | TX | 44778 | 49183.65 | -4405.65 | -8.958% | 48995.34 | -4217.34 | -8.608%
San Antonio - Ops Ctr GM | TX | 354578.5 | 402379.481 | -47800.981 | -11.88% | 368569.85 | -13991.35 | -3.796%
San Antonio - Ctr (Bldg 201) | TX | 45527.563 | 48827.54 | -3299.977 | -6.758% | 49001.29 | -3473.727 | -7.089%
San Antonio - Ops Ctr (Bldg 203) | TX | 47804.93 | 46856.28 | 948.65 | 2.025% | 50374.44 | -2569.51 | -5.101%
San Antonio - Ops Ctr (Bldg 205) | TX | 42735.674 | 44483.808 | -1748.134 | -3.93% | 46547.027 | -3811.353 | -8.188%
San Antonio - Ops Ctr (Bldg 307) | TX | 45090.3 | 48395.117 | -3304.817 | -6.829% | 47885.515 | -2795.215 | -5.837%
San Antonio - Ctr (Bldg 308) | TX | 43583.361 | 47290.87 | -3707.509 | -7.84% | 46551.9 | -2968.539 | -6.377%
San Antonio - Ops Ctr (Bldg 104) | TX | 9548.7 | 14818.6 | -5269.9 | -35.56% | 14249.4 | -4700.7 | -32.99%
San Antonio - Ops Ctr (Bldg 102) | TX | 48809.125 | 44825.09 | 3984.035 | 8.888% | 52102.041 | -3292.916 | -6.32%
Lodi - Lodi Vineyard | CA | 24356.2188 | 30860.61 | -6504.3913 | -21.08% | 30761 | -6404.7812 | -20.82%
Arden Fair Mall | CA | 12260.7188 | 16384.46 | -4123.7412 | -25.17% | 18570 | -6309.2812 | -33.98%
Modesto - Modesto Main | CA | 8507.75 | 10998.11 | -2490.36 | -22.64% | 18012.64 | -9504.89 | -52.77% | 1.IMT Ambient temperature sensor is not communicating. | 1.SR091735
Stevens Creek | CA | 3800.2137 | 3760.653 | 39.5607 | 1.052% | 4062 | -261.7863 | -6.445%
s

## Nov
Wells Fargo |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 1000281.1448 | 1102637.0541 | -102355.9093 | -9.283% | 1087384.6798 | -87103.535 | -8.01% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 533.8 | 0 | 533.8 |  | 696 | -162.2 | -23.3%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0
San Leandro | CA | 24847.25 | 32794 | -7946.75 | -24.23% | 26239.82 | -1392.57 | -5.307% | 1. Inverter 3 is offline from 7:00AM to 10:45AM on 11/24 2. Inverter 4 is underperforming 7KW and Inverter 2,7 are underperforming by approximately 3KW down compared to its peers. | 1. SR093579 2. SR091496, SR088261
Van Nuys | CA | 935.7 | 0 | 935.7 |  | 1405.826 | -470.126 | -33.44%
98th & Grant | CO | 531 | 0 | 531 |  | 1195 | -664 | -55.56%
Arapahoe Crossings | CO | 1651.0054 | 0 | 1651.0054 |  | 2162.681 | -511.6756 | -23.66%
Aurora City Center | CO | 941.6 | 0 | 941.6 |  | 1064 | -122.4 | -11.5%
Dry Creek | CO | 1130.9 | 0 | 1130.9 |  | 1287 | -156.1 | -12.13%
Highlands Ranch S. | CO | 840.9 | 0 | 840.9 |  | 1141 | -300.1 | -26.3%
Lone Tree | CO | 1466.5 | 0 | 1466.5 |  | 2625 | -1158.5 | -44.13%
Meridian | CO | 1541.5 | 0 | 1541.5 |  | 1548 | -6.5 | -0.4199%
Southglenn | CO |  | 0
Standley Lake | CO | 1610.1 | 0 | 1610.1 |  | 2181 | -570.9 | -26.18%
Havana Gardens | CO | 1551.5 | 0 | 1551.5 |  | 853 | 698.5 | 81.89%
East Hartford | CT | 330 | 407.3371 | -77.3371 | -18.99% | 381.4008 | -51.4008 | -13.48%
Norwalk | CT | 385.9 | 205.9931 | 179.9069 | 87.34% | 451.1932 | -65.2932 | -14.47% | 1. Weather station reporting erroneous values from 07/04/2024 | 1. SR088667
Hialeah Gardens | FL | 2503.6039 | 2947.127 | -443.5231 | -15.05% | 3330 | -826.3961 | -24.82%
West Des Moines - HMHQ | IA | 0 | 0 | 0 |  | 0 | 0
W. Des Moines Campus EAST | IA | 95506.5 | 102912.1 | -7405.6 | -7.196% | 109300 | -13793.5 | -12.62%
W. Des Moines Campus SW | IA | 49492.75 | 58672.7 | -9179.95 | -15.65% | 56047.79 | -6555.04 | -11.7% | 1. Meter is not capturing all inverters production due to drop in phase B current. Meter is reporting 30kW less than all inverters. B phase current is 60 amps lower than A and C currents from 10/11 to 11/05 | 1. SR092064
WF - CIC | NC | 99330 | 98282.06 | 1047.94 | 1.066% | 116623 | -17293 | -14.83%
Charlotte - Wells Fargo - DUC | NC | 96341 | 112449.8 | -16108.8 | -14.33% | 131113.7 | -34772.7 | -26.52%
East Windsor | NJ | 540.2 | 605.5006 | -65.3006 | -10.78% | 516.3958 | 23.8042 | 4.61%
Burlington | NJ | 1568.6 | 1266.532 | 302.068 | 23.85% | 1289.854 | 278.746 | 21.61%
Bayonne | NJ | 1820.7 | 1761.138 | 59.562 | 3.382% | 1887.599 | -66.899 | -3.544%
Clifton | NJ | 2081.2109 | 2245.136 | -163.9251 | -7.301% | 2547.254 | -466.0431 | -18.3%
North Elizabeth | NJ | 1624.9 | 1416.063 | 208.837 | 14.75% | 1724.608 | -99.708 | -5.781%
Haddon Westmont Plaza | NJ | 1122.8 | 1196.225 | -73.425 | -6.138% | 1224.774 | -101.974 | -8.326%
Parsippany | NJ | 1642.6 | 2118.97 | -476.37 | -22.48% | 1489.945 | 152.655 | 10.25%
Clark | NJ | 1306.8 | 1207.878 | 98.922 | 8.19% | 1197.404 | 109.396 | 9.136%
Closter | NJ | 226.2 | 271.6192 | -45.4192 | -16.72% | 624.4837 | -398.2837 | -63.78%
Holmdel | NJ | 1129.9 | 991.861 | 138.039 | 13.92% | 1000.646 | 129.254 | 12.92%
Ellisburg Circle Center | NJ | 522.5 | 583.0385 | -60.5385 | -10.38% | 559.7479 | -37.2479 | -6.654%
Nutley | NJ | 1714.3 | 1688.807 | 25.493 | 1.51% | 2125.604 | -411.304 | -19.35%
Marlton | NJ | 2250.8 | 1561.603 | 689.197 | 44.13% | 2028.546 | 222.254 | 10.96%
Middletown | NJ | 2156.1 | 1489.972 | 666.128 | 44.71% | 1903.302 | 252.798 | 13.28%
Whiting Crestwood | NJ | 3074.4 | 3133.589 | -59.189 | -1.889% | 2781.804 | 292.596 | 10.52%
Barnegat | NJ | 2872.9062 | 2168.042 | 704.8643 | 32.51% | 2453.069 | 419.8373 | 17.11%
Manchester | NJ | 1634.3 | 1849.991 | -215.691 | -11.66% | 2528.85 | -894.55 | -35.37%
West Deptford - Woodbury | NJ | 2655.8 | 2226.352 | 429.448 | 19.29% | 2296.058 | 359.742 | 15.67%
Edison | NJ | 2130.1 | 1558.068 | 572.032 | 36.71% | 1919.294 | 210.806 | 10.98%
Flemington | NJ | 1696 | 1570.488 | 125.512 | 7.992% | 1717.883 | -21.883 | -1.274%
Route 22 | NJ | 1871.1 | 2926.976 | -1055.876 | -36.07% | 1617.948 | 253.152 | 15.65%
Laurelton | NJ | 982.8 | 1245.514 | -262.714 | -21.09% | 1389.307 | -406.507 | -29.26% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 | 1. SR075812
Mahwah | NJ | 1238.3 | 1309.531 | -71.231 | -5.439% | 1251.927 | -13.627 | -1.088%
Franklin Township WF | NJ | 1507.7 | 1312.009 | 195.691 | 14.92% | 1782.599 | -274.899 | -15.42%
Bordentown | NJ | 1557.1 | 1112.349 | 444.751 | 39.98% | 1353.265 | 203.835 | 15.06%
South Plainfield | NJ | 998.1 | 781.9416 | 216.1584 | 27.64% | 916.6824 | 81.4176 | 8.882%
Somerset | NJ | 1524.3 | 2070.848 | -546.548 | -26.39% | 1410.593 | 113.707 | 8.061%
Clinton Main Relo | NJ | 1466.4766 | 1627.311 | -160.8344 | -9.883% | 1512.824 | -46.3474 | -3.064%
North Brunswick | NJ | 1065.1 | 1364.456 | -299.356 | -21.94% | 1750.64 | -685.54 | -39.16%
Cherry Hill | NJ | 1152.1914 | 1293.27 | -141.0786 | -10.91% | 1109.545 | 42.6464 | 3.844% | 1. Meter phase B current intermittently underreporting while inverter production unaffected. Reported energy loss may be retroactively corrected. | 1. SR077660
Hainesport | NJ | 1438.7 | 1353.939 | 84.761 | 6.26% | 1224.437 | 214.263 | 17.5%
San Antonio - Ops Ctr (Bldg 106) | TX | 34119 | 39805.08 | -5686.08 | -14.28% | 35220.77 | -1101.77 | -3.128%
San Antonio - Ops Ctr GM | TX | 282785.75 | 326416.8 | -43631.05 | -13.37% | 273080 | 9705.75 | 3.554%
San Antonio - Ctr (Bldg 201) | TX | 35010.5625 | 39502.94 | -4492.3775 | -11.37% | 35289.05 | -278.4875 | -0.7892%
San Antonio - Ops Ctr (Bldg 203) | TX | 37209.5 | 35826.93 | 1382.57 | 3.859% | 36618.05 | 591.45 | 1.615%
San Antonio - Ops Ctr (Bldg 205) | TX | 32635.9506 | 35976.2 | -3340.2494 | -9.285% | 33137.73 | -501.7794 | -1.514%
San Antonio - Ops Ctr (Bldg 307) | TX | 34377.5606 | 39158.55 | -4780.9894 | -12.21% | 34593.39 | -215.8294 | -0.6239%
San Antonio - Ctr (Bldg 308) | TX | 35064.8125 | 38261.52 | -3196.7075 | -8.355% | 33812.62 | 1252.1925 | 3.703%
San Antonio - Ops Ctr (Bldg 104) | TX | 5367.5635 | 11990.93 | -6623.3665 | -55.24% | 10250.96 | -4883.3965 | -47.64%
San Antonio - Ops Ctr (Bldg 102) | TX | 36683.875 | 35344.95 | 1338.925 | 3.788% | 37726.67 | -1042.795 | -2.764%
Lodi - Lodi Vineyard | CA | 18380.4375 | 21354.99 | -2974.5525 | -13.93% | 21024 | -2643.5625 | -12.57%
Arden Fair Mall | CA | 9241.1406 | 11329.5 | -2088.3594 | -18.43% | 12919 | -3677.8594 | -28.47%
Modesto - Modesto Main | CA | 6356.8573 | 9123.175 | -2766.3177 | -30.32% | 12253.14 | -5896.2827 | -48.12% | 1. IMT Ambient temperature sensor is not communicating. | 1. SR091735
Stevens Creek | CA | 3003.6401 | 2565.354 | 438.2861 | 17.08% | 2677 | 326.6401 | 12.2%

## Dec
Wells Fargo |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 816818.0586 | 930290.9963 | -113472.9377 | -12.2% | 975598.5154 | -158780.4568 | -16.28%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adams & Broadway | CA | 410.5 | 0 | 410.5 |  | 590 | -179.5 | -30.42%
Otay Mesa | CA | 0 | 0 | 0 |  | 0 | 0
San Leandro | CA | 20111.125 | 28532.47 | -8421.345 | -29.51% | 21079.89 | -968.765 | -4.596% | 1. Inverter 4 is underperforming 7KW and Inverter 2,7 are underperforming by approximately 3KW down compared to its peers. | 1.SR091496
Van Nuys | CA | 746.0024 | 0 | 746.0024 |  | 1195.45 | -449.4476 | -37.6%
98th & Grant | CO | 550.9 | 0 | 550.9 |  | 1080 | -529.1 | -48.99%
Arapahoe Crossings | CO | 1990.01 | 0 | 1990.01 |  | 1985.045 | 4.965 | 0.2501%
Aurora City Center | CO | 1102.9 | 0 | 1102.9 |  | 990 | 112.9 | 11.4%
Dry Creek | CO | 1263.3 | 0 | 1263.3 |  | 1163 | 100.3 | 8.624%
Highlands Ranch S. | CO | 1001.3 | 0 | 1001.3 |  | 1032 | -30.7 | -2.975%
Lone Tree | CO | 1722.8 | 0 | 1722.8 |  | 2382 | -659.2 | -27.67%
Meridian | CO | 1678.9 | 0 | 1678.9 |  | 1424 | 254.9 | 17.9%
Southglenn | CO | 1527.4 | 0 | 1527.4 |  | 1499 | 28.4 | 1.895%
Standley Lake | CO | 1586.2 | 0 | 1586.2 |  | 1998 | -411.8 | -20.61%
Havana Gardens | CO | 1706.2 | 0 | 1706.2 |  | 783 | 923.2 | 117.9%
East Hartford | CT | 206.8 | 334.4062 | -127.6062 | -38.16% | 256.4553 | -49.6553 | -19.36%
Norwalk | CT | 143.9 | 966.0821 | -822.1821 | -85.1% | 300.6717 | -156.7717 | -52.14% | 1. Weather station reporting erroneous values from 07/04/2024. | 1. SR088667
Hialeah Gardens | FL | 2267.9032 | 2731.058 | -463.1548 | -16.96% | 3154 | -886.0968 | -28.09%
West Des Moines - HMHQ | IA | 0 | 0 | 0 |  | 0 | 0
W. Des Moines Campus EAST | IA | 73221 | 87267.3 | -14046.3 | -16.1% | 88400 | -15179 | -17.17%
W. Des Moines Campus SW | IA | 40669 | 49796.4 | -9127.4 | -18.33% | 47594.41 | -6925.41 | -14.55%
WF - CIC | NC | 93130 | 93129.55 | 0.45 | 0.0004832% | 107291 | -14161 | -13.2% | 1. Inverter is offline from 07:45 to 13:45 on 12/11/2024. | 1. SR094414
Charlotte - Wells Fargo - DUC | NC | 89167 | 106893.9 | -17726.9 | -16.58% | 112005.2 | -22838.2 | -20.39%
East Windsor | NJ | 364.6 | 487.9543 | -123.3543 | -25.28% | 376.034 | -11.434 | -3.041%
Burlington | NJ | 1078 | 1011.957 | 66.043 | 6.526% | 945.3061 | 132.6939 | 14.04%
Bayonne | NJ | 1199.4 | 1309.381 | -109.981 | -8.399% | 1590.928 | -391.528 | -24.61%
Clifton | NJ | 1312.5312 | 1830.968 | -518.4368 | -28.31% | 2132.854 | -820.3227 | -38.46%
North Elizabeth | NJ | 1133.8 | 1052.792 | 81.008 | 7.695% | 1107.163 | 26.637 | 2.406%
Haddon Westmont Plaza | NJ | 671.9 | 941.8847 | -269.9847 | -28.66% | 836.5682 | -164.6682 | -19.68%
Parsippany | NJ | 972.5 | 1739.743 | -767.243 | -44.1% | 902.0869 | 70.4131 | 7.806%
Clark | NJ | 801.1 | 921.0287 | -119.9287 | -13.02% | 768.0344 | 33.0656 | 4.305%
Closter | NJ | 147.6 | 196.3877 | -48.7877 | -24.84% | 376.7055 | -229.1055 | -60.82%
Holmdel | NJ | 676.6 | 700.2972 | -23.6972 | -3.384% | 635.2573 | 41.3427 | 6.508%
Ellisburg Circle Center | NJ | 322.9 | 458.733 | -135.833 | -29.61% | 382.8797 | -59.9797 | -15.67%
Nutley | NJ | 1102.2 | 1373.825 | -271.625 | -19.77% | 1361.247 | -259.047 | -19.03%
Marlton | NJ | 1459.8 | 1228.989 | 230.811 | 18.78% | 1451.041 | 8.759 | 0.6036%
Middletown | NJ | 1621.2 | 1166.723 | 454.477 | 38.95% | 1315.991 | 305.209 | 23.19%
Whiting Crestwood | NJ | 2426.3 | 2387.711 | 38.589 | 1.616% | 2301.099 | 125.201 | 5.441%
Barnegat | NJ | 2302.0625 | 1730.374 | 571.6885 | 33.04% | 1858.517 | 443.5455 | 23.87%
Manchester | NJ | 1341.4 | 1410.117 | -68.717 | -4.873% | 2123.28 | -781.88 | -36.82%
West Deptford - Woodbury | NJ | 2045.4 | 1785.971 | 259.429 | 14.53% | 1655.556 | 389.844 | 23.55%
Edison | NJ | 1545.2 | 1192.966 | 352.234 | 29.53% | 1336.242 | 208.958 | 15.64%
Flemington | NJ | 1100.7 | 1236.029 | -135.329 | -10.95% | 1137.222 | -36.522 | -3.212%
Route 22 | NJ | 1322.3 | 1600.945 | -278.645 | -17.41% | 1102.199 | 220.101 | 19.97%
Laurelton | NJ | 748.4 | 975.6636 | -227.2636 | -23.29% | 1055.084 | -306.684 | -29.07% | 1. Production meter reporting low production due to phase A voltage dropped to zero from 04/27 | 1. SR075812
Mahwah | NJ | 757.9 | 1148.01 | -390.11 | -33.98% | 819.4824 | -61.5824 | -7.515%
Franklin Township WF | NJ | 1044.6 | 1055.965 | -11.365 | -1.076% | 1470.433 | -425.833 | -28.96%
Bordentown | NJ | 1101.1 | 872.9477 | 228.1523 | 26.14% | 1011.085 | 90.015 | 8.903%
South Plainfield | NJ | 703.7 | 598.4736 | 105.2264 | 17.58% | 602.0026 | 101.6974 | 16.89%
Somerset | NJ | 1014.9 | 1630.27 | -615.37 | -37.75% | 972.7613 | 42.1387 | 4.332%
Clinton Main Relo | NJ | 819.2969 | 1245.171 | -425.8741 | -34.2% | 997.326 | -178.0291 | -17.85%
North Brunswick | NJ | 976.9 | 1062.344 | -85.444 | -8.043% | 1190.89 | -213.99 | -17.97% | 1.Due to MC4 connector replacement and RSD device being RMA'd, Inverter was taken offline from 11:15 to 12:15 on 12/12 | 1.SR090252
Cherry Hill | NJ | 787.2578 | 987.4975 | -200.2397 | -20.28% | 824.1755 | -36.9177 | -4.479% | 1. Meter phase B current intermittently underreporting while inverter production unaffected. Reported energy loss may be retroactively corrected. | 1. SR077660
Hainesport | NJ | 1015.4 | 1028.715 | -13.315 | -1.294% | 875.6435 | 139.7565 | 15.96%
San Antonio - Ops Ctr (Bldg 106) | TX | 26104.5 | 33475.56 | -7371.06 | -22.02% | 31972.7 | -5868.2 | -18.35%
San Antonio - Ops Ctr GM | TX | 225027.5 | 263560.7 | -38533.2 | -14.62% | 268008 | -42980.5 | -16.04%
San Antonio - Ctr (Bldg 201) | TX | 27090.8125 | 33231.34 | -6140.5275 | -18.48% | 32322.87 | -5232.0575 | -16.19%
San Antonio - Ops Ctr (Bldg 203) | TX | 28731.9375 | 28219.91 | 512.0275 | 1.814% | 33703.74 | -4971.8025 | -14.75%
San Antonio - Ops Ctr (Bldg 205) | TX | 25004.5625 | 30281.09 | -5276.5275 | -17.43% | 30427.63 | -5423.0675 | -17.82%
San Antonio - Ops Ctr (Bldg 307) | TX | 26341.8144 | 32932.41 | -6590.5956 | -20.01% | 31584.95 | -5243.1356 | -16.6%
San Antonio - Ctr (Bldg 308) | TX | 26807.5625 | 32168.65 | -5361.0875 | -16.67% | 31170.49 | -4362.9275 | -14%
San Antonio - Ops Ctr (Bldg 104) | TX | 6858.8896 | 10078.53 | -3219.6404 | -31.95% | 9309.999 | -2451.1094 | -26.33%
San Antonio - Ops Ctr (Bldg 102) | TX | 29315.1875 | 29340.51 | -25.3225 | -0.08631% | 34662.37 | -5347.1825 | -15.43%
Lodi - Lodi Vineyard | CA | 13596.4688 | 14625.05 | -1028.5812 | -7.033% | 17886 | -4289.5312 | -23.98%
Arden Fair Mall | CA | 6724.2031 | 7955.84 | -1231.6369 | -15.48% | 10428 | -3703.7969 | -35.52%
Modesto - Modesto Main | CA | 5224.2833 | 6842.891 | -1618.6077 | -23.65% | 10234.55 | -5010.2667 | -48.95% | 1. IMT Ambient temperature sensor is not communicating. | 1. SR091735
Stevens Creek | CA | 1870.2478 | 1557.515 | 312.7328 | 20.08% | 2169 | -298.7522 | -13.77% | 1.Site is offline from 12/24 till end of the month. | 1.SR095090

## Sites
Portfolio: | Wells Fargo
Site DAS Name | Site | State | Update | DAS
BE 191334 - Adams & Broadway | Adams & Broadway | CA | AF | PowerTrack
BE 196270 - Otay Mesa (ATM) | Otay Mesa | CA |  | PowerTrack
BE 144682 - San Leandro Ops Center | San Leandro | CA | AEF | PowerTrack
BE 191705 - Van Nuys | Van Nuys | CA | AF | PowerTrack
BE 103541 - 98th & Grant | 98th & Grant | CO | AF | PowerTrack
BE 101451 - Arapahoe Crossings | Arapahoe Crossings | CO | AF | PowerTrack
BE 120617 - Aurora City Center | Aurora City Center | CO | AF | PowerTrack
BE 101995 - Dry Creek | Dry Creek | CO | AEF | PowerTrack
BE 102040 - Highlands Ranch South | Highlands Ranch S. | CO | AF | PowerTrack
BE 120717 - Lone Tree | Lone Tree | CO | AF | PowerTrack
BE 103553 - Meridian | Meridian | CO | AF | PowerTrack
BE 105797 - Southglenn Relocation | Southglenn | CO |  | PowerTrack
BE 120768 - Standley Lake | Standley Lake | CO | AF | PowerTrack
BE 106004 - Havana Gardens | Havana Gardens | CO | AF | PowerTrack
BE 144783 - East Hartford | East Hartford | CT | AEF | PowerTrack
BE 144725 - Norwalk Post Road | Norwalk | CT | AEF | PowerTrack
BE 107447 - Hialeah Gardens | Hialeah Gardens | FL | AEF | PowerTrack
BE 150140 - HMHQ | West Des Moines - HMHQ | IA |  | PowerTrack
BE 150496 - West Des Moines Campus - East | W. Des Moines Campus EAST | IA | AEF | PowerTrack
BE 150496 - West Des Moines Campus - SW | W. Des Moines Campus SW | IA | AEF | PowerTrack
BE 141278 - CIC | WF - CIC | NC |  | PowerTrack
BE 141954 - DUC | Charlotte - Wells Fargo - DUC | NC |  | PowerTrack
BE 140171 - East Windsor | East Windsor | NJ | AEF | PowerTrack
BE 141423 - Burlington Springside | Burlington | NJ | AEF | PowerTrack
BE 141327 - Bayonne Office | Bayonne | NJ | AEF | PowerTrack
BE 141382 - Clifton Office | Clifton | NJ | AEF | PowerTrack
BE 141427 - North Elizabeth Office | North Elizabeth | NJ | AEF | PowerTrack
BE 145739 - Westmont Plaza | Haddon Westmont Plaza | NJ | AEF | PowerTrack
BE 141464 - Parsippany Route 46 | Parsippany | NJ | AEF | PowerTrack
BE 141467 - Clark Office | Clark | NJ | AEF | PowerTrack
BE 141468 - Closter Office | Closter | NJ | AEF | PowerTrack
BE 140216 - Holmdel - Rt. 35 | Holmdel | NJ | AEF | PowerTrack
BE 144566 - Ellisburg Circle Center | Ellisburg Circle Center | NJ | AEF | PowerTrack
BE 141317 - Nutley Franklin | Nutley | NJ | AEF | PowerTrack
BE 140334 - Marlton | Marlton | NJ | AEF | PowerTrack
BE 140262 - Middletown - UC | Middletown | NJ | AEF | PowerTrack
BE 141443 - Whiting Crestwood | Whiting Crestwood | NJ | AEF | PowerTrack
BE 141441 - Barnegat Office | Barnegat | NJ | AEF | PowerTrack
BE 141445 - Manchester Office | Manchester | NJ | AEF | PowerTrack
BE 144269 - West Deptford / Woodbury | West Deptford - Woodbury | NJ | AEF | PowerTrack
BE 141344 - Edison Office | Edison | NJ | AEF | PowerTrack
BE 142050 - Flemington | Flemington | NJ | AEF | PowerTrack
BE 140332 - Rt. 22 Springfield | Route 22 | NJ | AEF | PowerTrack
BE 141466 - Laurelton Office | Laurelton | NJ | AEF | PowerTrack
BE 142088 - Mahwah | Mahwah | NJ | AEF | PowerTrack
BE 144110 - Franklin Township | Franklin Township WF | NJ | AEF | PowerTrack
BE 144103 - Bordentown | Bordentown | NJ | AEF | PowerTrack
BE 141918 - South Plainfield Oak Park | South Plainfield | NJ | AEF | PowerTrack
BE 144813 - Somerset | Somerset | NJ | AEF | PowerTrack
BE 145709 - Clinton | Clinton Main Relo | NJ |  | PowerTrack
BE 143233 - North Brunswick Financial Ctr | North Brunswick | NJ | AEF | PowerTrack
BE 141916 - Cherry Hill Short Hills | Cherry Hill | NJ | AEF | PowerTrack
BE 142875 - Hainesport Crossroads | Hainesport | NJ | AEF | PowerTrack
BE 144679 - 106 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 106) | TX |  | PowerTrack
BE 144679 - GM - San Antonio Ops | San Antonio - Ops Ctr GM | TX |  | PowerTrack
BE 144679 - 201 - San Antonio Ops | San Antonio - Ctr (Bldg 201) | TX |  | PowerTrack
BE 144679 - 203 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 203) | TX |  | PowerTrack
BE 144679 - 205 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 205) | TX |  | PowerTrack
BE 144679 - 307 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 307) | TX |  | PowerTrack
BE 144679 - 308 - San Antonio Ops | San Antonio - Ctr (Bldg 308) | TX |  | PowerTrack
BE 144679 - 104 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 104) | TX |  | PowerTrack
BE 144679 - 102 - San Antonio Ops | San Antonio - Ops Ctr (Bldg 102) | TX |  | PowerTrack
BE 105499 - Lodi Vineyard | Lodi - Lodi Vineyard | CA | AEF | PowerTrack
BE 144486 - Arden Fair Mall | Arden Fair Mall | CA | AEF | PowerTrack
BE 199250 - Modesto Main | Modesto - Modesto Main | CA | AEF | PowerTrack
BE 199506 - Stevens Creek | Stevens Creek | CA | AEF | PowerTrack