## Year to Date
Agilitas Energy |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 4439783.8833 | 3812598.801 | 627185.0823 | 16.45% | 4257604.35 | 182179.5333 | 4.279%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 515605.9046 | 528892.26 | -13286.3554 | -2.512% | 420655.77 | 2586.4946 | 0.6149%
Auburn - Leicester Street Solar | MA | 1481682.6667 | 1323328.587 | 158354.0797 | 11.97% | 0 | 1481682.6667
Rochester - Old Middleboro | MA | 2134633.312 | 1960377.954 | 174255.358 | 8.889% | 3836948.58 | 585028.852 | 15.25%
Dover - Littleworth Road | NH | 76761 | 0 | 76761 |  | 0 | 76761
Milton - Landfill | NH | 231101 | 0 | 231101 |  | 0 | 231101

## 1st Qtr
Agilitas Energy |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 4081355.2197 | 3449243.358 | 632111.8617 | 18.33% | 1712996.49 | 2368358.7297 | 138.3%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 157177.241 | 165536.817 | -8359.576 | -5.05% | 163392.03 | -6214.789 | -3.804%
Auburn - Leicester Street Solar | MA | 1481682.6667 | 1323328.587 | 158354.0797 | 11.97% | 0 | 1481682.6667
Rochester - Old Middleboro | MA | 2134633.312 | 1960377.954 | 174255.358 | 8.889% | 1549604.46 | 585028.852 | 37.75%
Dover - Littleworth Road | NH | 76761 | 0 | 76761 |  | 0 | 76761
Milton - Landfill | NH | 231101 | 0 | 231101 |  | 0 | 231101

## 2nd Qtr
Agilitas Energy |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 7162125.6251 | 6142431.22 | 1019694.4051 | 16.6% | 2544607.86 | 4617517.7651 | 181.5%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 265030.1976 | 268035.72 | -3005.5224 | -1.121% | 257263.74 | 7766.4576 | 3.019%
Auburn - Leicester Street Solar | MA | 2706720 | 2809460.8 | -102740.8 | -3.657% | 0 | 2706720
Rochester - Old Middleboro | MA | 3706056.4275 | 3064934.7 | 641121.7275 | 20.92% | 2287344.12 | 1418712.3075 | 62.02%
Dover - Littleworth Road | NH | 128040 | 0 | 128040 |  | 0 | 128040
Milton - Landfill | NH | 356279 | 0 | 356279 |  | 0 | 356279

## 3rd Qtr
Agilitas Energy |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 2397003.742 | 11418182.1 | -9021178.358 | -79.01% | 0 | 2397003.742 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 93398.466 | 95319.723 | -1921.257 | -2.016% |  | 1034.826
Auburn - Leicester Street Solar | MA | 964199.4 | 991770.102 | -27570.702 | -2.78% |  | 964199.4
Rochester - Old Middleboro | MA | 1152335.876 | 10331092.275 | -9178756.399 | -88.85% |  | 341109.836
Dover - Littleworth Road | NH | 47158 | 0 | 47158 |  |  | 47158
Milton - Landfill | NH | 139912 | 0 | 139912 |  |  | 139912

## 4th Qtr
Agilitas Energy |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 0 | 0 | 0 |  |  | 0
Auburn - Leicester Street Solar | MA | 0 | 0 | 0 |  |  | 0
Rochester - Old Middleboro | MA | 0 | 0 | 0 |  |  | 0
Dover - Littleworth Road | NH | 0 | 0 | 0 |  |  | 0
Milton - Landfill | NH | 0 | 0 | 0 |  |  | 0

## Jan
Agilitas Energy |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 643797.6434 | 502858.5 | 140939.1434 | 28.03% | 459223.17 | 184574.4734 | 40.19%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 23660.31 | 29500.5 | -5840.19 | -19.8% | 37551.17 | -13890.86 | -36.99%
Auburn - Leicester Street Solar | MA | 172284.3333 | 0 | 172284.3333 |  | 0 | 172284.3333 |  | 1. Site was offline on 01/07 at 10:00AM and later back online on 01/08 at 15:30. 2. Site tripped offline on 01/22 at 10:15AM and later back online on 01/25 at 15:45. 3. Inverters 28, 29 & 39 are offline from 01/26 and later back online on 01/31 at 14:45. | 1. SR080001 2. SR080133 3. SR080577
Rochester - Old Middleboro | MA | 406951 | 473358 | -66407 | -14.03% | 421672 | -14721 | -3.491% | 1. Site was offline on 01/13 from 06:15 to 11:30 . 2. Site was offline from 01/14 at 11:00 to 01/15 at 15:00. | 1. SR080191 2. SR080222
Dover - Littleworth Road | NH | 10197 | 0 | 10197 |  | 0 | 10197
Milton - Landfill | NH | 30705 | 0 | 30705 |  | 0 | 30705

## Feb
Agilitas Energy |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 1572309.9733 | 1222939.16 | 349370.8133 | 28.57% | 544279.56 | 1028030.4133 | 188.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 65179.64 | 66094.16 | -914.52 | -1.384% | 53397.96 | 11781.68 | 22.06%
Auburn - Leicester Street Solar | MA | 610539.3333 | 467792.3 | 142747.0333 | 30.52% | 0 | 610539.3333
Rochester - Old Middleboro | MA | 761805 | 689052.7 | 72752.3 | 10.56% | 490881.6 | 270923.4 | 55.19% | 1. Site relay tripped open at 15:00 on 02/29 and back online next day. | 1. SR081475
Dover - Littleworth Road | NH | 33324 | 0 | 33324 |  | 0 | 33324
Milton - Landfill | NH | 101462 | 0 | 101462 |  | 0 | 101462 |  | 1. Inverter 11 tripped offline twice this month and self-resolved itself each time. | 1. SR081067

## Mar
Agilitas Energy |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 1865247.603 | 1723445.698 | 141801.905 | 8.228% | 709493.76 | 1155753.843 | 162.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 68337.291 | 69942.157 | -1604.866 | -2.295% | 72442.9 | -4105.609 | -5.667%
Auburn - Leicester Street Solar | MA | 698859 | 855536.287 | -156677.287 | -18.31% | 0 | 698859 |  | 1. inverters 13, 14, 15 are offline on 03/22 and back online at 16:15 on 03/22. 2. Inverters 7, 8, and 9 tripped offline on an AC disconnected fault at 16:15 on 03/25 and back online at 16:30 on 03/25. | 1. SR082379 2. SR082723
Rochester - Old Middleboro | MA | 965877.312 | 797967.254 | 167910.058 | 21.04% | 637050.86 | 328826.452 | 51.62%
Dover - Littleworth Road | NH | 33240 | 0 | 33240 |  | 0 | 33240 |  | 1. Site has not started on 03/24 and has started on 10:45am on 03/24. | 1. SR082614
Milton - Landfill | NH | 98934 | 0 | 98934 |  | 0 | 98934 |  | 1. Inverter 11 tripped offline at 10:00am on 03/21 and back online on 03/22 2. Inverter 22 is offline on 03/24 and back online on 03/25. | 1. SR082351 2. SR082691

## Apr
Agilitas Energy |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 2086903.6251 | 1814581.3 | 272322.3251 | 15.01% | 780206.34 | 1306697.2851 | 167.5%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 79228.3976 | 79840.2 | -611.8024 | -0.7663% | 82261.44 | -3033.0424 | -3.687%
Auburn - Leicester Street Solar | MA | 806444 | 847614.4 | -41170.4 | -4.857% | 0 | 806444
Rochester - Old Middleboro | MA | 1051496.2275 | 887126.7 | 164369.5275 | 18.53% | 697944.9 | 353551.3275 | 50.66% | 1. Inverter 1 tripped offline on 04/28 at 07:00 and back online on 04/29 at 07:00 and again tripped offline at 14:00 on 04/29 and back online on 04/30, again inverter tripped offline at 18:00 on 04/30 | 1. SR083899
Dover - Littleworth Road | NH | 39653 | 0 | 39653 |  | 0 | 39653
Milton - Landfill | NH | 110082 | 0 | 110082 |  | 0 | 110082 |  | 1. Inverter 12 tripped offline on 04/02 at 01:35 PM and back online on 04/03 at 12:00 PM. 2. Site tripped offline on 04/04 at 09:15 and back online on 04/06 at 08:20 AM. Inverters 11 and 22 are offline after site re-energized and back online on 04/07. 3. Inverter 21 is derating by 5kW during peak hours from 04/25 | 1. SR083024 2. SR083071 3. SR083818

## May
Agilitas Energy |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 2378796 | 2044259.92 | 334536.08 | 16.36% | 881066.6 | 1497729.4 | 170%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 90222.8 | 90753.52 | -530.72 | -0.5848% | 88730.3 | 1492.5 | 1.682% | 1. Inverter 13 is overheating on high irradiance days and is about 7 kW down for multiple days. | 1. SR085127
Auburn - Leicester Street Solar | MA | 891783 | 932322.4 | -40539.4 | -4.348% | 0 | 891783
Rochester - Old Middleboro | MA | 1235742.2 | 1021184 | 214558.2 | 21.01% | 792336.3 | 443405.9 | 55.96%
Dover - Littleworth Road | NH | 42525 | 0 | 42525 |  | 0 | 42525
Milton - Landfill | NH | 118523 | 0 | 118523 |  | 0 | 118523 |  | 1. Inverter 21 is derating by 5kW during peak hours from 04/25 2. Inverter 5 is derating by 8kW during peak hours from 05/21 | 1. SR083818 2. SR084975

## Jun
Agilitas Energy |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 2696426 | 2283590 | 412836 | 18.08% | 883334.92 | 1813091.08 | 205.3%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 95579 | 97442 | -1863 | -1.912% | 86272 | 9307 | 10.79% | 1. Inverter 13 is derating due to overheating on sunny days. Issue occurred throughout the month | 1. SR085127
Auburn - Leicester Street Solar | MA | 1008493 | 1029524 | -21031 | -2.043% | 0 | 1008493 |  | 1. Site tripped offline at 19:50 on 06/19 and back online at 10:45 on 06/20 | 1. SR086453
Rochester - Old Middleboro | MA | 1418818 | 1156624 | 262194 | 22.67% | 797062.92 | 621755.08 | 78.01%
Dover - Littleworth Road | NH | 45862 | 0 | 45862 |  | 0 | 45862
Milton - Landfill | NH | 127674 | 0 | 127674 |  | 0 | 127674 |  | 1. Inverter 21 is derating by 5kW during peak hours from 04/25 throughout the month 2. Inverter 5 is derating by 8kW during peak hours from 05/21 throughout the month | 1. SR083818 2. SR084975

## Jul
Agilitas Energy |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 2397003.742 | 11418182.1 | -9021178.358 | -79.01% | 903589.68 | 1493414.062 | 165.3%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 93398.466 | 95319.723 | -1921.257 | -2.016% | 92363.64 | 1034.826 | 1.12%
Auburn - Leicester Street Solar | MA | 964199.4 | 991770.102 | -27570.702 | -2.78% | 0 | 964199.4 |  | 1. Inverters 25, 26 and 27 are offline on 07/05 and back online on 07/08 at 10:15 AM 2. Site tripped offline at 17:30 on 07/23 and back online on 07/24 at 06:00 AM | 1. SR087391 2. SR088075
Rochester - Old Middleboro | MA | 1152335.876 | 10331092.275 | -9178756.399 | -88.85% | 811226.04 | 341109.836 | 42.05% | 1. Inverter 1 stopped communicating, as per meter offline on 07/11 at 13:00 and back online on 07/12 at 08:30 AM 2. Inverter 2 tripped offline at 15:15 on 07/11 and back online on 07/12 at 13:00 again tripped offline on 07/14 at 10:00 AM, back online on 07/15 at 07:30 AM Inverter 2 tripped offline at 17:30 on 07/18 and back online on 07/19 at 07:45 3. Inverter 1 tripped offline at 13:00 on 07/22 and back online on 07/24 at 12:15 4. Inverter 2 and 3 are offline on 07/23 and back online on 07/24 | 1. SR087558 2. SR087558, SR087578 3. SR087988, SR087990 4. SR088071
Dover - Littleworth Road | NH | 47158 | 0 | 47158 |  | 0 | 47158
Milton - Landfill | NH | 139912 | 0 | 139912 |  | 0 | 139912

## Aug
Agilitas Energy |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA
Auburn - Leicester Street Solar | MA
Rochester - Old Middleboro | MA
Dover - Littleworth Road | NH
Milton - Landfill | NH

## Sep
Agilitas Energy |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA
Auburn - Leicester Street Solar | MA
Rochester - Old Middleboro | MA
Dover - Littleworth Road | NH
Milton - Landfill | NH

## Oct
Agilitas Energy |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA
Auburn - Leicester Street Solar | MA
Rochester - Old Middleboro | MA
Dover - Littleworth Road | NH
Milton - Landfill | NH

## Nov
Agilitas Energy |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA
Auburn - Leicester Street Solar | MA
Rochester - Old Middleboro | MA
Dover - Littleworth Road | NH
Milton - Landfill | NH

## Dec
Agilitas Energy |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA
Auburn - Leicester Street Solar | MA
Rochester - Old Middleboro | MA
Dover - Littleworth Road | NH
Milton - Landfill | NH

## Sites
Portfolio: | Agilitas Energy
Site DAS Name | Site | State | Update | DAS
Central Street Solar, Rowley | Rowley - Central Street Solar | MA | AEF | PowerTrack
Leicester Street Solar: DAS + BESS | Auburn - Leicester Street Solar | MA | AEF | PowerTrack
Middleboro Road | Rochester - Old Middleboro | MA | AEF | PowerTrack
Littleworth Road Solar | Dover - Littleworth Road | NH |  | SolrenView
Milton Municipal Landfill | Milton - Landfill | NH |  | SolrenView