## Year to Date
MN8 Bond |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 17139843.0307 | 18199307.18 | -1059464.1493 | -5.821% | 14513936.16 | 2625906.8707 | 18.09%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Grafton II | MA | 2704740.509 | 2605271.1 | 99469.409 | 3.818% | 2325644 | -131661.491 | -5.661%
Clara Barton | MA | 982455.1417 | 1024558.52 | -42103.3783 | -4.109% | 846556.98 | -59831.7805 | -7.068%
Fairhaven Solar | MA | 763261 | 802474.14 | -39213.14 | -4.887% | 646733.99 | 1599.61 | 0.2473%
Plympton-1 | MA | 1020806.9951 | 1056816.43 | -36009.4349 | -3.407% | 833604.93 | -21065.93 | -2.527%
French River 2 | MA | 1022971.11 | 1140482.37 | -117511.26 | -10.3% | 843431 | -12609.89 | -1.495%
French River 3 | MA | 2009945.87 | 2021580.4 | -11634.53 | -0.5755% | 1615232.2 | -5460.98 | -0.3381%
French River 4 | MA | 2025524.6364 | 2211020.2 | -185495.5636 | -8.39% | 1683772.1 | -37845.9636 | -2.248%
French River 5 | MA | 1861113.39 | 2139429.8 | -278316.41 | -13.01% | 1653182.9 | -90612.41 | -5.481%
French River 6 | MA | 1816224.43 | 1829599.6 | -13375.17 | -0.731% | 1586096.1 | -80776.57 | -5.093%
Stillwater River 1A | MA | 512050.0275 | 507837.46 | 4212.5675 | 0.8295% | 407002.51 | 3513.78 | 0.8633%
Stillwater River 2 | MA | 1004804.12 | 1170470.18 | -165666.06 | -14.15% | 852306.99 | -38015.67 | -4.46%
Stillwater River 3 | MA | 1003762.4 | 1134221.86 | -130459.46 | -11.5% | 839077.59 | -30572.69 | -3.644%
Stillwater River 4 | MA | 412183.401 | 555545.12 | -143361.719 | -25.81% | 381294.87 | -28589.2815 | -7.498%

## 1st Qtr
MN8 Bond |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 5209766.1952 | 5804753.64 | -594987.4448 | -10.25% | 5740352.13 | -530585.9348 | -9.243%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Grafton II | MA | 816220.8408 | 874147.8 | -57926.9592 | -6.627% | 946539 | -130318.1592 | -13.77%
Clara Barton | MA | 271481.9995 | 311908.02 | -40426.0205 | -12.96% | 331313.78 | -59831.7805 | -18.06%
Fairhaven Solar | MA | 250961 | 274575.84 | -23614.84 | -8.6% | 249361.39 | 1599.61 | 0.6415%
Plympton-1 | MA | 297435 | 317931.23 | -20496.23 | -6.447% | 318500.93 | -21065.93 | -6.614%
French River 2 | MA | 320252.11 | 372903.77 | -52651.66 | -14.12% | 332862 | -12609.89 | -3.788%
French River 3 | MA | 632578.12 | 566613.7 | 65964.42 | 11.64% | 638039.1 | -5460.98 | -0.8559%
French River 4 | MA | 627309.6364 | 724748.1 | -97438.4636 | -13.44% | 665155.6 | -37845.9636 | -5.69%
French River 5 | MA | 562261.39 | 701281.3 | -139019.91 | -19.82% | 652873.8 | -90612.41 | -13.88%
French River 6 | MA | 545632.43 | 605090.4 | -59457.97 | -9.826% | 626409 | -80776.57 | -12.9%
Stillwater River 1A | MA | 164251.25 | 145917.63 | 18333.62 | 12.56% | 160737.47 | 3513.78 | 2.186%
Stillwater River 2 | MA | 298612.12 | 373006.08 | -74393.96 | -19.94% | 336627.79 | -38015.67 | -11.29%
Stillwater River 3 | MA | 300820.4 | 371261.36 | -70440.96 | -18.97% | 331393.09 | -30572.69 | -9.226%
Stillwater River 4 | MA | 121949.8985 | 165368.41 | -43418.5115 | -26.26% | 150539.18 | -28589.2815 | -18.99%

## 2nd Qtr
MN8 Bond |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 8871453.4288 | 9219914.86 | -348461.4312 | -3.779% | 8773584.03 | 97869.3988 | 1.116%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Grafton II | MA | 1401773.81 | 1290931.7 | 110842.11 | 8.586% | 1379105 | 22668.81 | 1.644%
Clara Barton | MA | 526097 | 525286.3 | 810.7 | 0.1543% | 515243.2 | 10853.8 | 2.107%
Fairhaven Solar | MA | 384318 | 393613.2 | -9295.2 | -2.362% | 397372.6 | -13054.6 | -3.285%
Plympton-1 | MA | 543586.9951 | 551321.5 | -7734.5049 | -1.403% | 515104 | 28482.9951 | 5.53%
French River 2 | MA | 521028 | 570681.4 | -49653.4 | -8.701% | 510569 | 10459 | 2.048%
French River 3 | MA | 1022134 | 1083611.1 | -61477.1 | -5.673% | 977193.1 | 44940.9 | 4.599%
French River 4 | MA | 1038020 | 1106160.3 | -68140.3 | -6.16% | 1018616.5 | 19403.5 | 1.905%
French River 5 | MA | 966230 | 1071581.8 | -105351.8 | -9.831% | 1000309.1 | -34079.1 | -3.407%
French River 6 | MA | 946130 | 915179.1 | 30950.9 | 3.382% | 959687.1 | -13557.1 | -1.413%
Stillwater River 1A | MA | 257903.5275 | 269560.55 | -11657.0225 | -4.324% | 246265.04 | 11638.4875 | 4.726%
Stillwater River 2 | MA | 524893 | 588997.6 | -64104.6 | -10.88% | 515679.2 | 9213.8 | 1.787%
Stillwater River 3 | MA | 522670 | 566398.9 | -43728.9 | -7.721% | 507684.5 | 14985.5 | 2.952%
Stillwater River 4 | MA | 216669.0963 | 286591.41 | -69922.3138 | -24.4% | 230755.69 | -14086.5938 | -6.105%

## 3rd Qtr
MN8 Bond |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 3058623.4066 | 3174638.68 | -116015.2734 | -3.654% | 0 | 3058623.4066 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Grafton II | MA | 486745.8582 | 440191.6 | 46554.2582 | 10.58% |  | -24012.1418
Clara Barton | MA | 184876.1422 | 187364.2 | -2488.0578 | -1.328% |  | -7253.3578
Fairhaven Solar | MA | 127982 | 134285.1 | -6303.1 | -4.694% |  | -14733.9
Plympton-1 | MA | 179785 | 187563.7 | -7778.7 | -4.147% |  | -6702.5
French River 2 | MA | 181691 | 196897.2 | -15206.2 | -7.723% |  | -7943
French River 3 | MA | 355233.75 | 371355.6 | -16121.85 | -4.341% |  | -7445.45
French River 4 | MA | 360195 | 380111.8 | -19916.8 | -5.24% |  | -17852.8
French River 5 | MA | 332622 | 366566.7 | -33944.7 | -9.26% |  | -38641
French River 6 | MA | 324462 | 309330.1 | 15131.9 | 4.892% |  | -31718.5
Stillwater River 1A | MA | 89895.25 | 92359.28 | -2464.03 | -2.668% |  | -1497.68
Stillwater River 2 | MA | 181299 | 208466.5 | -27167.5 | -13.03% |  | -10074.8
Stillwater River 3 | MA | 180272 | 196561.6 | -16289.6 | -8.287% |  | -8136.3
Stillwater River 4 | MA | 73564.4062 | 103585.3 | -30020.8938 | -28.98% |  | -12078.3537

## 4th Qtr
MN8 Bond |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Grafton II | MA | 0 | 0 | 0 |  |  | 0
Clara Barton | MA | 0 | 0 | 0 |  |  | 0
Fairhaven Solar | MA | 0 | 0 | 0 |  |  | 0
Plympton-1 | MA | 0 | 0 | 0 |  |  | 0
French River 2 | MA | 0 | 0 | 0 |  |  | 0
French River 3 | MA | 0 | 0 | 0 |  |  | 0
French River 4 | MA | 0 | 0 | 0 |  |  | 0
French River 5 | MA | 0 | 0 | 0 |  |  | 0
French River 6 | MA | 0 | 0 | 0 |  |  | 0
Stillwater River 1A | MA | 0 | 0 | 0 |  |  | 0
Stillwater River 2 | MA | 0 | 0 | 0 |  |  | 0
Stillwater River 3 | MA | 0 | 0 | 0 |  |  | 0
Stillwater River 4 | MA | 0 | 0 | 0 |  |  | 0

## Jan
MN8 Bond |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 777232.6144 | 1271145.13 | -493912.5156 | -38.86% | 1396020.46 | -618787.8456 | -44.33%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA | 108788.8408 | 176557 | -67768.1592 | -38.38% | 245116 | -136327.1592 | -55.62% | 1. Site tripped offline on 01/10 at 13:15 and later back online on 01/11 at 11:45AM. 2. Inverter 5.6B was did not came back online after site re-enerziation 01/11 at and later back online on 01/12 at 09:15AM. 3. Inverters 5.7B, 6.2B, and 6.5B are offline from 01/25 and later 5.7B is back online on 01/30 at 09:00AM | 1. SR080136 2. SR080158 3. SR080474
Clara Barton | MA | 41686.1447 | 61398.72 | -19712.5753 | -32.11% | 84576.48 | -42890.3353 | -50.71% | 1. Inverter 5.8 has tripped offline on 01/17 at 12:00 and back oline on 01/17 at 15:00. 2. Site tripped offline on 01/26 at 18:45 and back online on 01/27 at 10:45AM | 1. SR080289 2. SR080520
Fairhaven Solar | MA | 55436 | 67352.87 | -11916.87 | -17.69% | 63727.01 | -8291.01 | -13.01% | 1. Inverter 3 is offline on 01/11 after site is re-energized later back online on 01/11 at 13:30. 2. Inverters 1,4 12, 25, 28, 29 & 49 offline on 01/15 from 07:00AM and later back online on 01/17 at 11:15AM. 3. Site was tripped offline on 01/11 at 07:00 and back online 11:45 | 1. SR080159 2. SR080243 1. SR080152
Plympton-1 | MA | 67619 | 73871.03 | -6252.03 | -8.463% | 79420.95 | -11801.95 | -14.86%
French River 2 | MA | 41541.11 | 80016.27 | -38475.16 | -48.08% | 78833 | -37291.89 | -47.3% | 01. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080519
French River 3 | MA | 86149.12 | 150506.8 | -64357.68 | -42.76% | 151308.7 | -65159.58 | -43.06% | 01. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080519
French River 4 | MA | 85549.4664 | 154184.8 | -68635.3336 | -44.51% | 157760 | -72210.5336 | -45.77% | 01. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080519
French River 5 | MA | 83292.5 | 147678.6 | -64386.1 | -43.6% | 154754.9 | -71462.4 | -46.18% | 1. Inverter 62 is offline on 01/14 and later back online on 01/15 2. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080199 2. SR080519
French River 6 | MA | 78703 | 125159 | -46456 | -37.12% | 148483.1 | -69780.1 | -47% | 1. Inverter 41B is offline on 01/13 and later back online 01/14. 2. Inverter 62B is offline on 01/14 and later back online on 01/15. 3. Inverters 60 and 62 are tripped offline on 01/22 at 14:00, later 62B is back online on 01/23 at 07:00AM and 60B have multiple tripping events. 4. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080195 2. SR080198 3. SR080402 4. SR080519
Stillwater River 1A | MA | 21302 | 36938.76 | -15636.76 | -42.33% | 38086.07 | -16784.07 | -44.07% | 01. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080519
Stillwater River 2 | MA | 44604.12 | 82849.68 | -38245.56 | -46.16% | 79775.59 | -35171.47 | -44.09% | 01. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080519
Stillwater River 3 | MA | 44552 | 81817.76 | -37265.76 | -45.55% | 78530.19 | -33978.19 | -43.27% | 01. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080519
Stillwater River 4 | MA | 18009.3125 | 32813.84 | -14804.5275 | -45.12% | 35648.47 | -17639.1575 | -49.48% | 01. Site was tripped offline on 01/26 at 18:00 and back online at 01/27 at 8:00 AM. | 1. SR080519

## Feb
MN8 Bond |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2159606.8769 | 2449165.73 | -289558.8531 | -11.82% | 1818738.41 | 340868.4669 | 18.74%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA | 323940 | 341873.5 | -17933.5 | -5.246% | 295886 | 28054 | 9.481% | 1. Inverters 5.7B & 6.5B tripped offline due to isolation failures and are detecting ground faults. 2. Inverter 3.2C tripped offline and is reporting a generic "Error" code and back online on 02/20 3. Inverter 9.7B is offline on 02/21 and back online on same day. 4. Inverter 6.4b tripped offline on 02/22 and is reporting a generic inverter Error and back online on same day. | 1. SR081002 2. SR081064 3. SR081151 4. SR081183
Clara Barton | MA | 116495.3139 | 126875.4 | -10380.0861 | -8.181% | 101882.3 | 14613.0139 | 14.34% | 1. Inverter 2.1 tripped offline at 08:00 on 02/20 and back online at 14:22 on 02/22. Inverter again tripped offline at 08:00 on 02/25, Inverter being RMA'd 2. Site tripped offline at 08:30 on 02/28 and back online at 08:00 on 02/29 | 1. SR081306,SR081139 2. SR081400
Fairhaven Solar | MA | 89525 | 98220.97 | -8695.97 | -8.853% | 78120.28 | 11404.72 | 14.6% | 1. Inverter 2 tripped offline at 11:30 and back online at 15:45 by remote reset on 02/04 2. Inverter 41 is offline on 02/29 and back online at 08:15 on 03/01 by remote reset | 1. SR080714 2. SR081449
Plympton-1 | MA | 114034 | 124223.6 | -10189.6 | -8.203% | 98091.58 | 15942.42 | 16.25% | 1. Inverter SA-4 3-D was underperforming 4kW cpmpared to peers and was troubleshooted on 02/21 | 1. SR081140
French River 2 | MA | 132153 | 156172.9 | -24019.9 | -15.38% | 106405 | 25748 | 24.2%
French River 3 | MA | 257405 | 299390.1 | -41985.1 | -14.02% | 203894.6 | 53510.4 | 26.24% | 1. Inverter 40 is underperforming 3kW compared to peers from 02/20/24 | 1. SR081195
French River 4 | MA | 265549.75 | 304548.2 | -38998.45 | -12.81% | 212563.8 | 52985.95 | 24.93%
French River 5 | MA | 243741 | 295557.5 | -51816.5 | -17.53% | 208635.1 | 35105.9 | 16.83% | 1. Inverter 39 is offline several times in the month 2. Inverter 158 is offline from 01/28 and relay board was replaced on 02/07 at 15:00 3. Inverter 129 tripped offline at 10:00 on 02/12 and back online at 7:00 on 02/16 4. Inverters 106 and 141 are underperforming 4kW each compared to its peers 5. Inverter 76 was offline on 02/20,02/28 and back online by next day | 1. SR080867,SR080705 2. SR080754 3. SR080950 4. SR081033 5. SR081147
French River 6 | MA | 230604 | 254770 | -24166 | -9.485% | 200185.5 | 30418.5 | 15.2% | 1. Inverter 62-6B was offline on 02/12 and back online on 02/14 2. Inverter 97-6A was offline from 02/19 and back online on 02/21. Inverter 97 again offline from 02/24 and back online on 02/27 3. Inverter 68-6A is offline the entire month. Inverter being RMA'd 4. Inverter 60-6B is offline the entire month. Inverter being RMA'd | 1. SR080951 2. SR081119 3. SR081135 4. SR078134
Stillwater River 1A | MA | 65138.813 | 63898.28 | 1240.533 | 1.941% | 51386.81 | 13752.003 | 26.76%
Stillwater River 2 | MA | 134132 | 158022.2 | -23890.2 | -15.12% | 107616.5 | 26515.5 | 24.64%
Stillwater River 3 | MA | 134092 | 158570.9 | -24478.9 | -15.44% | 105943.3 | 28148.7 | 26.57%
Stillwater River 4 | MA | 52797 | 67042.18 | -14245.18 | -21.25% | 48127.64 | 4669.36 | 9.702% | 1. Inverter 20-4A was offline from 01/26 and back online on 02/05. Inverter 20 again 02/28 and back online on 03/01 | 1.SR080709, SR081456

## Mar
MN8 Bond |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 2272926.704 | 2084442.78 | 188483.924 | 9.042% | 2525593.26 | -252666.556 | -10%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA | 383492 | 355717.3 | 27774.7 | 7.808% | 405537 | -22045 | -5.436% | 1. Inverters 5.7B, 6.4B & 6.5B are offline due to Insulation failure on 03/05 and back online on 03/06 and 6.5B again offline on 03/23 and back online at 14:45 on 03/23. 2. Inverters 5.7B, 9.3B are offline today due to insulation failure on 03/23 and inverter 9.3B back online at 16:15 on 03/23 and inverter 5.7B is back online on 03/24. 3. Inverter 5.3B tripped offline on an arc fault at 14:30 on 03/17 and back online at 15:15 and again tripped offline at 15:15 on 03/19 and back online at 16:30 and again tripped offline again at 13:42 on 03/27 and back online at 17:00 on 03/27 and again tripped offline at 14:45 on 03/30 4. Inverters 5.7b 6.4b 6.5b 7.7b 9.3b didn't start for production and reporting "Insulation failure" on 03/28 and back online on 03/29. 5. Inverter 9.7b is offline on 03/01, 03/2, 03/15 & 03/23. Inverter being RMA'd | 1. SR081590 2. SR081590 3. SR081974 4. SR082875 5. SR081151
Clara Barton | MA | 113300.541 | 123633.9 | -10333.359 | -8.358% | 144855 | -31554.459 | -21.78% | 1. Inverter 2.5 is offline due to 6411 interference device fault from 03/13 2. Inverter 4.6 tripping offline due to DC fault at 10:30 on 03/18 and back online at 15:15 on 03/18 and having several tripping events on multiple days. 3. Inverter 5.7 is offline on an arc fault at 12:00pm from 03/06 4. Inverter 21 is being RMA'd 5. Site tripped offline on 03/02 at 18:30 and back online on 03/03 at 08:00am | 1. SR081993 2. SR081994 3. SR082311 4. SR081306 5. SR081400
Fairhaven Solar | MA | 106000 | 109002 | -3002 | -2.754% | 107514.1 | -1514.1 | -1.408% | 1. Inverter 2 tripped offline at 10:15 on 03/08 and back online at 11:15 by remote reset on 03/08. | 1. SR081698
Plympton-1 | MA | 115782 | 119836.6 | -4054.6 | -3.383% | 140988.4 | -25206.4 | -17.88% | 1. Site offline due to utility planned outage from 03/28 at 13:15. 2. Inverter 1-8A was offline from 03/15 t and back online on 03/22 after replacing | 1. SR081605 2. SR081943
French River 2 | MA | 146558 | 136714.6 | 9843.4 | 7.2% | 147624 | -1066 | -0.7221%
French River 3 | MA | 289024 | 116716.8 | 172307.2 | 147.6% | 282835.8 | 6188.2 | 2.188% | 1. Inverter 115 is offline on 03/17 and back online at 10:00am on 03/17 | 1. SR081964
French River 4 | MA | 276210.42 | 266015.1 | 10195.32 | 3.833% | 294831.8 | -18621.38 | -6.316% | 1. Site was taken offline by USNE to install new transformer on 03/25between 07:30am to 16:00 | 1. SR081807
French River 5 | MA | 235227.89 | 258045.2 | -22817.31 | -8.842% | 289483.8 | -54255.91 | -18.74% | 1. Inverter 54 is being RMA'd 2. Inverter 17 tripped offline on 03/22 at 11:45 and back online on 03/23 3. Inverter 76 was offline on 03/03 & 03/18 4. Inverter 39 is offline from 03/01 to 03/06 5. Inverters 106 and 141 are underperforming 4kW each compared to its peers 6. Site is offline at 11:15 on 03/24 and back online at 10:45 on 03/30 a due to utility Planned outage. | 1. SR082907 2. SR082496 3. SR081147 4. SR080867 5. SR081033 6. SR082320
French River 6 | MA | 236325.43 | 225161.4 | 11164.03 | 4.958% | 277740.4 | -41414.97 | -14.91% | 1. Site is offline at 11:30 on 03/24 and back online at 12:15 on 03/29 a due to utility Planned outage. 2. Inverter 68-6A is offline the entire month. Inverter being RMA'd 3. Inverter 72 & 84 are offline from 03/29 and back online on 04/01 | 1. SR082321 2. SR081135 3. SR082909
Stillwater River 1A | MA | 77810.437 | 45080.59 | 32729.847 | 72.6% | 71264.59 | 6545.847 | 9.185%
Stillwater River 2 | MA | 119876 | 132134.2 | -12258.2 | -9.277% | 149235.7 | -29359.7 | -19.67% | 1. Site is offline at 11:15 on 03/24 and back online at 11:00 on 03/30 a due to utility Planned outage. | 1. SR082325, SR082326
Stillwater River 3 | MA | 122176.4 | 130872.7 | -8696.3 | -6.645% | 146919.6 | -24743.2 | -16.84% | 1. Site is offline at 11:15 on 03/24 and back online at 11:00 on 03/30 a due to utility Planned outage. | 1. SR082327
Stillwater River 4 | MA | 51143.586 | 65512.39 | -14368.804 | -21.93% | 66763.07 | -15619.484 | -23.4% | 1. Site is offline at 11:15 on 03/24 and back online at 10:45 on 03/30 a due to utility Planned outage. | 1. SR082328

## Apr
MN8 Bond |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 2585724.0951 | 2705253.3 | -119529.2049 | -4.418% | 2704748.74 | -119024.6449 | -4.401%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA | 406325.32 | 383163.7 | 23161.62 | 6.045% | 444997 | -38671.68 | -8.69% | 1. Inverter 5.3B is tripped offline on 03/30 at 14:45 and back online on 04/01 with remote reset at 13:30 and again tripped offline on 14:45 on same day and back online on 9:00am on 04/05 2. Inverters 2.2B, 5.4B, 5.7B and 6.5B are offline and reporting insulation failure on 04/04 and later self resolved on afternoon. 3. Inverter 4.1B is underproducing 9kW compared to its peers from 04/17 to 04/24 | 1. SR081974 2. SR083073 3. SR083728
Clara Barton | MA | 151790 | 150612.3 | 1177.7 | 0.7819% | 163762 | -11972 | -7.311% | 1. Inverter 8.7 tripped offline on 04/9 at 1:45pm and back online on 04/11 and again offline on 04/12 to 04/17 and again offline on 04/21 and is being RMA'd 2. Inverter 6.7 is offline on 04/04, 04/12, 04/15, 04/17,04/18 and technician has replaced inverter and it is back online on 04/19. 3. Inverter 1.3 is offline on 04/01 and technician powercycled the inverter it is back online on 04/08 at 8:15am. 4. Site tripped offline and reporting A phase Voltages on 04/18 at 16:45 and is back online at 19:00 on same day and again offline with same fault on 04/30 at 5:30am and back online on same day at 8:15am. | 1. SR083611 2. SR083420 3. SR083156 4. SR083608, SR083988
Fairhaven Solar | MA | 104937 | 105598 | -661 | -0.626% | 123663.1 | -18726.1 | -15.14% | 1.Site was offline due to utility outage on 04/07 from 12:00 to 15:00. 2. Site was offline due to utility outage from 04/08 at 09:00am to 14:45. 3. Inverter 5 tripped ofline on 04/13 from 11:45 to 15:00. 4. Site tripped offline on 04/16 at 11:45 and back online on 04/19 at 07:00 and again tripped offline on 04/20 from 10:15 to 16:00. 5.Inverter 30 tripped offline on 04/20 at 16:00 and back online on 04/21 at 07:00. | 1.SR083159 2.SR083168 3.SR083385 4.SR083490 5. SR083652
Plympton-1 | MA | 161073.9951 | 160586.2 | 487.7951 | 0.3038% | 162902.4 | -1828.4049 | -1.122%
French River 2 | MA | 152350 | 168447.2 | -16097.2 | -9.556% | 154735 | -2385 | -1.541% | 1. Site was taken offline on 04/26 at 11:30am and reenergised at 12:30pm | 1. PM2819
French River 3 | MA | 301481 | 320682.3 | -19201.3 | -5.988% | 296383.2 | 5097.8 | 1.72% | 1. Site was taken offline on 04/26 at 07:00am and reenergised at 08:00am | 1. PM2819
French River 4 | MA | 302821 | 326893.3 | -24072.3 | -7.364% | 308948 | -6127 | -1.983% | 1. Site was taken offline on 04/26 at 08:30am and reenergised at 10:00am | 1. PM2820
French River 5 | MA | 280833 | 316928.7 | -36095.7 | -11.39% | 303377.1 | -22544.1 | -7.431% | 1. Inverter 54 is offline from 04/01 to 04/18 2. Inverter 123 is offline from 04/01 to 04/30 3. Inverter 165 is offline from 04/25 | 1. SR082907 2. SR082908 3. SR083837
French River 6 | MA | 276927 | 274522.2 | 2404.8 | 0.876% | 291071.4 | -14144.4 | -4.859% | 1. Inverter 10 6A tripped offline on 04/12 at 15:45 and back online on 04/15 at 08:45am 2. Inverter 98 6B was tripped offline on 04/08 at 13:30 and back online on 04/11 at 10:15am 3. Inverter 73 was offline on 04/07, 04/25 and self resolved on next day 4. Inverter 56 was offline on 04/02, 04/16, 04/18, 04/26 and self resolved on next day 5. Inverter 60 is offline for most of the days in month and being RMA'd | 1. SR083386 2. SR083203 3. SR083142 4. SR083028 5. SR078134
Stillwater River 1A | MA | 75569.09 | 79753.7 | -4184.61 | -5.247% | 74666.54 | 902.55 | 1.209%
Stillwater River 2 | MA | 154773 | 170679 | -15906 | -9.319% | 156355.5 | -1582.5 | -1.012%
Stillwater River 3 | MA | 153420 | 166403.6 | -12983.6 | -7.802% | 153930.2 | -510.2 | -0.3314%
Stillwater River 4 | MA | 63423.69 | 80983.1 | -17559.41 | -21.68% | 69957.3 | -6533.61 | -9.339% | 1. Inverter 20 4A is offline from 04/11 to 04/14 and was offline on 04/05 and back online on 04/06 2. Inverter 14 4A tripped offline on 04/15 at 14:15 | 1. SR083128 2. SR083462

## May
MN8 Bond |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 2997080.805 | 3076133.86 | -79053.055 | -2.57% | 3037038.1 | -39957.295 | -1.316%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA | 482443.68 | 433338.9 | 49104.78 | 11.33% | 468050 | 14393.68 | 3.075% | 1. Inverters 5.7B & 6.2B are offline between 07:00 to 16:30 on 05/16 2. Inverter 10.2A was offline from 05/24 to 06/02 | 1. SR084771 2. SR085153
Clara Barton | MA | 178515 | 175637.8 | 2877.2 | 1.638% | 174462 | 4053 | 2.323% | 1. Site was offline on 05/08 between 09:15am to 12:45pm 2. Site tripped offline on 05/27 and back online on 05/28 at 07:00am 3. Inverter 8.7 is offline and being RMA'd 4. Inverter 5.10 offline on from 05/26 and being RMA'd 5. Inverter 5.8 offline from 05/26 and back online on 05/28 6. Inverter 4.1 offline from 05/26 and being RMA'd | 1. SR084424 2. SR085200 3. SR083611 4. SR085080 5. SR084869 6. SR085165
Fairhaven Solar | MA | 135590 | 135996.6 | -406.6 | -0.299% | 136467.3 | -877.3 | -0.6429% | 1. Inverter 13 is offline from 05/25 and being RMA'd 2. Inverter 37 is offline on 05/26 & 05/27 3. Inverter 26 is offline from 05/29 4. Inverter 14 was offline from 05/31 | 1. SR085068 2. SR085166 3. SR085290 4. SR085365
Plympton-1 | MA | 180284 | 182321.4 | -2037.4 | -1.117% | 176437.3 | 3846.7 | 2.18% | 1. Inverter 31C tripped offline at 10:30 on 05/16 and back online at 10:30 on 05/20 | 1. SR084772
French River 2 | MA | 173798 | 189859.6 | -16061.6 | -8.46% | 178136 | -4338 | -2.435% | 1. Inverters 43,44,45 are underperforming 7 kW each on 05/21 and fuses were closed on 05/22 | 1. SR084968
French River 3 | MA | 342706 | 360003.1 | -17297.1 | -4.805% | 340894.3 | 1811.7 | 0.5315% | 1. Inverter 40 was underperforming offline from 05/31 2. Inverter 115 was offline throughout the month | 1. SR085387 2. SR083436
French River 4 | MA | 348062 | 367665.5 | -19603.5 | -5.332% | 355344.7 | -7282.7 | -2.049%
French River 5 | MA | 326568 | 356494.8 | -29926.8 | -8.395% | 348966.3 | -22398.3 | -6.418% | 1. Inverter 110 was offline from 05/17 and back online at 14:30 on 05/21 | 1. SR084747
French River 6 | MA | 318681 | 303071 | 15610 | 5.151% | 334789.1 | -16108.1 | -4.811%
Stillwater River 1A | MA | 86181.625 | 89111.65 | -2930.025 | -3.288% | 85923.2 | 258.425 | 0.3008%
Stillwater River 2 | MA | 175262 | 197484.9 | -22222.9 | -11.25% | 179921.2 | -4659.2 | -2.59% | 1. Inverter 8-2C was offline throughout the month | 1. SR084088
Stillwater River 3 | MA | 175939 | 188956.7 | -13017.7 | -6.889% | 177132.5 | -1193.5 | -0.6738%
Stillwater River 4 | MA | 73050.5 | 96191.91 | -23141.41 | -24.06% | 80514.2 | -7463.7 | -9.27% | 1. Inverter 14-4A is offline throughout the month 2. Inverter 22-4A is underperforming 3kW compared to peers. Issue may be internal to the inverter. 3. Inverter 21-4A was offline on 05/13 and back online at 11:00am on 05/14. Inverter 8-4A tripped offline at 12:00pm on 05/15 and back online on 05/16. | 1. SR083462 2. SR083820 3. SR084629

## Jun
MN8 Bond |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 3288648.5288 | 3438527.7 | -149879.1712 | -4.359% | 3031797.19 | 256851.3388 | 8.472%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA | 513004.81 | 474429.1 | 38575.71 | 8.131% | 466058 | 46946.81 | 10.07% | 1. Inverter 10.2A was offline from 05/25 to 06/02 2. Inverter 9.2B was offline from 06/06 to whole month 3. Inverter 6.2C tripped offline at 9:15am 0n 06/02 and back online at 13:00 on 06/03 | 1. SR085153 2. SR085698 3. SR085422
Clara Barton | MA | 195792 | 199036.2 | -3244.2 | -1.63% | 177019.2 | 18772.8 | 10.6% | 1. Inverter 6.5 has not started on 06/01 and was offline for whole month 2. Inverter 4.1 was offline from 05/26 and back online at 13:00 on 06/12 3. Inverter 5.10 was offline from 05/26 and back online at 13:00 on 06/12 4. Inverter 8.7 was offline from 04/21 and back online at 13:00 on 06/12 5. Site tripped offline at 20:26 on 06/26 and back online at 6am on 06/27 | 1. SR085319 2. SR085165 3. SR085080 4. SR083611, SR085080 5. SR087011
Fairhaven Solar | MA | 143791 | 152018.6 | -8227.6 | -5.412% | 137242.2 | 6548.8 | 4.772% | 1. Inverter 14 tripped offline at 12:45pm on 05/31 and back online at 11am on 06/05 2. Inverter 26 tripped offline at 14:00 on 05/29 and back online at 11am on 06/05; again tripped offline at 11:34am on 06/07 and back online on 06/13 3. Inverter 13 tripped offline at 11:30am on 05/31 and back online at 11;30am on 06/05 4. Inverter 15 was offline from 06/06 5. Site was offline from 13:00 of 06/12 to 7:30am of 06/13 6. Site was offline from 09:00 to 14:00 on 06/24 7. Inverters 8 & 47 tripped offline at 13:00 on 06/14 and back online at 9am on 06/17 | 1. SR085365 2. SR085290, SR085839 3. SR085364 4. SR085705 5. SR086107 6. SR086849 7. SR086248
Plympton-1 | MA | 202229 | 208413.9 | -6184.9 | -2.968% | 175764.3 | 26464.7 | 15.06% | 1.Site was taken offline from 9:45am to 10:20am for MV inspection on 06/03
French River 2 | MA | 194880 | 212374.6 | -17494.6 | -8.238% | 177698 | 17182 | 9.669% | 1. Inverters 139, 140 and 141 underproducing since 5/28 and resolved on 06/14 2. Inverter 115 was offlilne from 06/02 to 06/10 and again offline from 06/12 to 06/27 (till 13:00) 3. Inverter 40 tripped offline at 12pm on 05/31 and back online on 06/04 at 13:00 4. Inverter 42 tripped offline at 12pm on 06/07 and back online on 06/11 at 12pm | 1. SR086215 2. SR083436, SR086097 3. SR085387 4. SR085805
French River 3 | MA | 377947 | 402925.7 | -24978.7 | -6.199% | 339915.6 | 38031.4 | 11.19%
French River 4 | MA | 387137 | 411601.5 | -24464.5 | -5.944% | 354323.8 | 32813.2 | 9.261%
French River 5 | MA | 358829 | 398158.3 | -39329.3 | -9.878% | 347965.7 | 10863.3 | 3.122% | 1. Inverter 159 was offline for whole month 2. Inverter 82 tripped offline at 16:00 on 06/04 and was offline for whole month 3. Inverter 162 was offline since 6/20 4. Inverter 179 was offline from 06/13 to 11pm of 06/26 5. Inverter 189 was offline from 06/13 EOD to 9am of 07/03 | 1. SR085403, SR086977 2. SR085562, SR086978 3. SR086905, SR087239, SR087346 4. SR086156 5. SR086177
French River 6 | MA | 350522 | 337585.9 | 12936.1 | 3.832% | 333826.6 | 16695.4 | 5.001% | 1. Inverter 100A tripped offline at 13:15 on 06/22 and was offline for whole month 2. Inverter 72B tripped offline at 11:30 on 05/22 and was back online on 07/03 3. Inverter 75B tripped offline at 15:00 on 06/20 and back online at 8am on 06/28 4. Inverter 93B was offline from 06/13 and was RMA'd | 1. SR086979 2. SR084982, SR087079 3. SR086845 4. SR086243
Stillwater River 1A | MA | 96152.8125 | 100695.2 | -4542.3875 | -4.511% | 85675.3 | 10477.5125 | 12.23%
Stillwater River 2 | MA | 194858 | 220833.7 | -25975.7 | -11.76% | 179402.5 | 15455.5 | 8.615% | 1. Inverter 8C was offline on 06/23, 06/24 & 06/27 | 1. SR086858
Stillwater River 3 | MA | 193311 | 211038.6 | -17727.6 | -8.4% | 176621.8 | 16689.2 | 9.449% | 1. Inverter 42 tripped offline at 12:15pm on 06/06 and back online on 06/12 | 1. SR085724
Stillwater River 4 | MA | 80194.9062 | 109416.4 | -29221.4937 | -26.71% | 80284.19 | -89.2838 | -0.1112% | 1. Inverter 4A was offline from 15:00 of 06/18 to 10am of 06/26 2. Inverter 14A was offline throughout the month | 1. SR086456 2. SR087080, SR086309, SR083462,

## Jul
MN8 Bond |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 3058623.4066 | 3174638.68 | -116015.2734 | -3.654% | 3246713.19 | -188089.7834 | -5.793%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA | 486745.8582 | 440191.6 | 46554.2582 | 10.58% | 510758 | -24012.1418 | -4.701% | 1.Inverter 9.2B was offline from 06/06 2. Inverter 3.1B is offline on 07/02 and back online at 12:00 on 07/03 3.Site tripped offline at 17:45 on 07/11 and back online at 07:30 on 07/12 | 1.SR085698 2.SR087310 3.SR087601
Clara Barton | MA | 184876.1422 | 187364.2 | -2488.0578 | -1.328% | 192129.5 | -7253.3578 | -3.775% | 1.Inverter 3.1 is offline from 07/03 and back online at 06:00 on 07/13 2.Inverter 6.1 started late at 12:00 on 07/08 and at 14:00 on 07/09 and was offline on 07/10 and again started late at 14:30 on 07/11 and offline from 07/12 to 07/17 3.Site was offline from 3:30AM to 04:15AM on 07/18 4.Site tripped offline at 19:30 and back online at 21:00 on 07/31 | 1.SR087350 2.SR087469 3.SR087866 4.SR088482
Fairhaven Solar | MA | 127982 | 134285.1 | -6303.1 | -4.694% | 142715.9 | -14733.9 | -10.32% | 1.Inverter 15 was offline through the month 2.Inverter 38 tripped offline at 10:30 on 07/02 and back online at 06:00 on 07/03 3.Inverters 1,12,21,25,28,29,40,41 &49 are offline on 07/07 and back online at 06:00 on 07/08 4.Inverters 1,12,21,28,29 and 41 are tripped offline at 08:00 on 07/11 and back online at 06:00 on 07/12 5.Inverter 29 is offline on 07/13 and back online at 08:00 on 07/15 6. Inverter 55 tripped offline at 13:15 on 07/20 and back online at 07:15 on 07/22 7.Inverter 26 is offline on 07/27 through out the month | 1.SR085705 2.SR087247 3.SR087440 4.SR087585 5.SR087646 6.SR087963 7.SR088298
Plympton-1 | MA | 179785 | 187563.7 | -7778.7 | -4.147% | 186487.5 | -6702.5 | -3.594% | 1.Site tripped offline at 11:15 on 07/16 and back online at 10:15 on 07/17 | 1.SR087757
French River 2 | MA | 181691 | 196897.2 | -15206.2 | -7.723% | 189634 | -7943 | -4.189%
French River 3 | MA | 355233.75 | 371355.6 | -16121.85 | -4.341% | 362679.2 | -7445.45 | -2.053% | 1. Inverter 28 is tripped offline at 14:00 on 07/09 throgh out the month | 1.SR087518
French River 4 | MA | 360195 | 380111.8 | -19916.8 | -5.24% | 378047.8 | -17852.8 | -4.722%
French River 5 | MA | 332622 | 366566.7 | -33944.7 | -9.26% | 371263 | -38641 | -10.41% | 1. Inverter 82 is offline for whole month 2.Inverter 126 is offline for whole day on 07/01 3.Inverter 159 was back online at 11:15 on 07/26 4.Inverter 162 is back online at 12:45 on 07/26 5.Inverter 77 tripped offline at 07:00 on 07/07 and back online at 15:45 on 07/22 6. Inverter 78 tripped offline at 15:00 on 07/05 and back online at 17:00 on 07/05 7.Inverter 111 was offline on 07/07 for whole day 8.Inverter 158 started late for production at 13:00 on 07/08 9.Inverter 134 has tripped offline at 16:00 on 07/08 and back online at 14:00 on 07/10 10.Inverter 132 tripped offline at 09:30 and back online 14:00 on 07/10 11Inverter 5 tripped offline at 10:00 on 07/11 and back online 10:00 on 07/23 12.Inverter 191 tripped offline at 16:00 on 07/13 and back online at 06:00 on 07/15 13.Inverter 109 tripped offline at 18:00 on 07/14 and back online at 15:30 on 07/17 14.Inverter 139 tripped offline at 08:15 on 07/24 back online at 12:15 on 07/25 | 1.SR086978 2.SR087174 3.SR086977 4.SR087239 5.SR087375 6.SR087397 7.SR087448 8.SR087466 9.SR087488 10.SR087546 11.SR087587 12.SR087650 13.SR087698 14.SR088122
French River 6 | MA | 324462 | 309330.1 | 15131.9 | 4.892% | 356180.5 | -31718.5 | -8.905% | 1.Inverter 6A-100 is back online at 08:00 on 07/25 2.Inverter 72B was back online on 07/03 3. Inverter 6A.83 was offline on 07/06 and back online on 07/07 4.Inverter 83 tripped offline at 10:36 on 07/26 and back online on 07/27 and again tripped offline at 10:00 5. Inverter 72A, 73A are tripped offline at 13:15 on 07/30 and back online on 07/31 | 1.SR086979 2. SR084982, SR087079 3.SR087410 4.SR088283
Stillwater River 1A | MA | 89895.25 | 92359.28 | -2464.03 | -2.668% | 91392.93 | -1497.68 | -1.639%
Stillwater River 2 | MA | 181299 | 208466.5 | -27167.5 | -13.03% | 191373.8 | -10074.8 | -5.264% | 1.Inverter 8C started late at 14:30 on 07/05 and again offline at 07/06 and back online on 07/07 at 12:30 and started late at 12:15 on 07/18 again started late at 14:30 on 07/25 again offline at 07/29 and back online on 07/30 at 15:30 | 1.SR086858
Stillwater River 3 | MA | 180272 | 196561.6 | -16289.6 | -8.287% | 188408.3 | -8136.3 | -4.318%
Stillwater River 4 | MA | 73564.4062 | 103585.3 | -30020.8938 | -28.98% | 85642.76 | -12078.3537 | -14.1% | 1.Inverter 17 tripped offline on 07/06 at 14:45 through out the month 2. Inverter 4B.11 is offline for whole day on 07/17 and back online at 13:30 on 07/18 3. Inverter 23-4B tripped offline at 08:15 on 07/24 and back online at 16:45 on 07/25 | 1.SR087425 2.SR087841 3.SR088124

## Aug
MN8 Bond |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA
Clara Barton | MA
Fairhaven Solar | MA
Plympton-1 | MA
French River 2 | MA
French River 3 | MA
French River 4 | MA
French River 5 | MA
French River 6 | MA
Stillwater River 1A | MA
Stillwater River 2 | MA
Stillwater River 3 | MA
Stillwater River 4 | MA

## Sep
MN8 Bond |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA
Clara Barton | MA
Fairhaven Solar | MA
Plympton-1 | MA
French River 2 | MA
French River 3 | MA
French River 4 | MA
French River 5 | MA
French River 6 | MA
Stillwater River 1A | MA
Stillwater River 2 | MA
Stillwater River 3 | MA
Stillwater River 4 | MA

## Oct
MN8 Bond |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA
Clara Barton | MA
Fairhaven Solar | MA
Plympton-1 | MA
French River 2 | MA
French River 3 | MA
French River 4 | MA
French River 5 | MA
French River 6 | MA
Stillwater River 1A | MA
Stillwater River 2 | MA
Stillwater River 3 | MA
Stillwater River 4 | MA

## Nov
MN8 Bond |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA
Clara Barton | MA
Fairhaven Solar | MA
Plympton-1 | MA
French River 2 | MA
French River 3 | MA
French River 4 | MA
French River 5 | MA
French River 6 | MA
Stillwater River 1A | MA
Stillwater River 2 | MA
Stillwater River 3 | MA
Stillwater River 4 | MA

## Dec
MN8 Bond |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Grafton II | MA
Clara Barton | MA
Fairhaven Solar | MA
Plympton-1 | MA
French River 2 | MA
French River 3 | MA
French River 4 | MA
French River 5 | MA
French River 6 | MA
Stillwater River 1A | MA
Stillwater River 2 | MA
Stillwater River 3 | MA
Stillwater River 4 | MA

## Sites
Portfolio: | MN8 Bond
Site DAS Name | Site | State | Update | DAS
MA-02-001 - Grafton II | Grafton II | MA | AEF | PowerTrack
MA-02-002 - Clara Barton | Clara Barton | MA | AEF | PowerTrack
MA-02-003 - Fairhaven Solar | Fairhaven Solar | MA | AEF | PowerTrack
MA-02-004 - Plympton | Plympton-1 | MA | AEF | PowerTrack
MA-02-005A - French River 2 | French River 2 | MA | AEF | PowerTrack
MA-02-005B - French River 3 | French River 3 | MA | AEF | PowerTrack
MA-02-005C - French River 4 | French River 4 | MA | AEF | PowerTrack
MA-02-005D - French River 5 | French River 5 | MA | AEF | PowerTrack
MA-02-005E - French River 6 | French River 6 | MA | AEF | PowerTrack
MA-02-006A - Stillwater River 1A | Stillwater River 1A | MA | AEF | PowerTrack
MA-02-006B - Stillwater River 2 | Stillwater River 2 | MA | AEF | PowerTrack
MA-02-006C - Stillwater River 3 | Stillwater River 3 | MA | AEF | PowerTrack
MA-02-006D - Stillwater River 4 | Stillwater River 4 | MA | AEF | PowerTrack