## Year to Date
MN8 NY8 |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 31851706.3592 | 30016703.03 | 1835003.3292 | 6.113% | 32070529.82 | -218823.4608 | -0.6823%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Janis | NY | 15775777.3592 | 15473637.58 | 302139.7792 | 1.953% | 16103107.5 | -327330.1408 | -2.033%
Puckett Solar | NY | 16075929 | 14543065.45 | 1532863.55 | 10.54% | 15967422.32 | 322802 | 2.022%

## 1st Qtr
MN8 NY8 |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 11520955.9415 | 10438513.4 | 1082442.5415 | 10.37% | 11714693 | -193737.0585 | -1.654%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Janis | NY | 5634708.9415 | 5879750 | -245041.0585 | -4.168% | 6151248 | -516539.0585 | -8.397%
Puckett Solar | NY | 5886247 | 4558763.4 | 1327483.6 | 29.12% | 5563445 | 322802 | 5.802%

## 2nd Qtr
MN8 NY8 |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 20330750.4177 | 19578189.63 | 752560.7877 | 3.844% | 20355836.82 | -25086.4023 | -0.1232%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Janis | NY | 10141068.4177 | 9593887.58 | 547180.8377 | 5.703% | 9951859.5 | 189208.9177 | 1.901%
Puckett Solar | NY | 10189682 | 9984302.05 | 205379.95 | 2.057% | 10403977.32 | -214295.32 | -2.06%

## 3rd Qtr
MN8 NY8 |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Janis | NY | 0 | 0 | 0 |  |  | 0
Puckett Solar | NY | 0 | 0 | 0 |  |  | 0

## 4th Qtr
MN8 NY8 |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Janis | NY | 0 | 0 | 0 |  |  | 0
Puckett Solar | NY | 0 | 0 | 0 |  |  | 0

## Jan
MN8 NY8 |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1386024.184 | 1687476.4 | -301452.216 | -17.86% | 2753954 | -1367929.816 | -49.67%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY | 641158.184 | 1056577 | -415418.816 | -39.32% | 1516236 | -875077.816 | -57.71% | 1. Inverter 3.1,4.1 Module 1 and 5.1 module 2 has not started production on 01/09, 01/16, 01/18, 01/19 and 01/31 2.Inverter module 1.1 offline on 01/19 to 01/22 and started on 01/23 at 12:15 | 1.SR080623, SR080624 2.SR080390
Puckett Solar | NY | 744866 | 630899.4 | 113966.6 | 18.06% | 1237718 | -492852 | -39.82% | 1.Production meter was damaged they had to by pass the meter. 2.Inverter 5.1 module 2 is offfline on 01/17 and started on 01/18 at 10:45 3.Site tripped offlinedue to Utility planned outage on 01/25 at 12:00 and back online 02/01. Actual energy data is taken from Inverters data since production meter data is not available*** | 1.SR073174 2.SR080283 3.SR080466

## Feb
MN8 NY8 |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 5046188.7575 | 4124450 | 921738.7575 | 22.35% | 3585377 | 1460811.7575 | 40.74%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY | 2476319.7575 | 2363767 | 112552.7575 | 4.762% | 1923083 | 553236.7575 | 28.77% | 1. Inverter 5.1 module 1 did not start for production and back online at 14:00 on 02/29 | 1. SR081450
Puckett Solar | NY | 2569869 | 1760683 | 809186 | 45.96% | 1662294 | 907575 | 54.6% | 1. Inverters 6.1 Combiner boxes 1,2,3, 12,18,19,20 were barely producing on 02/09 and and issue resolved due to inverter being powercycled at 14:00. Issue reoccurred on 02/13 and resolved due to inverter being powercycled at 09:00 on 02/14 | 1. SR080883, SR080968

## Mar
MN8 NY8 |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 5088743 | 4626587 | 462156 | 9.989% | 5375362 | -286619 | -5.332%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY | 2517231 | 2459406 | 57825 | 2.351% | 2711929 | -194698 | -7.179%
Puckett Solar | NY | 2571512 | 2167181 | 404331 | 18.66% | 2663433 | -91921 | -3.451%

## Apr
MN8 NY8 |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 5434443.04 | 5120409.63 | 314033.41 | 6.133% | 6170938.82 | -736495.78 | -11.93%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY | 2731784.04 | 2587991.58 | 143792.46 | 5.556% | 3099310.5 | -367526.46 | -11.86% | 1.Inverter 6.1 module 1 and module 2 tripped offline on 04/06 at 12:15 and came back online on 04/12 at 11:45. 2.AE has set the PPC back to it’s 20Mw limit, because site is producing beyond what is allowed in interconnection agreement. Site is supposed to be capped at 20MW, but produces 22.2MW on sunny days. 3.LM2 pyranometer reporting 0 value | 1.SR083149 2.SR083699 3.SR079176
Puckett Solar | NY | 2702659 | 2532418.05 | 170240.95 | 6.722% | 3071628.32 | -368969.32 | -12.01% | 1.Inverter 6.1 combiner boxes 1, 2, 3, 12, 18, 19, 20 are offline on 04/07 throughout the day. 2.Inverter 6.1 combiner boxes 4-7 and 13 to 15 are offline on 04/25 and back online on 04/26 3.Inverter 6.1 combiner boxes 1, 2, 3, 12, 18, 19, 20 are offline again on 04/20 at 06:30am and came back online on 04/22 at 02:30pm. 4. Inverter 6.1 combiner boxes 1, 2, 3, 12, 18, 19, 20 are offline again on 04/23 from 06:30am back online at 15:30 5. Inverter 6.1 combiner boxes 1, 2, 3, 12, 18, 19, 20 are offline again on 04/29 from 06:30am back online at 15:30 6. Production meter was damaged they had to by pass the meter. | 1. SR083157 2. SR083794 3. SR083961 4. SR083741 5. SR083961 6. SR073174

## May
MN8 NY8 |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 7337210 | 7060126 | 277084 | 3.925% | 7197771 | 139439 | 1.937%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY | 3675907 | 3486882 | 189025 | 5.421% | 3475027 | 200880 | 5.781%
Puckett Solar | NY | 3661303 | 3573244 | 88059 | 2.464% | 3722744 | -61441 | -1.65% | 1. Inverter 4.1 module 1 and 2 tripped offline on 05/12 at 13:55 and back online on 05/13 at 09:00 am. 2. Inverter 3, Combiner box 3 - String 7 offline from 05/23 to 05/29. | 1. SR084601 2. SR085088

## Jun
MN8 NY8 |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 7559097.3777 | 7397654 | 161443.3777 | 2.182% | 6987127 | 571970.3777 | 8.186%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY | 3733377.3777 | 3519014 | 214363.3777 | 6.092% | 3377522 | 355855.3777 | 10.54%
Puckett Solar | NY | 3825720 | 3878640 | -52920 | -1.364% | 3609605 | 216115 | 5.987% | 1. Site tripped offline at 09:36 on 06/10 and back online at 10:32 on 06/10 2. Inverter 6.1 Combiner boxes 1, 2, 3, 12, 18, 19, 20 are barely producing through out the day on 06/17 and resolved on 06/18 and also again inverter 6.1 Combiner boxes 1, 2, 3, 12, 18, 19 & 20 are barely producing (approximately 10 Amp) through out the day on 06/27 and resolved on 06/28 3. Production meter was damaged they had to by pass the meter. Actual energy data is taken from Inverters data since production meter data is not available*** | 1. SR085806 2. SR086319 3. SR073174

## Jul
MN8 NY8 |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY
Puckett Solar | NY

## Aug
MN8 NY8 |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY
Puckett Solar | NY

## Sep
MN8 NY8 |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY
Puckett Solar | NY

## Oct
MN8 NY8 |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY
Puckett Solar | NY

## Nov
MN8 NY8 |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY
Puckett Solar | NY

## Dec
MN8 NY8 |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Janis | NY
Puckett Solar | NY

## Sites
Portfolio: | MN8 NY8
Site DAS Name | Site | State | Update | DAS
Janis | Janis | NY |  | PowerTrack
Puckett Solar | Puckett Solar | NY |  | PowerTrack