## Year to Date
Ecofin |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 41898728.0067 | 43530154.4131 | -1631426.4064 | -3.748% | 45142398.952 | -3243670.9453 | -7.185%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 681782.96 | 1262396.2066 | -580613.2466 | -45.99% | 1322015.77 | -501625.81 | -37.94%
San Luis Valley | CO | 1198880.4824 | 1109984.942 | 88895.5404 | 8.009% | 0 | 1198880.4824
Golden NREL 2 | CO | 118530 | 111165.3515 | 7364.6485 | 6.625% | 121822.312 | -3292.312 | -2.703%
Golden NREL Wind 3 | CO | 235974.7853 | 681892.41 | -445917.6247 | -65.39% | 0 | 235974.7853
Pratt Solar Farm | KS | 9225590 | 11102721.191 | -1877131.191 | -16.91% | 10754911.31 | -1529321.31 | -14.22%
Rochester - 5516 Valleyhigh NW | MN | 13837474.779 | 15938864.85 | -2101390.071 | -13.18% | 16463344.99 | -2625870.211 | -15.95%
Warsaw - 2201 Richmond | VA | 7767883.1 | 5126638.051 | 2641245.049 | 51.52% | 6955916.43 | 811966.67 | 11.67%
Mount Jackson - Randolf | VA | 3938178.8 | 4019700.2 | -81521.4 | -2.028% | 4007371.3 | -69192.5 | -1.727%
Callands Gretna - Monroe | VA | 2615728 | 1914485.402 | 701242.598 | 36.63% | 2766555.57 | -150827.57 | -5.452%
Rockbridge Baths - Small Mouth Bass | VA | 2278705.1 | 2262305.809 | 16399.291 | 0.7249% | 2750461.27 | -471756.17 | -17.15%

## 1st Qtr
Ecofin |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 2107421 | 2460365.2047 | -352944.2047 | -14.35% | 2220161.3 | -112740.3 | -5.078%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 288610 | 269702.0699 | 18907.9301 | 7.011% | 311701.3 | -23091.3 | -7.408%
San Luis Valley | CO | 0 | 0 | 0 |  | 0 | 0
Golden NREL 2 | CO | 22181 | 22245.2058 | -64.2058 | -0.2886% | 28731.96 | -6550.96 | -22.8%
Golden NREL Wind 3 | CO | 0 | 0 | 0 |  | 0 | 0
Pratt Solar Farm | KS | 1796630 | 2168417.929 | -371787.929 | -17.15% | 1879728.04 | -83098.04 | -4.421%
Rochester - 5516 Valleyhigh NW | MN | 0 | 0 | 0 |  | 0 | 0
Warsaw - 2201 Richmond | VA | 0 | 0 | 0 |  | 0 | 0
Mount Jackson - Randolf | VA | 0 | 0 | 0 |  | 0 | 0
Callands Gretna - Monroe | VA | 0 | 0 | 0 |  | 0 | 0
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Ecofin |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 12072123.0177 | 15855426.8949 | -3783303.8772 | -23.86% | 16394922.89 | -4322799.8723 | -26.37%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 171524 | 471593.7604 | -300069.7604 | -63.63% | 412241.35 | -102110.35 | -24.77%
San Luis Valley | CO | 403386.4177 | 168822.4 | 234564.0177 | 138.9% | 0 | 403386.4177
Golden NREL 2 | CO | 40847 | 36063.9035 | 4783.0965 | 13.26% | 40515.72 | 331.28 | 0.8177%
Golden NREL Wind 3 | CO | 28261 | 81324 | -53063 | -65.25% | 0 | 28261
Pratt Solar Farm | KS | 2543370 | 3358562.73 | -815192.73 | -24.27% | 3405558.5 | -862188.5 | -25.32%
Rochester - 5516 Valleyhigh NW | MN | 3935122 | 6649248.45 | -2714126.45 | -40.82% | 7166100.09 | -3230978.09 | -45.09%
Warsaw - 2201 Richmond | VA | 3142172.4 | 3258789.451 | -116617.051 | -3.579% | 3404946.43 | -262774.03 | -7.717%
Mount Jackson - Randolf | VA | 769106.9 | 866456.3 | -97349.4 | -11.24% | 828310.8 | -59203.9 | -7.148%
Callands Gretna - Monroe | VA | 552581 | 472595.2 | 79985.8 | 16.92% | 582500 | -29919 | -5.136%
Rockbridge Baths - Small Mouth Bass | VA | 485752.3 | 491970.7 | -6218.4 | -1.264% | 554750 | -68997.7 | -12.44%

## 3rd Qtr
Ecofin |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 19178742.8577 | 15923513.8236 | 3255229.0341 | 20.44% | 18559425.72 | 619317.1377 | 3.337%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 75483.96 | 349159.9263 | -273675.9663 | -78.38% | 385554.62 | -310070.66 | -80.42%
San Luis Valley | CO | 516756.8316 | 598577.842 | -81821.0104 | -13.67% | 0 | 516756.8316
Golden NREL 2 | CO | 39208 | 35497.9523 | 3710.0477 | 10.45% | 37829.29 | 1378.71 | 3.645%
Golden NREL Wind 3 | CO | 117586.3872 | 427229.96 | -309643.5728 | -72.48% | 0 | 117586.3872
Pratt Solar Farm | KS | 2901160 | 3473493.732 | -572333.732 | -16.48% | 3477587.67 | -576427.67 | -16.58%
Rochester - 5516 Valleyhigh NW | MN | 7655387.779 | 6856021 | 799366.779 | 11.66% | 7122057 | 533330.779 | 7.488%
Warsaw - 2201 Richmond | VA | 3129137.3 | 207824.7 | 2921312.6 | 1406% | 2241955 | 887182.3 | 39.57%
Mount Jackson - Randolf | VA | 2101915.4 | 2153510.4 | -51595 | -2.396% | 2246960.3 | -145044.9 | -6.455%
Callands Gretna - Monroe | VA | 1383884 | 740593.802 | 643290.198 | 86.86% | 1515055.57 | -131171.57 | -8.658%
Rockbridge Baths - Small Mouth Bass | VA | 1258223.2 | 1081604.509 | 176618.691 | 16.33% | 1532426.27 | -274203.07 | -17.89%

## 4th Qtr
Ecofin |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 8540441.1313 | 9290848.49 | -750407.3587 | -8.077% | 7967889.042 | 572552.0893 | 7.186%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 146165 | 171940.45 | -25775.45 | -14.99% | 212518.5 | -66353.5 | -31.22%
San Luis Valley | CO | 278737.2331 | 342584.7 | -63847.4669 | -18.64% | 0 | 278737.2331
Golden NREL 2 | CO | 16294 | 17358.29 | -1064.29 | -6.131% | 14745.342 | 1548.658 | 10.5%
Golden NREL Wind 3 | CO | 90127.3982 | 173338.45 | -83211.0518 | -48% | 0 | 90127.3982
Pratt Solar Farm | KS | 1984430 | 2102246.8 | -117816.8 | -5.604% | 1992037.1 | -7607.1 | -0.3819%
Rochester - 5516 Valleyhigh NW | MN | 2246965 | 2433595.4 | -186630.4 | -7.669% | 2175187.9 | 71777.1 | 3.3%
Warsaw - 2201 Richmond | VA | 1496573.4 | 1660023.9 | -163450.5 | -9.846% | 1309015 | 187558.4 | 14.33%
Mount Jackson - Randolf | VA | 1067156.5 | 999733.5 | 67423 | 6.744% | 932100.2 | 135056.3 | 14.49%
Callands Gretna - Monroe | VA | 679263 | 701296.4 | -22033.4 | -3.142% | 669000 | 10263 | 1.534%
Rockbridge Baths - Small Mouth Bass | VA | 534729.6 | 688730.6 | -154001 | -22.36% | 663285 | -128555.4 | -19.38%

## Jan
Ecofin |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 78991 | 79673 | -682 | -0.856% | 100783 | -21792 | -21.62% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 72896 | 73786 | -890 | -1.206% | 93005 | -20109 | -21.62% | 1. Inverter 1 is offline on 01/09, 01/10, 01/12, 01/17. | 1. SR080094
San Luis Valley | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicating from 04/22 | 1. SR077495
Golden NREL 2 | CO | 6095 | 5887 | 208 | 3.533% | 7778 | -1683 | -21.64% | 1. Inverter was barely produced on 1/13, 1/14 and 1/15 | 1. SR080235
Golden NREL Wind 3 | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicating from 05/23/2022 | 1. SR079089
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Feb
Ecofin |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 911881 | 1076640.553 | -164759.553 | -15.3% | 944891.36 | -33010.36 | -3.494% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 100394 | 90505.5 | 9888.5 | 10.93% | 97813.3 | 2580.7 | 2.638%
San Luis Valley | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site stopped communicating from 04/22 | 1. SR077494
Golden NREL 2 | CO | 6597 | 7237.8 | -640.8 | -8.854% | 8862.2 | -2265.2 | -25.56%
Golden NREL Wind 3 | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicating from 05/23/2022 | 1. SR079089
Pratt Solar Farm | KS | 804890 | 978897.253 | -174007.253 | -17.78% | 838215.86 | -33325.86 | -3.976% | 1.(A) Inverter 2 was taken offline by technician on 02/26/2024 at 13:30 to 15:00 & inverter 1 at 15:00 - 16:15. 1.(B) Inverter 2 tripped offline on 02/27/2024 at 15:48 & back online at 12:00 on 02/28/2024. | 1. SR081345
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Mar
Ecofin |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 1116549 | 1304051.6517 | -187502.6517 | -14.38% | 1174486.94 | -57937.94 | -4.933% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 115320 | 105410.5699 | 9909.4301 | 9.401% | 120883 | -5563 | -4.602%
San Luis Valley | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site stopped communicating from 04/22/20223 and communication regained on 04/03 | 1. SR077494
Golden NREL 2 | CO | 9489 | 9120.4058 | 368.5942 | 4.041% | 12091.76 | -2602.76 | -21.53%
Golden NREL Wind 3 | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicating from 05/23/2022 | 1. SR079089
Pratt Solar Farm | KS | 991740 | 1189520.676 | -197780.676 | -16.63% | 1041512.18 | -49772.18 | -4.779% | 1. Inverter 2 is derating, due to overheating 2 modules are offline | 1. SR081345
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Apr
Ecofin |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 3747463.737 | 4085138.2825 | -337674.5455 | -8.266% | 4373274.39 | -625810.653 | -14.31% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 129640 | 120725.5538 | 8914.4462 | 7.384% | 129601.73 | 38.27 | 0.02953%
San Luis Valley | CO | 100708.837 | 0 | 100708.837 |  | 0 | 100708.837
Golden NREL 2 | CO | 12208 | 10993.1857 | 1214.8143 | 11.05% | 12899.28 | -691.28 | -5.359%
Golden NREL Wind 3 | CO | 0 | 0 |  | 0% | 0 | 0 |  | 1. Site was not communicating from 05/23/2022 | 1. SR079089
Pratt Solar Farm | KS | 883580 | 1136253.17 | -252673.17 | -22.24% | 1094871.95 | -211291.95 | -19.3% | 1. Inverter 2 is derating, due to overheating 2 modules are offline 2. Site is offline from 04/17 to 04/19. | 1. SR081345 2. SR083483
Rochester - 5516 Valleyhigh NW | MN | 1731010 | 1818032.74 | -87022.74 | -4.787% | 2098181.42 | -367171.42 | -17.5% | 1. Inverter 37 is derating due to fan fault during peak hours 2. Inverter 60 is derating during morning hours due to issue with tracker 3. Inverter 30 tripped offline at 12:45 on 04/19 and was back online at 13:00 on 04/22 4. Inverter 47 was offline from 04/01 and was replaced at 13:00 on 04/23 5. Inverter 53 tripped offline at 14:00 on 04/24 and back online at 07:00 on 05/26 | 1. SR083529 2. SR085269 3. SR083529 4. SR083529 5. SR083529
Warsaw - 2201 Richmond | VA | 890316.9 | 999133.633 | -108816.733 | -10.89% | 1037720.01 | -147403.11 | -14.2% | 1. Inverters production not as expected due to issue with trackers throughout the month | 1. SR087216
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## May
Ecofin |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 3618468.59 | 4947868.0124 | -1329399.4224 | -26.87% | 4965072.7 | -1346604.11 | -27.12% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 41884 | 123308.2066 | -81424.2066 | -66.03% | 144032.62 | -102148.62 | -70.92% | 1. Inverter 2 is offline since 05/03. 2. Inverter 1 didn't start for producton on 05/21 and back online at 01:15 on 05/21 and again offline since 05/22 | 1. SR084239 2. SR084949
San Luis Valley | CO | 122065.89 | 0 | 122065.89 |  | 0 | 122065.89 |  | 1. Site was offline from 05/10 at 07:00am to 11:00am on 05/10. | 1. SR084536
Golden NREL 2 | CO | 14328 | 12274.7178 | 2053.2822 | 16.73% | 13666.44 | 661.56 | 4.841%
Golden NREL Wind 3 | CO | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicating from 05/23/2022 | 1. SR079089
Pratt Solar Farm | KS | 895550 | 1150841.56 | -255291.56 | -22.18% | 1173647.55 | -278097.55 | -23.7% | 1. Inverter 2 is derating, due to overheating 2 modules are offline 2. Inverter 1 is derating since 05/28. | 1. SR081345 2. SR085401
Rochester - 5516 Valleyhigh NW | MN | 1472046 | 2533439.71 | -1061393.71 | -41.9% | 2459554.67 | -987508.67 | -40.15% | 1. Inverter 1 is offline due to a permanent fault of the power module. Fault0010 at 14:00 from 05/21. 2. Inverter 27 tripped offline due to bus imbalance. Protect0070 at 12:30PM on 05/23. 3. Inverter 35 tripped offline due to AC SPD Fault. Warn0070 at 11:30 on 05/18. 4. Inverter 49 tripped offline due to bus imbalance. Protect0070 at 15:45 on 05/25. 5. Inverter 71 tripped offline due to a permanent fault of the power module. Fault0010 at 15:15 on 05/05. 6. Inverter 40 tripped offline and reporting Grid Phase Voltage Out of Range at 18:15 on 05/29. 7. Meter MV 2 is not communicated for whole month. | 1. SR085262 2. SR085263 3. SR085264 4. SR085265 5. SR085266 6. SR085294 7. SR085267
Warsaw - 2201 Richmond | VA | 1072594.7 | 1128003.818 | -55409.118 | -4.912% | 1174171.42 | -101576.72 | -8.651% | 1. Inverter 27 was derating due to fan fault during peak hours throughout the month till 05/22. Inverter 12 is derating due to external fan fault since 05/28 | 1. SR085335
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Jun
Ecofin |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 4706190.6907 | 6822420.6 | -2116229.9093 | -31.02% | 7056575.8 | -2350385.1093 | -33.31%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 0 | 227560 |  |  | 138607 |  | 0% | 1. Site is offline from 05/21/2024 | 1. SR084949, SR084239
San Luis Valley | CO | 180611.6907 | 168822.4 | 11789.2907 | 6.983% |  | 180611.6907
Golden NREL 2 | CO | 14311 | 12796 | 1515 | 11.84% | 13950 | 361 | 2.588%
Golden NREL Wind 3 | CO | 28261 | 81324 | -53063 | -65.25% | 0 | 28261 |  | 1. Site started communicating in Also Energy from 6/11.
Pratt Solar Farm | KS | 764240 | 1071468 | -307228 | -28.67% | 1137039 | -372799 | -32.79% | 1. Inverter 2 tripped offline at 15:00 on 06/15 and back online 06/24 at 14:45 2. Inverter 1 is derated by 1MW on 06/01 and back to expected production on 06/02 and inverter again derated on 06/02, back to expected production on 06/03 3. Inverter 1 started late on 06/09. 4. Inverter 2 is underperforming 550kW compared to inverter 1 for whole month. | 1. SR086275 2. SR085401 3. SR085772 4. SR085507
Rochester - 5516 Valleyhigh NW | MN | 732066 | 2297776 | -1565710 | -68.14% | 2608364 | -1876298 | -71.93% | 1. Inverters 29,30, 51,52,60 are perfroming low compared to peers due to issue with trackers 2. Inverter 64 tripped offline at 09:00 on 06/18 and back online at 16:00 on the same day 3. Inverter 80 tripped offline at 07:15 on 06/25 and back online on 06/26 4. Inverter 1 is offline from 05/21 and is still offline 5. Inverter 27 is from 05/23 and is still offline 6. Inverter 35 is offline from 05/18 and is still offline 7. Inverter 49 is offline from 05/25 and is still offline 8. Inverter 71 is offline from 05/05 and is still offline 9. Inverter 40 is offline from 05/29 and is still offline 10. Meter MV 2 is not communicated for whole month. | 1. SR085269 2. SR086382 3. SR086892 4. SR085262 5. SR085263 6. SR085264 7. SR085265 8. SR085266 9. SR085294 10. SR085267
Warsaw - 2201 Richmond | VA | 1179260.8 | 1131652 | 47608.8 | 4.207% | 1193055 | -13794.2 | -1.156% | 1. Inverter 31 is derating during peak hours due to fan fault from 06/01 and fan replaced on 06/26 2. Site tripped offline at 11:00 on 06/20 and back online at 12:45 on 06/26 | 1. SR085551 2. SR086496
Mount Jackson - Randolf | VA | 769106.9 | 866456.3 | -97349.4 | -11.24% | 828310.8 | -59203.9 | -7.148% | 1. Inverter 24 tripped offline at 16:30 on 06/06 and back online the next day. Inverter 24 again tripped offline at 17:15 on 06/17 and back online the next day 2. Site offline from 13:15 to 18:45 on 06/09 due to utility outage. Site again offline from 09:15 to 13:00 on 06/11 due to utility outage. 3. Inverters 13 and 20 are undeperforming compared to peers and back to expected production on 06/26 4. Inverter 15 tripped offline at 15:30 on 06/18 and back online on 06/19 5. Inverter 9 tripped offline at 10:15 on 06/23 and back online on next day | 1. SR085722 2. SR085785 3. SR086324 4. SR086416 5. SR086758
Callands Gretna - Monroe | VA | 552581 | 472595.2 | 79985.8 | 16.92% | 582500 | -29919 | -5.136% | 1. Inverters 6 and 10 tripped offline on 06/07 and back online at 18:30 on 06/11 but were curtailed to 50%. Inverters 6 and 10 started producing at rated capacity since 06/18 2. Site production sligthly dropping due to stuck trackers | 1. SR085882 2. SR087034, SR087035, SR087036
Rockbridge Baths - Small Mouth Bass | VA | 485752.3 | 491970.7 | -6218.4 | -1.264% | 554750 | -68997.7 | -12.44% | 1. Inverter 17 is underperforming by 28 kW and Inverter 18 is underperforming by 14kW according to site drawing. | 1. SR086325

## Jul
Ecofin |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 7769255.4867 | 5843224.9168 | 1926030.5699 | 32.96% | 7281625.16 | 487630.3267 | 6.697%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 0 | 125175.026 | -125175.026 | -100% | 135055.79 | -135055.79 | -100% | 1. Inverters 1 and 2 are offline for whole month. | 1. SR084949
San Luis Valley | CO | 199168.4523 | 179692.7 | 19475.7523 | 10.84% | 0 | 199168.4523
Golden NREL 2 | CO | 14687 | 13362.5908 | 1324.4092 | 9.911% | 13730.47 | 956.53 | 6.966%
Golden NREL Wind 3 | CO | 49800.0554 | 168468.2 | -118668.1446 | -70.44% | 0 | 49800.0554 |  | 1. There is a drop in production of 244 kW for most of days due to inverters 2 and 3 coolant systems will need to be recharged. | 1. SR087552
Pratt Solar Farm | KS | 952350 | 1179167 | -226817 | -19.24% | 1208224 | -255874 | -21.18% | 1. Inverter 2 is underperforming 550kW compared to inverter 1 for whole month. 2. Inverter 1 was derated by 1MW on 07/08, 07/09. 3. Inverter 1 was offline from 11:00am on 07/17 to 08:00am on 07/18 and inverter 2 was offline from 11:00 am on 07/18 to 15:00 on 07/20. | 1. SR085507 2. SR085401 3. PM7787
Rochester - 5516 Valleyhigh NW | MN | 3575657.779 | 2400687 | 1174970.779 | 48.94% | 2807476 | 768181.779 | 27.36% | 1. Inverter 1, 27, 35, 49 and 71 were offline from 07/01 to 07/09, Inverter 40 was offline from 07/01 to 07/30. 2. 20 to 30 tables were damaged due to strom(Number of modules damaged was unknown). 3. Inverter 43 was tripped offline on 07/15. 4. Inverter 58 was tripped offline on 07/19. 5. Inverter 70 was tripped offline on 07/17. | 1. SR085267 2. SR087734 3. SR087813 4. SR087934 5. SR087831
Warsaw - 2201 Richmond | VA | 1235587.6 | 207824.7 | 1027762.9 | 494.5% | 1146445 | 89142.6 | 7.776% | 1. Weather station was not communicated from 07/04 to 07/17 | 1. SR087384
Mount Jackson - Randolf | VA | 773484.9 | 809053.4 | -35568.5 | -4.396% | 842118.9 | -68634 | -8.15% | 1. Inverter 15 was tripped offline on 07/01 at 15:00and back online on 07/02 at 07:00 2. Site was tripped offline on 07/17 at 15:00 and back online on 07/18 at 11:00am 3. site was offline from 1:45 pm to 3:15 pm on 07/19, Site was offline on 07/23 from 10:15 to 11:30 and 13:15 to 13:45. 4. Inverter 9 was tripped offline on 07/19 at 13:00 and back online on 07/20, Inverter 9 again tripped offline on 07/21 at 16:00 and back online on 07/22 at 07:00 5. Inverter 24 tripped offline on 07/03 at 13:00 and back online on 07/04, Inverter 24 tripped offline on 07/24 at 13:00 and back online on 07/25 | 1. SR086416 2. SR087847 3. SR087932 4. SR086758 5. SR088273
Callands Gretna - Monroe | VA | 498995 | 369802.1 | 129192.9 | 34.94% | 565500 | -66505 | -11.76% | 1.Site production sligthly dropping due to stuck trackers | 1.. SR087034, SR087035, SR087036
Rockbridge Baths - Small Mouth Bass | VA | 469524.7 | 389992.2 | 79532.5 | 20.39% | 563075 | -93550.3 | -16.61%

## Aug
Ecofin |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 5965001.846 | 5260076.5968 | 704925.2492 | 13.4% | 6634886.62 | -669884.774 | -10.1%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 0 | 118520.9203 | -118520.9203 | -100% | 127744.09 | -127744.09 | -100% | 1. Inverters 1 and 2 are offline for whole month. | 1. SR084949
San Luis Valley | CO | 180799.889 | 217456.442 | -36656.553 | -16.86% | 0 | 180799.889
Golden NREL 2 | CO | 12253 | 11122.6415 | 1130.3585 | 10.16% | 12547.02 | -294.02 | -2.343%
Golden NREL Wind 3 | CO | 35148.357 | 133752.56 | -98604.203 | -73.72% | 0 | 35148.357 |  | 1. There is a drop in production of 244 kW for most of days due to inverters 2 and 3 coolant systems will need to be recharged. | 1. SR087552
Pratt Solar Farm | KS | 920370 | 1086254.732 | -165884.732 | -15.27% | 1157938.67 | -237568.67 | -20.52% | 1.Inverter 2 is underperforming 550kW compared to inverter 1 for whole month. 2.Inverter 1 tripped offline at 14:45 on 8/12 back online on 8/14 3.Site offline on 8/13 back online on 8/14 | 1.SR085507 2.SR088962 3.SR088989
Rochester - 5516 Valleyhigh NW | MN | 1982363 | 2092828 | -110465 | -5.278% | 2424610 | -442247 | -18.24% | 1. inverters 37, 43, 64 and 80 are being RMA'd. 2. 20 to 30 tables were damaged due to strom(Number of modules damaged was unknown). 3. Inverter 70 is offline for whole month and Inverter 51 was tripped offline on 08/18 | 1. SR089976 2. SR087734 3. SR087934
Warsaw - 2201 Richmond | VA | 1065874.6 | 0 | 1065874.6 |  | 1095510 | -29635.4 | -2.705% | 1. Site was offline from 8/05 to 08/09 due to planned outage. | 1. SR088605
Mount Jackson - Randolf | VA | 754902.9 | 774056.9 | -19154 | -2.474% | 772430 | -17527.1 | -2.269% | 1. Inverter 24 was tripped offline on 08/06 and back online on 08/07. inverter 24 was tripped offline on 08/09 and back online on 08/10 inverter 24 was tripped offline on 08/22 and back online on 08/23 2. Inverter 9 tripped offline on 08/05 and back online on 08/06. Inverter 9 tripped offline on 08/12 and back online on 08/13 3. Site was offline from 10:00 am to 13:00 on 08/22. | 1. SR088273 2. SR086758 3. SR089311
Callands Gretna - Monroe | VA | 518537 | 312679.292 | 205857.708 | 65.84% | 515555.57 | 2981.43 | 0.5783% | 1. Inverter 2 was tripped offline on 08/03 to 08/07. 2. POA, has been having intermittent communication issue since 08/03. | 1. SR088584 2. SR088821
Rockbridge Baths - Small Mouth Bass | VA | 494753.1 | 513405.109 | -18652.009 | -3.633% | 528551.27 | -33798.17 | -6.394% | 1. inverter 17 underperforming by 28 kW for whole month. inverter 18 underperforming by 10 kW for whole month. 2. Weather station lost communication at 23:00 on 08/29. | 1. SR086325 2. SR089748

## Sep
Ecofin |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 5444485.5251 | 4820212.31 | 624273.2151 | 12.95% | 4642913.94 | 801571.5851 | 17.26%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 75483.96 | 105463.98 | -29980.02 | -28.43% | 122754.74 | -47270.78 | -38.51% | 1. Inverter 2 offline from 12:00PM at 04:35PM on 09/28. | 1. SR091350
San Luis Valley | CO | 136788.4903 | 201428.7 | -64640.2097 | -32.09% | 0 | 136788.4903 |  | 1. Meter power dropped to zero at 11:30AM on 09/06 and back to normal production on 09/07 and again meter power dropped to zero at 08:30AM on 09/14 and back to normal production on 09/15. | 1. SR090079
Golden NREL 2 | CO | 12268 | 11012.72 | 1255.28 | 11.4% | 11551.8 | 716.2 | 6.2%
Golden NREL Wind 3 | CO | 32637.9747 | 125009.2 | -92371.2253 | -73.89% | 0 | 32637.9747
Pratt Solar Farm | KS | 1028440 | 1208072 | -179632 | -14.87% | 1111425 | -82985 | -7.467% | 1. There is a drop in production of 244 kW for most of days due to inverters 2 and 3 coolant systems will need to be recharged. | 1. SR087552
Rochester - 5516 Valleyhigh NW | MN | 2097367 | 2362506 | -265139 | -11.22% | 1889971 | 207396 | 10.97% | 1. Inverters 37, 43, 64 and 80 are being RMA'd from 09/04 and back online on 09/12, inverters 39 & 50 being RMA'd from 09/12. 2. Inverter 26 and 22 offline from 09/18 and inverter 38 is offline from 09/20. 3. Inverter 38 and 74 offline from 09/20. 4. Pads 2 and 3 tripped offline on 09/29 and back online on 10/03. | 1. SR089976, SR090628 2. SR090724 3. SR091004, SR091018 4. SR091359
Warsaw - 2201 Richmond | VA | 827675.1 | 0 | 827675.1 |  | 0 | 827675.1
Mount Jackson - Randolf | VA | 573527.6 | 570400.1 | 3127.5 | 0.5483% | 632411.4 | -58883.8 | -9.311%
Callands Gretna - Monroe | VA | 366352 | 58112.41 | 308239.59 | 530.4% | 434000 | -67648 | -15.59% | 1. Weather station Hukseflux SR15-D1 - POA having intermittent communication issue from 08/03 and resolved on 09/25 | 1. SR088821
Rockbridge Baths - Small Mouth Bass | VA | 293945.4 | 178207.2 | 115738.2 | 64.95% | 440800 | -146854.6 | -33.32% | 1. Weather station stopped communicating from 08/29 and communication resolved on 09/12. 2. Inverter 1 is offline from 07:00AM to 13:00 on 09/27. | 1. SR089748 2. SR091322

## Oct
Ecofin |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 5357695.4665 | 5880342.82 | -522647.3535 | -8.888% | 4562360.76 | 795334.7065 | 17.43%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 82019 | 94256 | -12237 | -12.98% | 114635.34 | -32616.34 | -28.45% | 1. Inverter 2 is underperforming approximately 30KW and also Derating approximately 280 kW from 10/11/24. | 1. SR091992, SR092240
San Luis Valley | CO | 146489.8581 | 183047.4 | -36557.5419 | -19.97% | 0 | 146489.8581 |  | 1. Inverter 2 is offline from 08/28 and back online on 10/31. | 1. SR092200, SR089642
Golden NREL 2 | CO | 10114 | 9652.32 | 461.68 | 4.783% | 8833.82 | 1280.18 | 14.49%
Golden NREL Wind 3 | CO | 46441.4084 | 102389.4 | -55947.9916 | -54.64% | 0 | 46441.4084 |  | 1. Inverters are reporting erroneous value in the DAS | 1. SR087552
Pratt Solar Farm | KS | 1181070 | 1182093 | -1023 | -0.08654% | 1069803 | 111267 | 10.4% | 1. Inverter 2 offline from 7:00AM to 11:30AM on 10/30/24. | 1. SR092276
Rochester - 5516 Valleyhigh NW | MN | 1546872 | 1749994 | -203122 | -11.61% | 1343988 | 202884 | 15.1% | 1. Pads 2 and 3 offline from 09/29 and back online on 10/03 at 11:30 AM 2. Inverter 26 is offline from 09/18 and back online on 10/11 and Inverters 38 and 74 are offline from 09/20 and back online on 10/24 3. Inverter 51 is offline from 08/18 and back online on 10/14 at 10:45 AM and Inverter 39 is offline from 09/12 and back online on 10/14 4. Inverter 43,64 and 80 offline from 09/29 and back online at 11:00AM on 10/03. | 1. SR091359 2.SR090724, SR090628, SR091004, SR091018 3.SR090628, SR090724 4.SR089976
Warsaw - 2201 Richmond | VA | 897740.4 | 1016724 | -118983.6 | -11.7% | 723990 | 173750.4 | 24% | 1. Due to utility outage site tripped offline on 10/14 at 7:45AM and back online on 10/18 at 9:30AM | 1. SR092121
Mount Jackson - Randolf | VA | 673737.3 | 637103.8 | 36633.5 | 5.75% | 539655.6 | 134081.7 | 24.85%
Callands Gretna - Monroe | VA | 429408 | 446419.7 | -17011.7 | -3.811% | 381000 | 48408 | 12.71%
Rockbridge Baths - Small Mouth Bass | VA | 343803.5 | 458663.2 | -114859.7 | -25.04% | 380455 | -36651.5 | -9.634%

## Nov
Ecofin |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 3182745.6648 | 3410505.67 | -227760.0052 | -6.678% | 3405528.282 | -222782.6172 | -6.542%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 64146 | 77684.45 | -13538.45 | -17.43% | 97883.16 | -33737.16 | -34.47% | 1. Inverter 2 is underperforming approximately 30KW and also Derating approximately 280 kW from 10/11/24 and issue resolved on 11/28. 2. Inverter 2 tripped offline on 10/17 and back online on 11/04 | 1. SR092240 2. SR092923
San Luis Valley | CO | 132247.375 | 159537.3 | -27289.925 | -17.11% | 0 | 132247.375 |  | 1.Inverter 2 is back online at 11/18, While technician is onsite Site tripped offline at 13:48 and back online at 14:22 on 11/18 | 1.SR092200
Golden NREL 2 | CO | 6180 | 7705.97 | -1525.97 | -19.8% | 5911.522 | 268.478 | 4.542%
Golden NREL Wind 3 | CO | 43685.9898 | 70949.05 | -27263.0602 | -38.43% | 0 | 43685.9898
Pratt Solar Farm | KS | 803360 | 920153.8 | -116793.8 | -12.69% | 922234.1 | -118874.1 | -12.89% | 1.Inverter A is derating and constantly producing 1000KW from 11/20. 2.Meter 1 voltages are dropped to zero at 23:30 PM on 11/13 and back online and producing at 8:00AM on 11/14 | 1.SR093458 2.SR093234
Rochester - 5516 Valleyhigh NW | MN | 700093 | 683601.4 | 16491.6 | 2.412% | 831199.9 | -131106.9 | -15.77% | 1.Inverter 13 is tripping on and off throughout the month | 1.SR093086
Warsaw - 2201 Richmond | VA | 598833 | 643299.9 | -44466.9 | -6.912% | 585025 | 13808 | 2.36% | 1.Site was taken for planned outage 14:45 PM to 16:00 PM on 11/01 | 1.SR091092, SR091091
Mount Jackson - Randolf | VA | 393419.2 | 362629.7 | 30789.5 | 8.491% | 392444.6 | 974.6 | 0.2483% | 1.Inverter 15 is tripped offline at 15:30 PM on 11/01 and back online on 11/02 at 07:15 AM and again tripped offline at 10:30 AM on 11/16 and back online on 11/17 at 06:30 AM 2.Inverter 7 is tripped offline at 12:30PM on 11/30 and back online on 12/01 at 07:00 AM | 1.SR092889 2.SR093740
Callands Gretna - Monroe | VA | 249855 | 254876.7 | -5021.7 | -1.97% | 288000 | -38145 | -13.24%
Rockbridge Baths - Small Mouth Bass | VA | 190926.1 | 230067.4 | -39141.3 | -17.01% | 282830 | -91903.9 | -32.49%

## Dec
Ecofin |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO
San Luis Valley | CO
Golden NREL 2 | CO
Golden NREL Wind 3 | CO
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Sites
Portfolio: | Ecofin
Site DAS Name | Site | State | Update | DAS
003 - Alamosa School District | Alamosa School District | CO
002 - San Luis Valley Regional MC | San Luis Valley | CO
002 - NREL 2 | Golden NREL 2 | CO
004 - NREL Wind 3 | Golden NREL Wind 3 | CO
Kenyon Energy KS Solar | Pratt Solar Farm | KS
MN WestSide Solar | Rochester - 5516 Valleyhigh NW | MN
Hemings (VA) - ODEC | Warsaw - 2201 Richmond | VA | AEF
Randolf (VA) - ODEC | Mount Jackson - Randolf | VA | AEF
Monroe Solar (MEC) - ODEC | Callands Gretna - Monroe | VA
Smallmouth Bass (BARC) - ODEC | Rockbridge Baths - Small Mouth Bass | VA