## Year to Date
LX International America, Inc. |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1222657.16 | 1461279.0603 | -238621.9003 | -16.33% | 0 | 1222657.16 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Lake Havasu City - Police Station | AZ | 453935.88 | 653200.2864 | -199264.4064 | -30.51% | 0 | 453935.88
AZ: Lake Havasu City - Aquatic Center | AZ | 464369.5 | 553351.1678 | -88981.6678 | -16.08% | 0 | 464369.5
AZ: Lake Havasu City - City Hall | AZ | 191205.25 | 233413.6461 | -42208.3961 | -18.08% | 0 | 191205.25
AZ: Lake Havasu City - Public Works | AZ | 113146.53 | 21313.96 | 91832.57 | 430.9% | 0 | 113146.53

## 1st Qtr
LX International America, Inc. |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 258190.65 | 85311.4903 | 172879.1597 | 202.6% | 0 | 258190.65 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Lake Havasu City - Police Station | AZ | 95587.13 | 34959.8864 | 60627.2436 | 173.4% | 0 | 95587.13
AZ: Lake Havasu City - Aquatic Center | AZ | 83875 | 20606.8878 | 63268.1122 | 307% | 0 | 83875
AZ: Lake Havasu City - City Hall | AZ | 53457.25 | 27968.7161 | 25488.5339 | 91.13% | 0 | 53457.25
AZ: Lake Havasu City - Public Works | AZ | 25271.27 | 1776 | 23495.27 | 1323% | 0 | 25271.27

## 2nd Qtr
LX International America, Inc. |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 405380.09 | 709269.29 | -303889.2 | -42.85% | 0 | 405380.09 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Lake Havasu City - Police Station | AZ | 144342 | 322778.91 | -178436.91 | -55.28% | 0 | 144342
AZ: Lake Havasu City - Aquatic Center | AZ | 162858.5 | 279326.35 | -116467.85 | -41.7% | 0 | 162858.5
AZ: Lake Havasu City - City Hall | AZ | 59647.75 | 107062.59 | -47414.84 | -44.29% | 0 | 59647.75
AZ: Lake Havasu City - Public Works | AZ | 38531.84 | 101.44 | 38430.4 | 37885% | 0 | 38531.84

## 3rd Qtr
LX International America, Inc. |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 366467.22 | 562529 | -196061.78 | -34.85% | 0 | 366467.22 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Lake Havasu City - Police Station | AZ | 130588.75 | 256239 | -125650.25 | -49.04% | 0 | 130588.75
AZ: Lake Havasu City - Aquatic Center | AZ | 148533 | 220141 | -71608 | -32.53% | 0 | 148533
AZ: Lake Havasu City - City Hall | AZ | 53856.75 | 86148 | -32291.25 | -37.48% | 0 | 53856.75
AZ: Lake Havasu City - Public Works | AZ | 33488.72 | 1 | 33487.72 | 3348772% | 0 | 33488.72

## 4th Qtr
LX International America, Inc. |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 192619.2 | 104169.28 | 88449.92 | 84.91% | 0 | 192619.2 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Lake Havasu City - Police Station | AZ | 83418 | 39222.49 | 44195.51 | 112.7% | 0 | 83418
AZ: Lake Havasu City - Aquatic Center | AZ | 69103 | 33276.93 | 35826.07 | 107.7% | 0 | 69103
AZ: Lake Havasu City - City Hall | AZ | 24243.5 | 12234.34 | 12009.16 | 98.16% | 0 | 24243.5
AZ: Lake Havasu City - Public Works | AZ | 15854.7 | 19435.52 | -3580.82 | -18.42% | 0 | 15854.7

## Jan
LX International America, Inc. |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 67928.5 | 6873 | 61055.5 | 888.3% | 0 | 67928.5 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 23850 | 2839 | 21011 | 740.1% | 0 | 23850 | 0% | 1. Weather station reporting erroneous values from 09/19/2023, due to that expected energy values are too low. | 1. SR071003
AZ: Lake Havasu City - Aquatic Center | AZ | 27794.5 | 2447 | 25347.5 | 1036% | 0 | 27794.5 | 0% | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too low | 1. SR071003
AZ: Lake Havasu City - City Hall | AZ | 9540 | 930 | 8610 | 925.8% | 0 | 9540 | 0% | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too low | 1. SR071003
AZ: Lake Havasu City - Public Works | AZ | 6744 | 657 | 6087 | 926.5% | 0 | 6744 | 0% | 1. The current weather station is analog and the current reporting is digital they do not match the weather station would need to be replaced to work correctly | 1. SR067178

## Feb
LX International America, Inc. |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 78555 | 50964 | 27591 | 54.14% | 0 | 78555 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 32012 | 19847 | 12165 | 61.29% | 0 | 32012 |  | 1. Weather station reporting erroneous values from 09/19/2023, due to that expected energy values are too low. 2. Inverter 3 is offline | 1. SR071003 2. SR081340
AZ: Lake Havasu City - Aquatic Center | AZ | 11202 | 7563 | 3639 | 48.12% | 0 | 11202 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too low. | 1. SR071003
AZ: Lake Havasu City - City Hall | AZ | 27630 | 22995 | 4635 | 20.16% | 0 | 27630 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too low. | 1. SR071003
AZ: Lake Havasu City - Public Works | AZ | 7711 | 559 | 7152 | 1279% | 0 | 7711 |  | 1. The current weather station is analog and the current reporting is digital they do not match the weather station would need to be replaced to work correctly | 1. SR067178

## Mar
LX International America, Inc. |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 111707.15 | 27474.4903 | 84232.6597 | 306.6% | 0 | 111707.15 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 39725.13 | 12273.8864 | 27451.2436 | 223.7% | 0 | 39725.13 |  | 1. Weather station reporting erroneous values from 09/19/2023, due to that expected energy values are too low. 2. Inverter 3 is offline | 1. SR071003 2. SR081340
AZ: Lake Havasu City - Aquatic Center | AZ | 44878.5 | 10596.8878 | 34281.6122 | 323.5% | 0 | 44878.5 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too low. | 1. SR071003
AZ: Lake Havasu City - City Hall | AZ | 16287.25 | 4043.7161 | 12243.5339 | 302.8% | 0 | 16287.25 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too low. | 1. SR071003
AZ: Lake Havasu City - Public Works | AZ | 10816.27 | 560 | 10256.27 | 1831% | 0 | 10816.27 |  | 1. The current weather station is analog and the current reporting is digital they do not match the weather station would need to be replaced to work correctly | 1. SR067178

## Apr
LX International America, Inc. |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 130413.03 | 217957.05 | -87544.02 | -40.17% | 0 | 130413.03 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 46701.5 | 99177.37 | -52475.87 | -52.91% | 0 | 46701.5 |  | 1. Weather station reporting erroneous values throughout the month, due to that expected energy values are too high. 2. Inverter 3 is offline | 1. SR071003 2. SR081340
AZ: Lake Havasu City - Aquatic Center | AZ | 51881.5 | 85809.38 | -33927.88 | -39.54% | 0 | 51881.5 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - City Hall | AZ | 19242.75 | 32875.86 | -13633.11 | -41.47% | 0 | 19242.75 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - Public Works | AZ | 12587.28 | 94.44 | 12492.84 | 13228% | 0 | 12587.28 |  | 1. The current weather station is analog and the current reporting is digital they do not match the weather station would need to be replaced to work correctly | 1. SR067178

## May
LX International America, Inc. |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 141493 | 235615 | -94122 | -39.95% | 0 | 141493 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 50781 | 107267 | -56486 | -52.66% | 0 | 50781 |  | 1. Weather station reporting erroneous values throughout the month, due to that expected energy values are too high. 2. Inverter 3 is offline | 1. SR071003 2. SR081340
AZ: Lake Havasu City - Aquatic Center | AZ | 56251 | 92798 | -36547 | -39.38% | 0 | 56251 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - City Hall | AZ | 21077 | 35543 | -14466 | -40.7% | 0 | 21077 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - Public Works | AZ | 13384 | 7 | 13377 | 191100% | 0 | 13384 |  | 1. The current weather station is analog and the current reporting is digital they do not match the weather station would need to be replaced to work correctly | 1. SR067178

## Jun
LX International America, Inc. |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 133474.06 | 255697.24 | -122223.18 | -47.8% | 0 | 133474.06 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 46859.5 | 116334.54 | -69475.04 | -59.72% | 0 | 46859.5 |  | 1. Weather station reporting erroneous values throughout the month, due to that expected energy values are too high. 2. Inverter 3 is offline | 1. SR071003 2. SR081340
AZ: Lake Havasu City - Aquatic Center | AZ | 54726 | 100718.97 | -45992.97 | -45.66% | 0 | 54726 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - City Hall | AZ | 19328 | 38643.73 | -19315.73 | -49.98% | 0 | 19328 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - Public Works | AZ | 12560.56 | 0 | 12560.56 |  | 0 | 12560.56 |  | 1. The current weather station is analog and the current reporting is digital they do not match the weather station would need to be replaced to work correctly | 1. SR067178

## Jul
LX International America, Inc. |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 131670.22 | 261135 | -129464.78 | -49.58% | 0 | 131670.22 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 46849.75 | 118817 | -71967.25 | -60.57% | 0 | 46849.75 |  | 1. Weather station reporting erroneous values throughout the month, due to that expected energy values are too high. 2. Inverter 3 is offline | 1. SR071003 2. SR081340
AZ: Lake Havasu City - Aquatic Center | AZ | 53557 | 102861 | -49304 | -47.93% | 0 | 53557 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - City Hall | AZ | 19060.75 | 39457 | -20396.25 | -51.69% | 0 | 19060.75 |  | 1. Weather station data is virtually taken from the LHC Police station, resulting in expected energy values that are too high. | 1. SR071003
AZ: Lake Havasu City - Public Works | AZ | 12202.72 | 0 | 12202.72 |  | 0 | 12202.72 |  | 1. Weather station is reporting 0 irradiance for whole month. | 1. SR087716

## Aug
LX International America, Inc. |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 122090 | 183699 | -61609 | -33.54% | 0 | 122090 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 43768 | 82274 | -38506 | -46.8% | 0 | 43768 |  | 1. Inverter 3 is offline | 1. SR081340
AZ: Lake Havasu City - Aquatic Center | AZ | 49693 | 70497 | -20804 | -29.51% | 0 | 49693
AZ: Lake Havasu City - City Hall | AZ | 17598 | 30928 | -13330 | -43.1% | 0 | 17598
AZ: Lake Havasu City - Public Works | AZ | 11031 | 0 | 11031 |  | 0 | 11031 |  | 1. Weather station is reporting 0 irradiance for whole month. | 1. SR087716

## Sep
LX International America, Inc. |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 112707 | 117695 | -4988 | -4.238% | 0 | 112707 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 39971 | 55148 | -15177 | -27.52% | 0 | 39971 |  | 1. Inverter 3 is offline | 1. SR081340, SR086335
AZ: Lake Havasu City - Aquatic Center | AZ | 45283 | 46783 | -1500 | -3.206% | 0 | 45283
AZ: Lake Havasu City - City Hall | AZ | 17198 | 15763 | 1435 | 9.104% | 0 | 17198
AZ: Lake Havasu City - Public Works | AZ | 10255 | 1 | 10254 | 1025400% | 0 | 10255 |  | 1. Weather station is reporting 0 irradiance. Weather station being RMA'd. | 1. SR087716

## Oct
LX International America, Inc. |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 107349.41 | 94962.77 | 12386.64 | 13.04% | 0 | 107349.41 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 46260.75 | 38844.56 | 7416.19 | 19.09% | 0 | 46260.75 |  | 1. Weather station reporting erroneous values from 10/29 throughout the day | 1. SR092908
AZ: Lake Havasu City - Aquatic Center | AZ | 38520 | 32956.35 | 5563.65 | 16.88% | 0 | 38520 |  | 1. Weather station reporting erroneous values from 10/29 throughout the day | 1. SR092908
AZ: Lake Havasu City - City Hall | AZ | 13676.5 | 12116.49 | 1560.01 | 12.88% | 0 | 13676.5 |  | 1. Weather station reporting erroneous values from 10/29 throughout the day | 1. SR092908
AZ: Lake Havasu City - Public Works | AZ | 8892.16 | 11045.37 | -2153.21 | -19.49% | 0 | 8892.16 |  | 1. Weather station was replaced on 10/3 | 1. SR087716

## Nov
LX International America, Inc. |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 85269.79 | 9206.51 | 76063.28 | 826.2% | 0 | 85269.79 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ | 37157.25 | 377.93 | 36779.32 | 9732% | 0 | 37157.25 |  | 1. The weather station has been reporting erroneous values since 10/29 throughout the day, causing the expected energy values to be too low. | 1. SR092908
AZ: Lake Havasu City - Aquatic Center | AZ | 30583 | 320.58 | 30262.42 | 9440% | 0 | 30583 |  | 1. The weather station has been reporting erroneous values since 10/29 throughout the day, causing the expected energy values to be too low. | 1.SR092908
AZ: Lake Havasu City - City Hall | AZ | 10567 | 117.85 | 10449.15 | 8866% | 0 | 10567 |  | 1. The weather station has been reporting erroneous values since 10/29 throughout the day, causing the expected energy values to be too low. | 1. SR092908
AZ: Lake Havasu City - Public Works | AZ | 6962.54 | 8390.15 | -1427.61 | -17.02% | 0 | 6962.54

## Dec
LX International America, Inc. |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Lake Havasu City - Police Station | AZ
AZ: Lake Havasu City - Aquatic Center | AZ
AZ: Lake Havasu City - City Hall | AZ
AZ: Lake Havasu City - Public Works | AZ

## Sites
Portfolio: | LX International America, Inc.
Site DAS Name | Site | State | Update | DAS
AZ: Lake Havasu City - Police Station | AZ: Lake Havasu City - Police Station | AZ
AZ: Lake Havasu City - Aquatic Center | AZ: Lake Havasu City - Aquatic Center | AZ
AZ: Lake Havasu City - City Hall | AZ: Lake Havasu City - City Hall | AZ
AZ: Lake Havasu City - Public Works | AZ: Lake Havasu City - Public Works | AZ