## Year to Date
Agilitas Energy |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 4674498.8208 | 4052534.931 | 621963.8898 | 15.35% | 7355219.7 | -2680720.8792 | -36.45%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 750320.8421 | 768828.39 | -18507.5479 | -2.407% | 740292.48 | 10028.3621 | 1.355%
Auburn - Leicester Street Solar | MA | 1481682.6667 | 1323328.587 | 158354.0797 | 11.97% | 0 | 1481682.6667
Rochester - Old Middleboro | MA | 2134633.312 | 1960377.954 | 174255.358 | 8.889% | 6614927.22 | 585028.852 | 8.844%
Dover - Littleworth Road | NH | 76761 | 0 | 76761 |  | 0 | 76761
Milton - Landfill | NH | 231101 | 0 | 231101 |  | 0 | 231101
Hopkinton - 71 Frankland Rd | MA

## 1st Qtr
Agilitas Energy |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 4081355.2197 | 3449243.358 | 632111.8617 | 18.33% | 1712996.49 | 2368358.7297 | 138.3%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 157177.241 | 165536.817 | -8359.576 | -5.05% | 163392.03 | -6214.789 | -3.804%
Auburn - Leicester Street Solar | MA | 1481682.6667 | 1323328.587 | 158354.0797 | 11.97% | 0 | 1481682.6667
Rochester - Old Middleboro | MA | 2134633.312 | 1960377.954 | 174255.358 | 8.889% | 1549604.46 | 585028.852 | 37.75%
Dover - Littleworth Road | NH | 76761 | 0 | 76761 |  | 0 | 76761
Milton - Landfill | NH | 231101 | 0 | 231101 |  | 0 | 231101
Hopkinton - 71 Frankland Rd | MA

## 2nd Qtr
Agilitas Energy |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 7162125.6251 | 6142431.22 | 1019694.4051 | 16.6% | 2544607.86 | 4617517.7651 | 181.5%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 265030.1976 | 268035.72 | -3005.5224 | -1.121% | 257263.74 | 7766.4576 | 3.019%
Auburn - Leicester Street Solar | MA | 2706720 | 2809460.8 | -102740.8 | -3.657% | 0 | 2706720
Rochester - Old Middleboro | MA | 3706056.4275 | 3064934.7 | 641121.7275 | 20.92% | 2287344.12 | 1418712.3075 | 62.02%
Dover - Littleworth Road | NH | 128040 | 0 | 128040 |  | 0 | 128040
Milton - Landfill | NH | 356279 | 0 | 356279 |  | 0 | 356279
Hopkinton - 71 Frankland Rd | MA

## 3rd Qtr
Agilitas Energy |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 6887197.4569 | 16025020.22 | -9137822.7631 | -57.02% | 3178729.29 | 3708468.1669 | 116.7%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 257834.216 | 262970.243 | -5136.027 | -1.953% | 259322.45 | -1488.234 | -0.5739%
Auburn - Leicester Street Solar | MA | 2654465.4 | 2846908.602 | -192443.202 | -6.76% | 0 | 2654465.4
Rochester - Old Middleboro | MA | 3015377.8409 | 12250861.975 | -9235484.1341 | -75.39% | 2237487.14 | 777890.7009 | 34.77%
Dover - Littleworth Road | NH | 127938 | 0 | 127938 |  | 0 | 127938
Milton - Landfill | NH | 379901 | 0 | 379901 |  | 0 | 379901
Hopkinton - 71 Frankland Rd | MA | 451681 | 664279.4 | -212598.4 | -32% | 681919.7 | -230238.7 | -33.76%

## 4th Qtr
Agilitas Energy |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 2565717.6786 | 2549580.21 | 16137.4686 | 0.6329% | 1101543.76 | 1464173.9186 | 132.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rowley - Central Street Solar | MA | 70279.1875 | 72285.61 | -2006.4225 | -2.776% | 60314.26 | 9964.9275 | 16.52%
Auburn - Leicester Street Solar | MA | 776008 | 1001527 | -225519 | -22.52% | 0 | 776008
Rochester - Old Middleboro | MA | 1059803.4911 | 892672 | 167131.4911 | 18.72% | 540491.5 | 519311.9911 | 96.08%
Dover - Littleworth Road | NH | 36138 | 0 | 36138 |  | 0 | 36138
Milton - Landfill | NH | 107854 | 0 | 107854 |  | 0 | 107854
Hopkinton - 71 Frankland Rd | MA | 515635 | 583095.6 | -67460.6 | -11.57% | 500738 | 14897 | 2.975%

## Jan
Agilitas Energy |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 643797.6434 | 502858.5 | 140939.1434 | 28.03% | 459223.17 | 184574.4734 | 40.19% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 23660.31 | 29500.5 | -5840.19 | -19.8% | 37551.17 | -13890.86 | -36.99%
Auburn - Leicester Street Solar | MA | 172284.3333 | 0 | 172284.3333 |  | 0 | 172284.3333 |  | 1. Site was offline on 01/07 at 10:00AM and later back online on 01/08 at 15:30. 2. Site tripped offline on 01/22 at 10:15AM and later back online on 01/25 at 15:45. 3. Inverters 28, 29 & 39 are offline from 01/26 and later back online on 01/31 at 14:45. | 1. SR080001 2. SR080133 3. SR080577
Rochester - Old Middleboro | MA | 406951 | 473358 | -66407 | -14.03% | 421672 | -14721 | -3.491% | 1. Site was offline on 01/13 from 06:15 to 11:30 . 2. Site was offline from 01/14 at 11:00 to 01/15 at 15:00. | 1. SR080191 2. SR080222
Dover - Littleworth Road | NH | 10197 | 0 | 10197 |  | 0 | 10197
Milton - Landfill | NH | 30705 | 0 | 30705 |  | 0 | 30705
Hopkinton - 71 Frankland Rd | MA

## Feb
Agilitas Energy |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 1572309.9733 | 1222939.16 | 349370.8133 | 28.57% | 544279.56 | 1028030.4133 | 188.9% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 65179.64 | 66094.16 | -914.52 | -1.384% | 53397.96 | 11781.68 | 22.06%
Auburn - Leicester Street Solar | MA | 610539.3333 | 467792.3 | 142747.0333 | 30.52% | 0 | 610539.3333
Rochester - Old Middleboro | MA | 761805 | 689052.7 | 72752.3 | 10.56% | 490881.6 | 270923.4 | 55.19% | 1. Site relay tripped open at 15:00 on 02/29 and back online next day. | 1. SR081475
Dover - Littleworth Road | NH | 33324 | 0 | 33324 |  | 0 | 33324
Milton - Landfill | NH | 101462 | 0 | 101462 |  | 0 | 101462 |  | 1. Inverter 11 tripped offline twice this month and self-resolved itself each time. | 1. SR081067
Hopkinton - 71 Frankland Rd | MA

## Mar
Agilitas Energy |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 1865247.603 | 1723445.698 | 141801.905 | 8.228% | 709493.76 | 1155753.843 | 162.9% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 68337.291 | 69942.157 | -1604.866 | -2.295% | 72442.9 | -4105.609 | -5.667%
Auburn - Leicester Street Solar | MA | 698859 | 855536.287 | -156677.287 | -18.31% | 0 | 698859 |  | 1. inverters 13, 14, 15 are offline on 03/22 and back online at 16:15 on 03/22. 2. Inverters 7, 8, and 9 tripped offline on an AC disconnected fault at 16:15 on 03/25 and back online at 16:30 on 03/25. | 1. SR082379 2. SR082723
Rochester - Old Middleboro | MA | 965877.312 | 797967.254 | 167910.058 | 21.04% | 637050.86 | 328826.452 | 51.62%
Dover - Littleworth Road | NH | 33240 | 0 | 33240 |  | 0 | 33240 |  | 1. Site has not started on 03/24 and has started on 10:45am on 03/24. | 1. SR082614
Milton - Landfill | NH | 98934 | 0 | 98934 |  | 0 | 98934 |  | 1. Inverter 11 tripped offline at 10:00am on 03/21 and back online on 03/22 2. Inverter 22 is offline on 03/24 and back online on 03/25. | 1. SR082351 2. SR082691
Hopkinton - 71 Frankland Rd | MA

## Apr
Agilitas Energy |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 2086903.6251 | 1814581.3 | 272322.3251 | 15.01% | 780206.34 | 1306697.2851 | 167.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 79228.3976 | 79840.2 | -611.8024 | -0.7663% | 82261.44 | -3033.0424 | -3.687%
Auburn - Leicester Street Solar | MA | 806444 | 847614.4 | -41170.4 | -4.857% | 0 | 806444
Rochester - Old Middleboro | MA | 1051496.2275 | 887126.7 | 164369.5275 | 18.53% | 697944.9 | 353551.3275 | 50.66% | 1. Inverter 1 tripped offline on 04/28 at 07:00 and back online on 04/29 at 07:00 and again tripped offline at 14:00 on 04/29 and back online on 04/30, again inverter tripped offline at 18:00 on 04/30 | 1. SR083899
Dover - Littleworth Road | NH | 39653 | 0 | 39653 |  | 0 | 39653
Milton - Landfill | NH | 110082 | 0 | 110082 |  | 0 | 110082 |  | 1. Inverter 12 tripped offline on 04/02 at 01:35 PM and back online on 04/03 at 12:00 PM. 2. Site tripped offline on 04/04 at 09:15 and back online on 04/06 at 08:20 AM. Inverters 11 and 22 are offline after site re-energized and back online on 04/07. 3. Inverter 21 is derating by 5kW during peak hours from 04/25 | 1. SR083024 2. SR083071 3. SR083818
Hopkinton - 71 Frankland Rd | MA

## May
Agilitas Energy |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 2378796 | 2044259.92 | 334536.08 | 16.36% | 881066.6 | 1497729.4 | 170% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 90222.8 | 90753.52 | -530.72 | -0.5848% | 88730.3 | 1492.5 | 1.682% | 1. Inverter 13 is overheating on high irradiance days and is about 7 kW down for multiple days. | 1. SR085127
Auburn - Leicester Street Solar | MA | 891783 | 932322.4 | -40539.4 | -4.348% | 0 | 891783
Rochester - Old Middleboro | MA | 1235742.2 | 1021184 | 214558.2 | 21.01% | 792336.3 | 443405.9 | 55.96%
Dover - Littleworth Road | NH | 42525 | 0 | 42525 |  | 0 | 42525
Milton - Landfill | NH | 118523 | 0 | 118523 |  | 0 | 118523 |  | 1. Inverter 21 is derating by 5kW during peak hours from 04/25 2. Inverter 5 is derating by 8kW during peak hours from 05/21 | 1. SR083818 2. SR084975
Hopkinton - 71 Frankland Rd | MA

## Jun
Agilitas Energy |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 2696426 | 2283590 | 412836 | 18.08% | 883334.92 | 1813091.08 | 205.3% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 95579 | 97442 | -1863 | -1.912% | 86272 | 9307 | 10.79% | 1. Inverter 13 is derating due to overheating on sunny days. Issue occurred throughout the month | 1. SR085127
Auburn - Leicester Street Solar | MA | 1008493 | 1029524 | -21031 | -2.043% | 0 | 1008493 |  | 1. Site tripped offline at 19:50 on 06/19 and back online at 10:45 on 06/20 | 1. SR086453
Rochester - Old Middleboro | MA | 1418818 | 1156624 | 262194 | 22.67% | 797062.92 | 621755.08 | 78.01%
Dover - Littleworth Road | NH | 45862 | 0 | 45862 |  | 0 | 45862
Milton - Landfill | NH | 127674 | 0 | 127674 |  | 0 | 127674 |  | 1. Inverter 21 is derating by 5kW during peak hours from 04/25 throughout the month 2. Inverter 5 is derating by 8kW during peak hours from 05/21 throughout the month | 1. SR083818 2. SR084975
Hopkinton - 71 Frankland Rd | MA

## Jul
Agilitas Energy |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 2397003.742 | 11418182.1 | -9021178.358 | -79.01% | 903589.68 | 1493414.062 | 165.3% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 93398.466 | 95319.723 | -1921.257 | -2.016% | 92363.64 | 1034.826 | 1.12%
Auburn - Leicester Street Solar | MA | 964199.4 | 991770.102 | -27570.702 | -2.78% | 0 | 964199.4 |  | 1. Inverters 25, 26 and 27 are offline on 07/05 and back online on 07/08 at 10:15 AM 2. Site tripped offline at 17:30 on 07/23 and back online on 07/24 at 06:00 AM | 1. SR087391 2. SR088075
Rochester - Old Middleboro | MA | 1152335.876 | 10331092.275 | -9178756.399 | -88.85% | 811226.04 | 341109.836 | 42.05% | 1. Inverter 1 stopped communicating, as per meter offline on 07/11 at 13:00 and back online on 07/12 at 08:30 AM 2. Inverter 2 tripped offline at 15:15 on 07/11 and back online on 07/12 at 13:00 again tripped offline on 07/14 at 10:00 AM, back online on 07/15 at 07:30 AM Inverter 2 tripped offline at 17:30 on 07/18 and back online on 07/19 at 07:45 3. Inverter 1 tripped offline at 13:00 on 07/22 and back online on 07/24 at 12:15 4. Inverter 2 and 3 are offline on 07/23 and back online on 07/24 | 1. SR087558 2. SR087558, SR087578 3. SR087988, SR087990 4. SR088071
Dover - Littleworth Road | NH | 47158 | 0 | 47158 |  | 0 | 47158
Milton - Landfill | NH | 139912 | 0 | 139912 |  | 0 | 139912
Hopkinton - 71 Frankland Rd | MA

## Aug
Agilitas Energy |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 2174088.2834 | 2112723.49 | 61364.7934 | 2.905% | 851867.88 | 1322220.4034 | 155.2% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 86826.8425 | 88596.39 | -1769.5475 | -1.997% | 89067.58 | -2240.7375 | -2.516% | 1. Inverter 9 tripped offline at 11:30AM and later stopped communication at 13:30 on 8/10 and back online on 8/11 | 1. SR088882
Auburn - Leicester Street Solar | MA | 905688 | 964745.1 | -59057.1 | -6.122% | 0 | 905688 |  | 1.Inverter 1,2,3 tripped offline at 14:30 on 8/7 back online on 8/8 | 1.SR088748
Rochester - Old Middleboro | MA | 1019650.4409 | 1059382 | -39731.5591 | -3.75% | 762800.3 | 256850.1409 | 33.67% | 1.Inverter 2 having multiple trippings through out the month 2.Inverter 1 tripped offline at 15:45pm on 8/18 and back online on 8/19 at 13:00 again inverter 1 offline on 8/24 back online on 8/26 | 1. SR088490 2.SR089238
Dover - Littleworth Road | NH | 40390 | 0 | 40390 |  | 0 | 40390 |  | 1. Inverter 5 is under-performing vs its peers (about 15 amps lower). Possibly fan issue. | 1. SR089574
Milton - Landfill | NH | 121533 | 0 | 121533 |  | 0 | 121533 |  | 1. Inverter 2 is offline on 8/10 and back online on 8/11 at 02:00PM 2. Inverter 13 is offline on 8/26 back online on 8/27 and again inverter offline on 8/30 back online on 8/31 | 1.SR088890 2. SR089571
Hopkinton - 71 Frankland Rd | MA

## Sep
Agilitas Energy |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 2316105.4315 | 2494114.63 | -178009.1985 | -7.137% | 1423271.73 | 892833.7015 | 62.73%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 77608.9075 | 79054.13 | -1445.2225 | -1.828% | 77891.23 | -282.3225 | -0.3625%
Auburn - Leicester Street Solar | MA | 784578 | 890393.4 | -105815.4 | -11.88% | 0 | 784578 |  | 1.Inverters 1, 2 and 3 tripped offline on 09/24 at 12":30 and back online on 09/26 at 09:30 | 1.SR091142
Rochester - Old Middleboro | MA | 843391.524 | 860387.7 | -16996.176 | -1.975% | 663460.8 | 179930.724 | 27.12% | 1.Inverter 1 is offline at 01:45 on 09/07 and back online at 17:30 on 09/13 | 1.SR089238
Dover - Littleworth Road | NH | 40390 | 0 | 40390 |  | 0 | 40390
Milton - Landfill | NH | 118456 | 0 | 118456 |  | 0 | 118456
Hopkinton - 71 Frankland Rd | MA | 451681 | 664279.4 | -212598.4 | -32% | 681919.7 | -230238.7 | -33.76%

## Oct
Agilitas Energy |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 2565717.6786 | 2549580.21 | 16137.4686 | 0.6329% | 1101543.76 | 1464173.9186 | 132.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA | 70279.1875 | 72285.61 | -2006.4225 | -2.776% | 60314.26 | 9964.9275 | 16.52% | 1. Inverter 9 being RMA'D since 08/10/2024. 2. Due to technician dispatch, Site offline from 8:30AM to 9:40AM on 10/09/2024. 3. Inverter 13 RMA'D from 09/06 and Inverter 3 is being RMA'D from 09/27. | 1. SR088882 2. PM4489 3.SR085127,SR090147,SR090151,SR093008
Auburn - Leicester Street Solar | MA | 776008 | 1001527 | -225519 | -22.52% | 0 | 776008 |  | 1. Inverters 4,5,6 tripped offline at 10:15AM on 10/13/2024 and back online on 10/14/2024 again offline from 08:45AM to 16:00 on 10/18/2024 and pad 2 is offline from 08:45AM to 11:45AM on 10/15 2. DC meter 10 is not capturing correct values. | 1. SR092116 2. SR091730,SR091878
Rochester - Old Middleboro | MA | 1059803.4911 | 892672 | 167131.4911 | 18.72% | 540491.5 | 519311.9911 | 96.08%
Dover - Littleworth Road | NH | 36138 | 0 | 36138 |  | 0 | 36138
Milton - Landfill | NH | 107854 | 0 | 107854 |  | 0 | 107854 |  | 1. Inverter 13 was offline on 10/01, 10/27, 10/29/2024. | 1. SR091590, SR092635
Hopkinton - 71 Frankland Rd | MA | 515635 | 583095.6 | -67460.6 | -11.57% | 500738 | 14897 | 2.975% | 1. Inverter 28 tripped offline at 11:15 on 10/18 and back online on 10/19. 2. Site is offline at 12:00 on 10/27 and back online at 13:30 on 10/28 3. The production meter energy data has been reporting negative values since 11:45 on 09/27. Note : We have taken the actual data into postive values | 1. SR092302 2. SR092633 3. SR093220

## Nov
Agilitas Energy |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA
Auburn - Leicester Street Solar | MA
Rochester - Old Middleboro | MA
Dover - Littleworth Road | NH
Milton - Landfill | NH
Hopkinton - 71 Frankland Rd | MA

## Dec
Agilitas Energy |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rowley - Central Street Solar | MA
Auburn - Leicester Street Solar | MA
Rochester - Old Middleboro | MA
Dover - Littleworth Road | NH
Milton - Landfill | NH
Hopkinton - 71 Frankland Rd | MA

## Sites
Portfolio: | Agilitas Energy
Site DAS Name | Site | State | Update | DAS
Central Street Solar, Rowley | Rowley - Central Street Solar | MA | AEF | PowerTrack
Leicester Street Solar: DAS + BESS | Auburn - Leicester Street Solar | MA | AEF | PowerTrack
Middleboro Road | Rochester - Old Middleboro | MA | AEF | PowerTrack
Littleworth Road Solar | Dover - Littleworth Road | NH |  | SolrenView
Milton Municipal Landfill | Milton - Landfill | NH |  | SolrenView
Frankland Solar | Hopkinton - 71 Frankland Rd | MA | AEF | PowerTrack