## Year to Date
Catalyze |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 6678604.289 | 8175994.59 | -1497390.301 | -18.31% | 44407294.033 | -37728689.744 | -84.96%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 947661.7547 | 998037.387 | -50375.6323 | -5.047% | 1055720.123 | -108058.3683 | -10.24%
Adelanto - 1 Sheep Creek Road | CA | 698121 | 899827.54 | -201706.54 | -22.42% | 8060978.31 | -1198363.45 | -14.87%
Blackstone - 83 Federal Street | MA | 1021429 | 1250983.5 | -229554.5 | -18.35% | 7041742 | -471279.3 | -6.693%
Charlton - 299 Worcester Road | MA | 106387.5 | 122897.92 | -16510.42 | -13.43% | 568227.83 | -17768.79 | -3.127%
Wareham - 8 Thatcher Drive | MA | 26732.625 | 32689.431 | -5956.806 | -18.22% | 164921.399 | -9322.204 | -5.653%
West Yarmouth - 42 Mid Tech | MA | 21092.2942 | 26594.646 | -5502.3518 | -20.69% | 159316.751 | -6768.8868 | -4.249%
Harrison - 130 Union Street | NY | 38110 | 49114.896 | -11004.896 | -22.41% | 235994.91 | -8334.25 | -3.532%
Staten Island - Ellis Storage | NY | 90871.75 | 116168.46 | -25296.71 | -21.78% | 540557.27 | -11927.27 | -2.206%
Amherst - 595 Scholles Road | NY | 1004650 | 1305937.17 | -301287.17 | -23.07% | 8647380.1 | -509052 | -5.887%
Lancaster 1 - Gunnville Road | NY | 993680 | 1203596.5 | -209916.5 | -17.44% | 6584963.71 | -32020 | -0.4863%
Lancaster 2 - Shisler Road | NY | 951657 | 1317386.2 | -365729.2 | -27.76% | 7212870.38 | -167958.1 | -2.329%
Fullerton - 200 W Orangethorpe | CA | 228387.8652 | 237208.44 | -8820.5748 | -3.718% | 1169843.67 | -40178.8048 | -3.435%
El Paso - 10500 Railroad Drive | TX | 302499.25 | 350397.5 | -47898.25 | -13.67% | 1359218.67 | -28355.72 | -2.086%
Friona - 900 Millard Ave | TX | 247324.25 | 265155 | -17830.75 | -6.725% | 1158534.08 | -10606.32 | -0.9155%
Augusta - 13 York Farm Road | ME | 0 | 0 | 0 |  | 309800.5 | 0 | 0%
Santa Ana - 1441 West | CA | 0 | 0 | 0 |  | 137224.33 | 0 | 0%
Jessup -7950 Oceano Ave | MD

## 1st Qtr
Catalyze |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 5923301.1 | 7368149.323 | -1444848.223 | -19.61% | 8460490.51 | -2537189.41 | -29.99%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 192358.5656 | 190192.12 | 2166.4456 | 1.139% | 217612.88 | -25254.3144 | -11.61%
Adelanto - 1 Sheep Creek Road | CA | 698121 | 899827.54 | -201706.54 | -22.42% | 1896484.45 | -1198363.45 | -63.19%
Blackstone - 83 Federal Street | MA | 1021429 | 1250983.5 | -229554.5 | -18.35% | 1492708.3 | -471279.3 | -31.57%
Charlton - 299 Worcester Road | MA | 106387.5 | 122897.92 | -16510.42 | -13.43% | 124156.29 | -17768.79 | -14.31%
Wareham - 8 Thatcher Drive | MA | 26732.625 | 32689.431 | -5956.806 | -18.22% | 36054.829 | -9322.204 | -25.86%
West Yarmouth - 42 Mid Tech | MA | 21092.2942 | 26594.646 | -5502.3518 | -20.69% | 27861.181 | -6768.8868 | -24.3%
Harrison - 130 Union Street | NY | 38110 | 49114.896 | -11004.896 | -22.41% | 46444.25 | -8334.25 | -17.94%
Staten Island - Ellis Storage | NY | 90871.75 | 116168.46 | -25296.71 | -21.78% | 102799.02 | -11927.27 | -11.6%
Amherst - 595 Scholles Road | NY | 1004650 | 1305937.17 | -301287.17 | -23.07% | 1513702 | -509052 | -33.63%
Lancaster 1 - Gunnville Road | NY | 993680 | 1203596.5 | -209916.5 | -17.44% | 1025700 | -32020 | -3.122%
Lancaster 2 - Shisler Road | NY | 951657 | 1317386.2 | -365729.2 | -27.76% | 1119615.1 | -167958.1 | -15%
Fullerton - 200 W Orangethorpe | CA | 228387.8652 | 237208.44 | -8820.5748 | -3.718% | 268566.67 | -40178.8048 | -14.96%
El Paso - 10500 Railroad Drive | TX | 302499.25 | 350397.5 | -47898.25 | -13.67% | 330854.97 | -28355.72 | -8.57%
Friona - 900 Millard Ave | TX | 247324.25 | 265155 | -17830.75 | -6.725% | 257930.57 | -10606.32 | -4.112%
Augusta - 13 York Farm Road | ME | 0 | 0 | 0 |  | 0 | 0
Santa Ana - 1441 West | CA | 0 | 0 | 0 |  | 0 | 0
Jessup -7950 Oceano Ave | MD

## 2nd Qtr
Catalyze |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 12687067.2893 | 13892911.39 | -1205844.1007 | -8.68% | 16400042.04 | -3712974.7507 | -22.64%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 362194.6219 | 382377.8 | -20183.1781 | -5.278% | 392007.1 | -29812.4781 | -7.605%
Adelanto - 1 Sheep Creek Road | CA | 1292585 | 1527342 | -234757 | -15.37% | 2950734 | -1658149 | -56.19%
Blackstone - 83 Federal Street | MA | 2014135 | 2344243.4 | -330108.4 | -14.08% | 2445554.4 | -431419.4 | -17.64%
Charlton - 299 Worcester Road | MA | 189047.25 | 198845.99 | -9798.74 | -4.928% | 206105.8 | -17058.55 | -8.277%
Wareham - 8 Thatcher Drive | MA | 57729.125 | 59578.27 | -1849.145 | -3.104% | 59234.58 | -1505.455 | -2.542%
West Yarmouth - 42 Mid Tech | MA | 55410.9076 | 59560.35 | -4149.4424 | -6.967% | 61214.37 | -5803.4624 | -9.481%
Harrison - 130 Union Street | NY | 82236.0625 | 88062.58 | -5826.5175 | -6.616% | 87265.51 | -5029.4475 | -5.763%
Staten Island - Ellis Storage | NY | 191765.875 | 207822.32 | -16056.445 | -7.726% | 204052.08 | -12286.205 | -6.021%
Amherst - 595 Scholles Road | NY | 2867321 | 2878595.31 | -11274.31 | -0.3917% | 3401178 | -533857 | -15.7%
Lancaster 1 - Gunnville Road | NY | 2083516 | 2359960.67 | -276444.67 | -11.71% | 2540431.6 | -456915.6 | -17.99%
Lancaster 2 - Shisler Road | NY | 2235309 | 2491591.1 | -256282.1 | -10.29% | 2787145.4 | -551836.4 | -19.8%
Fullerton - 200 W Orangethorpe | CA | 354761.1973 | 367438.7 | -12677.5027 | -3.45% | 393892.4 | -39131.2027 | -9.934%
El Paso - 10500 Railroad Drive | TX | 503296.5 | 500389.6 | 2906.9 | 0.5809% | 463380.8 | 39915.7 | 8.614%
Friona - 900 Millard Ave | TX | 397759.75 | 427103.3 | -29343.55 | -0.068704 | 407846 | -10086.25 | -0.024731
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## 3rd Qtr
Catalyze |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 24556373.3647 | 13338415.565 | 11217957.7997 | 84.1% | 16091335.063 | 8465038.3017 | 52.61%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 327335.75 | 356125.757 | -28790.007 | -8.084% | 356900.593 | -29564.843 | -8.284%
Adelanto - 1 Sheep Creek Road | CA | 2114215 | 1461106.78 | 653108.22 | 44.7% | 2614830 | -500615 | -19.15%
Blackstone - 83 Federal Street | MA | 13578462.9 | 2158752.5 | 11419710.4 | 529% | 2524794.7 | 11053668.2 | 437.8%
Charlton - 299 Worcester Road | MA | 177889.25 | 187940.82 | -10051.57 | -5.348% | 193805.18 | -15915.93 | -8.212%
Wareham - 8 Thatcher Drive | MA | 53263.1875 | 56020.57 | -2757.3825 | -4.922% | 56817.75 | -3554.5625 | -6.256%
West Yarmouth - 42 Mid Tech | MA | 48266.4314 | 50053.63 | -1787.1986 | -3.571% | 59052.35 | -10785.9186 | -18.27%
Harrison - 130 Union Street | NY | 76723.875 | 84368.2 | -7644.325 | -9.061% | 84686.16 | -7962.285 | -9.402%
Staten Island - Ellis Storage | NY | 176827.75 | 197643.68 | -20815.93 | -10.53% | 192599.3 | -15771.55 | -8.189%
Amherst - 595 Scholles Road | NY | 2877859 | 2974616.59 | -96757.59 | -3.253% | 3227692.3 | -349833.3 | -10.84%
Lancaster 1 - Gunnville Road | NY | 1949345 | 2223602.676 | -274257.676 | -12.33% | 2521779.91 | -572434.91 | -22.7%
Lancaster 2 - Shisler Road | NY | 2002886 | 2352331.324 | -349445.324 | -14.86% | 2763271.98 | -760385.98 | -27.52%
Fullerton - 200 W Orangethorpe | CA | 365346.001 | 377445.998 | -12099.997 | -3.206% | 407532.61 | -42186.609 | -10.35%
El Paso - 10500 Railroad Drive | TX | 316759 | 332052.47 | -15293.47 | -4.606% | 440187.4 | -123428.4 | -28.04%
Friona - 900 Millard Ave | TX | 250550.375 | 284730.52 | -34180.145 | -12% | 393920.8 | -143370.425 | -36.4%
Augusta - 13 York Farm Road | ME | 175245 | 177556.3 | -2311.3 | -1.302% | 179724.4 | -4479.4 | -2.492%
Santa Ana - 1441 West | CA | 65398.8448 | 64067.75 | 1331.0948 | 2.078% | 73739.63 | -8340.7852 | -11.31%
Jessup -7950 Oceano Ave | MD

## 4th Qtr
Catalyze |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 3118893.8389 | 3900092.66 | -781198.8211 | -20.03% | 3455426.42 | -336532.5811 | -9.739%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 65772.8172 | 69341.71 | -3568.8928 | -5.147% | 89199.55 | -23426.7328 | -26.26%
Adelanto - 1 Sheep Creek Road | CA | 325155.19 | 520859.43 | -195704.24 | -37.57% | 598929.86 | -273774.67 | -45.71%
Blackstone - 83 Federal Street | MA | 252743 | 624897.2 | -372154.2 | -59.55% | 578684.6 | -325941.6 | -56.32%
Charlton - 299 Worcester Road | MA | 53585 | 54004.93 | -419.93 | -0.7776% | 44160.56 | 9424.44 | 21.34%
Wareham - 8 Thatcher Drive | MA | 13329.25 | 14614.66 | -1285.41 | -8.795% | 12814.24 | 515.01 | 4.019%
West Yarmouth - 42 Mid Tech | MA | 10083.027 | 10303.93 | -220.903 | -2.144% | 11188.85 | -1105.823 | -9.883%
Harrison - 130 Union Street | NY | 20126.375 | 23942.07 | -3815.695 | -15.94% | 17598.99 | 2527.385 | 14.36%
Staten Island - Ellis Storage | NY | 47060.625 | 48562.54 | -1501.915 | -3.093% | 41106.87 | 5953.755 | 14.48%
Amherst - 595 Scholles Road | NY | 594632 | 508137.8 | 86494.2 | 17.02% | 504807.8 | 89824.2 | 17.79%
Lancaster 1 - Gunnville Road | NY | 607271 | 717300 | -110029 | -15.34% | 497052.2 | 110218.8 | 22.17%
Lancaster 2 - Shisler Road | NY | 636011 | 809279.2 | -173268.2 | -21.41% | 542837.9 | 93173.1 | 17.16%
Fullerton - 200 W Orangethorpe | CA | 86851.375 | 94171.76 | -7320.385 | -7.773% | 99851.99 | -13000.615 | -13.02%
El Paso - 10500 Railroad Drive | TX | 122042.8047 | 149453.3 | -27410.4953 | -18.34% | 124795.5 | -2752.6953 | -2.206%
Friona - 900 Millard Ave | TX | 92571.625 | 93674.19 | -1102.565 | -1.177% | 98836.71 | -6265.085 | -6.339%
Augusta - 13 York Farm Road | ME | 138014.9375 | 143255.2 | -5240.2625 | -3.658% | 130076.1 | 7938.8375 | 6.103%
Santa Ana - 1441 West | CA | 53643.8125 | 18294.74 | 35349.0725 | 193.2% | 63484.7 | -9840.8875 | -15.5%
Jessup -7950 Oceano Ave | MD

## Jan
Catalyze |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 592532.4922 | 833649.635 | -241117.1428 | -28.92% | 1493236.849 | -900704.3568 | -60.32% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 40368.4375 | 39837.75 | 530.6875 | 1.332% | 48161.71 | -7793.2725 | -16.18% | 1.Inverter 5 tripped offline on 01/19/2024 at 12:30 & back online at 14:00. | 1.SR080353
Adelanto - 1 Sheep Creek Road | CA | 80417 | 352340 | -271923 | -77.18% | 479912 | -399495 | -83.24% | 1. Site frequently experiencing outages due to its ongoing curtailment by CAISO | 1. SR077480, SR079342
Blackstone - 83 Federal Street | MA | 106968 | 0 | 106968 |  | 352931.5 | -245963.5 | -69.69% | 1. SIte was offline from 01/15/2024 - 01/17/2024. | 1. SR080251
Charlton - 299 Worcester Road | MA | 11889 | 21739.23 | -9850.23 | -45.31% | 32151.25 | -20262.25 | -63.02% | 1. Site was offline on 01/27/2024 & back online on 01/29/2024. | 1. SR080523
Wareham - 8 Thatcher Drive | MA | 5780.1687 | 7080.061 | -1299.8923 | -18.36% | 8785.329 | -3005.1603 | -34.21%
West Yarmouth - 42 Mid Tech | MA | 4426.7571 | 5459.478 | -1032.7209 | -18.92% | 6769.56 | -2342.8029 | -34.61%
Harrison - 130 Union Street | NY | 5693.0625 | 9025.686 | -3332.6235 | -36.92% | 10708.14 | -5015.0775 | -46.83%
Staten Island - Ellis Storage | NY | 12897.375 | 21330.59 | -8433.215 | -39.54% | 23412.4 | -10515.025 | -44.91%
Amherst - 595 Scholles Road | NY | 99935 | 131383.6 | -31448.6 | -23.94% | 286492 | -186557 | -65.12% | 1. Site tripped offlline at 01/31/2024 at 09:30 & back online at 11:41. 2. Inverter 1 was offline on 01/10/2024 & back online at 01/11/2024 at 16:30. | 1.SR080616 2. SR080129
Lancaster 1 - Gunnville Road | NY
Lancaster 2 - Shisler Road | NY
Fullerton - 200 W Orangethorpe | CA | 66219.8789 | 65950.86 | 269.0189 | 0.4079% | 75151.27 | -8931.3911 | -11.88%
El Paso - 10500 Railroad Drive | TX | 94436.375 | 110748.9 | -16312.525 | -14.73% | 95880.07 | -1443.695 | -1.506%
Friona - 900 Millard Ave | TX | 63501.4375 | 68753.48 | -5252.0425 | -7.639% | 72881.62 | -9380.1825 | -12.87% | 1. Inverter 6 tripping on & off throught out the month. 2. Inverter 7 has tripping event on 01/12,1/14,1/16,1/19. | 1. SR074295 2. SR079995
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Feb
Catalyze |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2118917.295 | 2947649.778 | -828732.483 | -28.12% | 2750893.591 | -631976.296 | -22.97% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 58842.25 | 57965.88 | 876.37 | 1.512% | 67323.77 | -8481.52 | -12.6% | 1. Inverter 5 tripped offline most of the days. | 1. SR080353
Adelanto - 1 Sheep Creek Road | CA | 300982 | 344128.54 | -43146.54 | -12.54% | 597256.79 | -296274.79 | -49.61% | 1. Expected data was not populated for multiple days due to a weather station issue. 2. Inverter 4 turned offline on 02/23 & continued. 3. Site frequently experiencing outages due to its ongoing curtailment by CAISO | 1. SR081023 2. SR081269 3. SR081208
Blackstone - 83 Federal Street | MA | 371405 | 591797.9 | -220392.9 | -37.24% | 474063.7 | -102658.7 | -21.66% | 1. Inverter tripped offline on 02/23/2024 & back online on 02/26/2024. | 1. SR081287
Charlton - 299 Worcester Road | MA | 41404 | 47717.86 | -6313.86 | -13.23% | 31813.95 | 9590.05 | 30.14% | 1. Inverter 1 is offline from 02/05 to 02/14 & tripped offline from 02/20 at 10:30 & back online on 02/26 at 16:30. 2. Inverter 13 tripping on and off during high irradiance days. | 1.SR080728 2. SR081303
Wareham - 8 Thatcher Drive | MA | 7001.2688 | 11238.1 | -4236.8312 | -37.7% | 11253.3 | -4252.0312 | -37.78%
West Yarmouth - 42 Mid Tech | MA | 4449.0054 | 8729.468 | -4280.4626 | -49.03% | 7749.511 | -3300.5056 | -42.59%
Harrison - 130 Union Street | NY | 10644.0445 | 17668.44 | -7024.3955 | -39.76% | 14230.04 | -3585.9955 | -25.2%
Staten Island - Ellis Storage | NY | 28780.5 | 41920.19 | -13139.69 | -31.34% | 28582.98 | 197.52 | 0.691%
Amherst - 595 Scholles Road | NY | 238762 | 462549 | -223787 | -48.38% | 462796 | -224034 | -48.41% | 1. Inverter 2 tripping on & off on 02/03 & 02/04 & continued offline from 02/05 to 02/28. 2. Site was taken offline on 02/27/2023 at 12:53 & back online on 02/28. | 1. SR080713 2. SR081369
Lancaster 1 - Gunnville Road | NY | 422356 | 522536.7 | -100180.7 | -19.17% | 381411.8 | 40944.2 | 10.73% | 1. Site tripped offline on 02/10 & back online on 02/12 at 15:15. | 1.SR080915
Lancaster 2 - Shisler Road | NY | 393093 | 577373.1 | -184280.1 | -31.92% | 412202.9 | -19109.9 | -4.636% | 1. Site tripped offline on 02/10 & back online on 02/12 at 15:15. 2. Inverter 4.4 is offline on 02/18 and back online next day. 3. Inverter 4.4 was derating on multiple days this month due to a fan fault... 3. Inverters 3.1 through 3.6, and inverters 3.8 through 3.10 started derating on 02/25 & continued. | 1. SR080916 2. SR081087 3. SR081047 4. SR081344
Fullerton - 200 W Orangethorpe | CA | 64169.3512 | 65724.88 | -1555.5288 | -2.367% | 81499 | -17329.6488 | -21.26%
El Paso - 10500 Railroad Drive | TX | 102707.75 | 113239.9 | -10532.15 | -9.301% | 101578.9 | 1128.85 | 1.111%
Friona - 900 Millard Ave | TX | 74321.125 | 85059.82 | -10738.695 | -12.62% | 79130.95 | -4809.825 | -6.078% | 1. Inverter 6 tripping on & off throught out the month. | 1.SR074295
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Mar
Catalyze |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3211851.3128 | 3586849.91 | -374998.5972 | -10.45% | 4216360.07 | -1004508.7572 | -23.82% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 93147.8781 | 92388.49 | 759.3881 | 0.822% | 102127.4 | -8979.5219 | -8.792% | 1. Site was offline on 03/20 between 10:50am to 12:15pm 2. Inverter 5 has tripping events on daily bases | 1. SR082279 2. SR082780
Adelanto - 1 Sheep Creek Road | CA | 316722 | 203359 | 113363 | 55.75% | 819315.66 | -502593.66 | -61.34% | 1. Weather station reporting zero from 03/01 and resolved on 03/20 at 13:00 due to that expected energy is low 2. Sit was offline on 03/27 between 08:00am to 12:00 pm 3. Inverter 4 is offline throughout the month, breaker need to be replaced | 1. SR081023 2. SR082819 3. SR081269
Blackstone - 83 Federal Street | MA | 543056 | 659185.6 | -116129.6 | -17.62% | 665713.1 | -122657.1 | -18.42% | 1. Inverter tripped offline on 03/24 at 12:00pm and back online on 03/25 at 10:15am | 1. SR082618
Charlton - 299 Worcester Road | MA | 53094.5 | 53440.83 | -346.33 | -0.6481% | 60191.09 | -7096.59 | -11.79%
Wareham - 8 Thatcher Drive | MA | 13951.1875 | 14371.27 | -420.0825 | -2.923% | 16016.2 | -2065.0125 | -12.89%
West Yarmouth - 42 Mid Tech | MA | 12216.5316 | 12405.7 | -189.1684 | -1.525% | 13342.11 | -1125.5784 | -8.436%
Harrison - 130 Union Street | NY | 21772.893 | 22420.77 | -647.877 | -2.89% | 21506.07 | 266.823 | 1.241%
Staten Island - Ellis Storage | NY | 49193.875 | 52917.68 | -3723.805 | -7.037% | 50803.64 | -1609.765 | -3.169%
Amherst - 595 Scholles Road | NY | 665953 | 712004.57 | -46051.57 | -6.468% | 764414 | -98461 | -12.88%
Lancaster 1 - Gunnville Road | NY | 571324 | 681059.8 | -109735.8 | -16.11% | 644288.2 | -72964.2 | -11.32% | 1. Site tripped offline on 03/10 at 17:30 and back online on 03/11 at 11:00am 2. Site tripped offline on 03/13 at 12:25pm and back online on 03/14 at 08:35am | 1. SR081733 2. SR081870
Lancaster 2 - Shisler Road | NY | 558564 | 740013.1 | -181449.1 | -24.52% | 707412.2 | -148848.2 | -21.04% | 1. Inverters 3.1 to 3.10 are derating from 02/26 to 03/09. 2. Site tripped offline, Voltages available at the meter. Possible main breaker trip at 12:15 on 03/13 and back online at 8:30 on 03/14. | 1. SR081344 2. SR081871
Fullerton - 200 W Orangethorpe | CA | 97998.635 | 105532.7 | -7534.065 | -7.139% | 111916.4 | -13917.765 | -12.44% | 1. Inverter 3 is derating on sunny days resolved on 03/26 2. Site was offline on 03/13 between 08:30am to 09:15 | 1. SR081571 2. SR081844
El Paso - 10500 Railroad Drive | TX | 105355.125 | 126408.7 | -21053.575 | -16.66% | 133396 | -28040.875 | -21.02% | 1. Site tripped offline due to missing "Phase A voltages" at 11:45 on 03/17 and back online at 10:30 on 03/25. | 1. SR081970
Friona - 900 Millard Ave | TX | 109501.6875 | 111341.7 | -1840.0125 | -1.653% | 105918 | 3583.6875 | 3.383% | 1. Inverter 6 tripping on & off on 03/05, 03/18, 03/25, 03/26. | 1. SR074295
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Apr
Catalyze |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 3586730.2794 | 4172026.29 | -585296.0106 | -14.03% | 4897603.03 | -1310872.7506 | -26.77% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 110443.9344 | 110570.8 | -126.8656 | -0.1147% | 119130.8 | -8686.8656 | -7.292% | 1. Inverter 5 has tripping events on daily bases. | 1. SR082780
Adelanto - 1 Sheep Creek Road | CA | 402561 | 693821 | -291260 | -41.98% | 898384 | -495823 | -55.19% | 1. Inverter 4 is offline throughout the month, breaker need to be replaced | 1. SR081269
Blackstone - 83 Federal Street | MA | 606024 | 680455.2 | -74431.2 | -10.94% | 770475.3 | -164451.3 | -21.34%
Charlton - 299 Worcester Road | MA | 56399 | 57742.91 | -1343.91 | -2.327% | 70885.53 | -14486.53 | -20.44% | 1. Inverter 6 tripped offline on 04/28 at 6:30AM and back online on 04/28 at 7:45am | 1. SR083896
Wareham - 8 Thatcher Drive | MA | 16925.875 | 17111.19 | -185.315 | -1.083% | 18394.93 | -1469.055 | -7.986%
West Yarmouth - 42 Mid Tech | MA | 16282.5227 | 16635.1 | -352.5773 | -2.119% | 18770.49 | -2487.9673 | -13.25%
Harrison - 130 Union Street | NY | 21737.375 | 23442.16 | -1704.785 | -7.272% | 26207.47 | -4470.095 | -17.06% | 1. Site was offline from 13:15 to 15:00 on 04/29. 2. Site is offline on 04/03 at 18:45 and back online on 9:30am on 04/05 and again offline on 04/07 10:00am and back online on 04/07 at 12:30pm. | 1. SR083973 2. SR082599
Staten Island - Ellis Storage | NY | 56581 | 60019.33 | -3438.33 | -5.729% | 60619.51 | -4038.51 | -6.662%
Amherst - 595 Scholles Road | NY | 718270 | 768638 | -50368 | -6.553% | 953051 | -234781 | -24.63% | 1. Site tripped offline on 04/09 at 17:52 and back online on 04/10 at 16:00 2. Site tripped offline on 04/17 at 10:52 and back online on 12:00pm | 1. SR083278 2. SR083540
Lancaster 1 - Gunnville Road | NY | 557874 | 635837.5 | -77963.5 | -12.26% | 746890.6 | -189016.6 | -25.31% | 1. Inverter 1.3 is offline on 04/08 and back online on 04/08 at 15:15 2. All inverters tripped offline at 15:02 on 04/19 and back online on 04/22 at 8:30am | 1. SR083167 2. SR083639
Lancaster 2 - Shisler Road | NY | 609258 | 678559.1 | -69301.1 | -10.21% | 820159.4 | -210901.4 | -25.71% | 1. All inverters tripped offline at 15:02 on 04/19 and back online on 04/22 at 8:30am | 1. SR083640
Fullerton - 200 W Orangethorpe | CA | 118417.1973 | 125423.7 | -7006.5027 | -5.586% | 121841.4 | -3424.2027 | -2.81% | 1. Site is offline on 04/13 at 21:00 on 04/13/2024 and back online on 04/13 at 23:00. | 1. SR083388
El Paso - 10500 Railroad Drive | TX | 160423.625 | 160278.5 | 145.125 | 0.09055% | 148074 | 12349.625 | 8.34% | 1. Inverter 6 tripping on and off on 04/02, 04/06, 04/20, 04/22, 04/27, 04/29 & 04/30 with fault "Fault to stop DC wrong polarity." | 1. SR083891
Friona - 900 Millard Ave | TX | 135532.75 | 143491.8 | -7959.05 | -5.547% | 124718.6 | 10814.15 | 8.671% | 1. Inverter 6 tripping on & off 04/12, 04/14, 04/17, 04/18, 04/20, 04/21 & 04/27 | 1. SR074295
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## May
Catalyze |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 4754643.5405 | 4977329.46 | -222685.9195 | -4.474% | 5677264.59 | -922621.0495 | -16.25% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 129623.4375 | 138492 | -8868.5625 | -6.404% | 137316 | -7692.5625 | -5.602%
Adelanto - 1 Sheep Creek Road | CA | 444296 | 486481 | -42185 | -8.671% | 998170 | -553874 | -55.49%
Blackstone - 83 Federal Street | MA | 667886 | 782886.8 | -115000.8 | -14.69% | 818352.4 | -150466.4 | -18.39% | 1. Site tripped offline at 15:15 on 05/15 and back online at 18:00 on 05/19. | 1. SR084815
Charlton - 299 Worcester Road | MA | 63015.5 | 66192.48 | -3176.98 | -4.8% | 69886.66 | -6871.16 | -9.832%
Wareham - 8 Thatcher Drive | MA | 19262.5 | 19740.83 | -478.33 | -2.423% | 20442.38 | -1179.88 | -5.772%
West Yarmouth - 42 Mid Tech | MA | 18404.1693 | 19706.43 | -1302.2607 | -6.608% | 20391.91 | -1987.7407 | -9.748%
Harrison - 130 Union Street | NY | 28316.3125 | 29728.98 | -1412.6675 | -4.752% | 30348.96 | -2032.6475 | -6.698%
Staten Island - Ellis Storage | NY | 63332.7462 | 67493.26 | -4160.5138 | -6.164% | 69978.38 | -6645.6338 | -9.497%
Amherst - 595 Scholles Road | NY | 1116729 | 1058881.31 | 57847.69 | 5.463% | 1200817 | -84088 | -7.003%
Lancaster 1 - Gunnville Road | NY | 849171 | 904354.17 | -55183.17 | -6.102% | 894596 | -45425 | -5.078% | 1. Site tripped offline at 16:15 on 05/22 and back online at 08:45AM on 05/23. | 1. SR085032
Lancaster 2 - Shisler Road | NY | 919274 | 954343 | -35069 | -3.675% | 981722 | -62448 | -6.361% | 1. Inverter 4.7 tripped offline at 14:53 on 05/03 additionally it stopped communicating, later data got backfilled and issue resolved on 05/15. 2. Inverter 4.7 tripped offline at 14:30 on 05/19 and back online at 07:00AM on 05/20 inverter tripped offline at 13:15 on 05/20 and back online at 07:00AM on 05/21 inverter again tripped offline at 14:00 on 05/26 and back online at 07:00AM on 05/27. 3. Site tripped offline at 16:15 on 05/22 and back online at 08:45AM on 05/23. 4. Inverter 3.2 tripped offline at 13:15 on 05/26 and back online at 15:30 on 5/29. | 1. SR084244 2. SR084914 3. SR085033 4. SR085171
Fullerton - 200 W Orangethorpe | CA | 113363 | 113261 | 102 | 0.09006% | 135181 | -21818 | -16.14%
El Paso - 10500 Railroad Drive | TX | 184602.875 | 182605.6 | 1997.275 | 1.094% | 160947.4 | 23655.475 | 14.7% | 1. Inverter 6 is offline from 08:00AM to 13:00 on 05/08. | 1. SR083891
Friona - 900 Millard Ave | TX | 137367 | 153162.6 | -15795.6 | -10.31% | 139114.5 | -1747.5 | -1.256% | 1. Site is offline from 13:00 to 14:45 on 05/16 and again site is offline 10:00AM from 12:15PM on 05/22 but inverters still not communicating. | 1. SR084785
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Jun
Catalyze |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 4345693.4694 | 4743555.64 | -397862.1706 | -8.387% | 5825174.42 | -1479480.9506 | -25.4% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 122127.25 | 133315 | -11187.75 | -8.392% | 135560.3 | -13433.05 | -9.909%
Adelanto - 1 Sheep Creek Road | CA | 445728 | 347040 | 98688 | 28.44% | 1054180 | -608452 | -57.72% | 1.Weather station stopped communicating from 06/21 at 10:00 throghout the month | 1.SR086598
Blackstone - 83 Federal Street | MA | 740225 | 880901.4 | -140676.4 | -15.97% | 856726.7 | -116501.7 | -13.6% | 1. Meter was replaced on 06/14. 2. Site tripped offline at 11:30 on 06/26 and back online at 16:23 on same day | 1. SR084901 2. SR086820
Charlton - 299 Worcester Road | MA | 69632.75 | 74910.6 | -5277.85 | -7.046% | 65333.61 | 4299.14 | 6.58%
Wareham - 8 Thatcher Drive | MA | 21540.75 | 22726.25 | -1185.5 | -5.216% | 20397.27 | 1143.48 | 5.606%
West Yarmouth - 42 Mid Tech | MA | 20724.2156 | 23218.82 | -2494.6044 | -10.74% | 22051.97 | -1327.7544 | -6.021% | 1. Inverter 1 was offline on 06/16 and back online on 06/17 | 1. SR086284
Harrison - 130 Union Street | NY | 32182.375 | 34891.44 | -2709.065 | -7.764% | 30709.08 | 1473.295 | 4.798%
Staten Island - Ellis Storage | NY | 71852.1288 | 80309.73 | -8457.6012 | -10.53% | 73454.19 | -1602.0612 | -2.181% | 1. Inverter 2 primary unit was offline from 06/06 and was being RMA'd | 1. SR085732
Amherst - 595 Scholles Road | NY | 1032322 | 1051076 | -18754 | -1.784% | 1247310 | -214988 | -17.24% | 1. SEL relay opened at 22:30 and was remotely reclosed at 23:00 on 06/28 | 1. SR083540
Lancaster 1 - Gunnville Road | NY | 676471 | 819769 | -143298 | -17.48% | 898945 | -222474 | -24.75% | 1. Site tripped offline at 11:30 on 06/27 due to utility outage and was still offline | 1. SR087032
Lancaster 2 - Shisler Road | NY | 706777 | 858689 | -151912 | -17.69% | 985264 | -278487 | -28.27% | 1. Site tripped offline at 11:30 on 06/27 due to utility outage and was still offline 2. Inverters 3.6, 3.10, 4.5 and 4.7 are derating compared to peers thorughout the month from 06/13 | 1. SR087033 2. SR086289, SR086502
Fullerton - 200 W Orangethorpe | CA | 122981 | 128754 | -5773 | -4.484% | 136870 | -13889 | -10.15% | 1. Inverter 2 tripped offline at 13:07 on 06/29 and back online on 06/30 | 1. SR087133
El Paso - 10500 Railroad Drive | TX | 158270 | 157505.5 | 764.5 | 0.4854% | 154359.4 | 3910.6 | 2.533% | 1. Inverter 6 tripping on and off throughout the month | 1. SR083891
Friona - 900 Millard Ave | TX | 124860 | 130448.9 | -5588.9 | -4.284% | 144012.9 | -19152.9 | -13.3%
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Jul
Catalyze |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 10168856.2742 | 4695360.013 | 5473496.2612 | 116.6% | 5873579.602 | 4295276.6722 | 73.13% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 115895.75 | 130968.021 | -15072.271 | -11.51% | 131600.289 | -15704.539 | -11.93% | 1.Inverter 2 is underproducing compared to its rated capacity on 7/25 2. Inverters 1, 5, 6, 7 are down strings. 100kW inverters producing roughly 60-65 kW through out the month | 1.SR088244 2.SR088370
Adelanto - 1 Sheep Creek Road | CA | 537972 | 424045 | 113927 | 26.87% | 950229 | -412257 | -43.39% | 1.Weather station stopped communicating from 06/21 at 10:00 and not communicated till 07/03 | 1.SR086598
Blackstone - 83 Federal Street | MA | 6510624 | 790280.4 | 5720343.6 | 723.8% | 914785.3 | 5595838.7 | 611.7% | 1.Inverter tripped offline from 7/16 at 11:15AM and back online on 7/17 at 07:30AM | 1.SR087755
Charlton - 299 Worcester Road | MA | 65183.75 | 69391.77 | -4208.02 | -6.064% | 67724.03 | -2540.28 | -3.751%
Wareham - 8 Thatcher Drive | MA | 19338 | 20306.2 | -968.2 | -4.768% | 20720.27 | -1382.27 | -6.671%
West Yarmouth - 42 Mid Tech | MA | 18250.4612 | 19901.52 | -1651.0588 | -8.296% | 22751.73 | -4501.2688 | -19.78%
Harrison - 130 Union Street | NY | 29157 | 32679.73 | -3522.73 | -10.78% | 32407.31 | -3250.31 | -10.03% | 1.Inverter 3 started to underperform by 15kW through out the month. | 1.SR087481
Staten Island - Ellis Storage | NY | 68730.75 | 75949.18 | -7218.43 | -9.504% | 73790.26 | -5059.51 | -6.857% | 1.Inverter 2 primary unit was offline from 06/06 and was being RMA'd | 1.SR085732
Amherst - 595 Scholles Road | NY | 1215073 | 1252059 | -36986 | -2.954% | 1284779 | -69706 | -5.426%
Lancaster 1 - Gunnville Road | NY | 603967 | 719584.66 | -115617.66 | -16.07% | 922070.49 | -318103.49 | -34.5% | 1.Site tripped offline from 06/27 at 11:30 due to utility outage and back online on 7/9 at 16:45. | 1.SR087032
Lancaster 2 - Shisler Road | NY | 565331 | 718700.599 | -153369.599 | -21.34% | 1010220.65 | -444889.65 | -44.04% | 1.Site tripped offline from 06/27 at 11:30 due to utility outage and back online on 7/10 at 19:30. 2.Inverters 3.6, 3.10, 4.5 and 4.7 are derating compared to peers thorughout the month from 06/13 | 1.SR087033 2. SR086289, SR088216
Fullerton - 200 W Orangethorpe | CA | 125670.813 | 140511.833 | -14841.02 | -10.56% | 145309.173 | -19638.36 | -13.51%
El Paso - 10500 Railroad Drive | TX | 161467.25 | 159590.3 | 1876.95 | 1.176% | 152764.1 | 8703.15 | 5.697% | 1.Inverter 6 having multilpe tripping events | 1.SR088483
Friona - 900 Millard Ave | TX | 132195.5 | 141391.8 | -9196.3 | -6.504% | 144428 | -12232.5 | -8.47% | 1.Inverter 6 has a history of tripping intermittently 2.Inverter 2 tripped offline from 7/20 at 14:45 through out the month | 1.SR087629 2.SR087961
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Aug
Catalyze |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 10206865.794 | 4550188.792 | 5656677.002 | 124.3% | 5433447.141 | 4773418.653 | 87.85% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 118176.875 | 123432.136 | -5255.261 | -4.258% | 127023.464 | -8846.589 | -6.965% | 1.Site offline from 12:00 to 13:00 | 1.SR089164
Adelanto - 1 Sheep Creek Road | CA | 896073 | 594050.18 | 302022.82 | 50.84% | 907237.63 | -11164.63 | -1.231% | 1. Inverters 12, 14, 16, and 19 have been RMA’d. Weather station stopped communications on 08/22 and regained communications on 08/27 | 1 SR089438
Blackstone - 83 Federal Street | MA | 6508477 | 751944.1 | 5756532.9 | 765.6% | 867226 | 5641251 | 650.5% | 1.Site tripped offline from 09:45AM to 18:00PM on 8/27 | 1.SR089606
Charlton - 299 Worcester Road | MA | 58878.25 | 62942.85 | -4064.6 | -6.458% | 65777.84 | -6899.59 | -10.49% | 1.Inverter 12 tripped offline at 11:45 from 8/17 and back online on 8/19 | 1. SR089195
Wareham - 8 Thatcher Drive | MA | 18908.75 | 19888.56 | -979.81 | -4.927% | 19571.71 | -662.96 | -3.387%
West Yarmouth - 42 Mid Tech | MA | 17724.5435 | 17631.99 | 92.5535 | 0.5249% | 20351.46 | -2626.9165 | -12.91%
Harrison - 130 Union Street | NY | 25807.4375 | 28003.88 | -2196.4425 | -7.843% | 28652.64 | -2845.2025 | -9.93%
Staten Island - Ellis Storage | NY | 57841.375 | 65548.18 | -7706.805 | -11.76% | 63963.51 | -6122.135 | -9.571% | 1.Inverter 2 back online on 8/13 at 12:30. 2.Inverter 7 offline on 8/4 | 1.SR085732 2.SR088588
Amherst - 595 Scholles Road | NY | 914981 | 945249.87 | -30268.87 | -3.202% | 1107868 | -192887 | -17.41% | 1. Site was tripped offline on 08/05 at 07:00am and back online at 09:00am on 08/05 | 1. SR088603
Lancaster 1 - Gunnville Road | NY | 633199 | 793351.616 | -160152.616 | -20.19% | 858359.02 | -225160.02 | -26.23% | 1.Site offline from 8/13 at 12:15 and back online on 8/16 at 14:45. | 1.SR088990
Lancaster 2 - Shisler Road | NY | 705750 | 876216.325 | -170466.325 | -19.45% | 941132.53 | -235382.53 | -25.01% | 1.Inverter 04.6 has started derating on 8/4 from 13:00 and is producing only 45kW. 2.Inverter 3.6 is underperforming by 15 Kw 3.Inverter 4.6, 4.8 are being RMAD | 1.SR088597 2. SR089161 3. SR088420
Fullerton - 200 W Orangethorpe | CA | 136080.188 | 130392.365 | 5687.823 | 4.362% | 140568.937 | -4488.749 | -3.193% | 1.Site had a brief outage from 23:45 on 08/06 to 00:02 on 08/07. | 1.SR088714
El Paso - 10500 Railroad Drive | TX | 65442.75 | 71995.97 | -6553.22 | -9.102% | 151100.7 | -85657.95 | -56.69% | 1. Site tripped offline at 11:55 from 8/14 due to on going roof fire investigations. Per Catalyze the site is to remain off | 1.SR089036
Friona - 900 Millard Ave | TX | 49525.625 | 69540.77 | -20015.145 | -28.78% | 134613.7 | -85088.075 | -63.21% | 1.Inverter 2 back online on 08/05 2.Inverter 4 being RMAD 3.Site is offline. Meter has voltage - possible main breaker trip. Per Catalyze the site is to remain off from 08/14 | 1.SR087961 2.SR088579 3.SR089026
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Sep
Catalyze |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 4180651.2964 | 4092866.76 | 87784.5364 | 2.145% | 4784308.32 | -603657.0236 | -12.62% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 93263.125 | 101725.6 | -8462.475 | -8.319% | 98276.84 | -5013.715 | -5.102%
Adelanto - 1 Sheep Creek Road | CA | 680170 | 443011.6 | 237158.4 | 53.53% | 757363.37 | -77193.37 | -10.19% | 1. Inverters 6 and 13 are offline from 10/16 inverter 6 is back online on 10/21 and inverter 13 back online on 10/29 | 1. SR092228
Blackstone - 83 Federal Street | MA | 559361.9 | 616528 | -57166.1 | -9.272% | 742783.4 | -183421.5 | -24.69% | 1. Inverters tripped offline at 11:30am and back online at 14:15am on 09/09. | 1. SR090037.
Charlton - 299 Worcester Road | MA | 53827.25 | 55606.2 | -1778.95 | -3.199% | 60303.31 | -6476.06 | -10.74%
Wareham - 8 Thatcher Drive | MA | 15016.4375 | 15825.81 | -809.3725 | -5.114% | 16525.77 | -1509.3325 | -9.133%
West Yarmouth - 42 Mid Tech | MA | 12291.4267 | 12520.12 | -228.6933 | -1.827% | 15949.16 | -3657.7333 | -22.93%
Harrison - 130 Union Street | NY | 21759.4375 | 23684.59 | -1925.1525 | -8.128% | 23626.21 | -1866.7725 | -7.901%
Staten Island - Ellis Storage | NY | 50255.625 | 56146.32 | -5890.695 | -10.49% | 54845.53 | -4589.905 | -8.369%
Amherst - 595 Scholles Road | NY | 747805 | 777307.72 | -29502.72 | -3.796% | 835045.3 | -87240.3 | -10.45%
Lancaster 1 - Gunnville Road | NY | 712179 | 710666.4 | 1512.6 | 0.2128% | 741350.4 | -29171.4 | -3.935%
Lancaster 2 - Shisler Road | NY | 731805 | 757414.4 | -25609.4 | -3.381% | 811918.8 | -80113.8 | -9.867% | 1. Inverter 4.8 are being RMAD | 1. SR088420
Fullerton - 200 W Orangethorpe | CA | 103595 | 106541.8 | -2946.8 | -2.766% | 121654.5 | -18059.5 | -14.84%
El Paso - 10500 Railroad Drive | TX | 89849 | 100466.2 | -10617.2 | -10.57% | 136322.6 | -46473.6 | -34.09% | 1. Site tripped offline at 11:55 from 8/14 and is back online on 09/12. 2. Inverter 6 is having tripping issue from 09/20 and inverter being RMAD from 10/01. | 1. SR089036. 2. SR090993.
Friona - 900 Millard Ave | TX | 68829.25 | 73797.95 | -4968.7 | -6.733% | 114879.1 | -46049.85 | -40.09% | 1. Site tripped offline at 12:30 from 8/14 and is back online on 09/10. 2. Inverter 4 being RMAD 3. Inverter 6 is having tripping issue from 09/23. | 1. SR089026. 2. SR088579, SR090275. 3. SR091081.
Augusta - 13 York Farm Road | ME | 175245 | 177556.3 | -2311.3 | -1.302% | 179724.4 | -4479.4 | -2.492%
Santa Ana - 1441 West | CA | 65398.8448 | 64067.75 | 1331.0948 | 2.078% | 73739.63 | -8340.7852 | -11.31%
Jessup -7950 Oceano Ave | MD

## Oct
Catalyze |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 3118893.8389 | 3900092.66 | -781198.8211 | -20.03% | 3455426.42 | -336532.5811 | -9.739% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 65772.8172 | 69341.71 | -3568.8928 | -5.147% | 89199.55 | -23426.7328 | -26.26%
Adelanto - 1 Sheep Creek Road | CA | 325155.19 | 520859.43 | -195704.24 | -37.57% | 598929.86 | -273774.67 | -45.71% | 1. Inverters 6 and 13 are offline from 10/16, inverter 6 back online on 10/21, inverter 14 is being RMA'd from 10/28 and inverter 13 and 14 are back online on 10/29. 2. BOM temperature sensor reporting zero value from 10/18. 3. Site appears to be curtailed. The site is not reaching past 370 kW on 10/30 and Curtailment period has ended at 2:15PM on 10/30 | 1. SR092228 2. SR092324 3. SR092807
Blackstone - 83 Federal Street | MA | 252743 | 624897.2 | -372154.2 | -59.55% | 578684.6 | -325941.6 | -56.32% | 1. Inverter tripped offline at 11:00 AM from 10/15 through out the month | 1. SR092161
Charlton - 299 Worcester Road | MA | 53585 | 54004.93 | -419.93 | -0.7776% | 44160.56 | 9424.44 | 21.34%
Wareham - 8 Thatcher Drive | MA | 13329.25 | 14614.66 | -1285.41 | -8.795% | 12814.24 | 515.01 | 4.019%
West Yarmouth - 42 Mid Tech | MA | 10083.027 | 10303.93 | -220.903 | -2.144% | 11188.85 | -1105.823 | -9.883%
Harrison - 130 Union Street | NY | 20126.375 | 23942.07 | -3815.695 | -15.94% | 17598.99 | 2527.385 | 14.36%
Staten Island - Ellis Storage | NY | 47060.625 | 48562.54 | -1501.915 | -3.093% | 41106.87 | 5953.755 | 14.48%
Amherst - 595 Scholles Road | NY | 594632 | 508137.8 | 86494.2 | 17.02% | 504807.8 | 89824.2 | 17.79% | 1. Site taken offline on 10/21 at 18:00 approximately 1hour 2. Inverter 1 under performance. Previous thermal flight attached, but there are likely more strings offline | 1. SR092384 2. SR092466
Lancaster 1 - Gunnville Road | NY | 607271 | 717300 | -110029 | -15.34% | 497052.2 | 110218.8 | 22.17% | 1. Site offline from 10/23 and back onine at 08:00AM on 10/25. 2.Site was taken offline from 10:45AM to 12:30PM on 10/17 for transformer work. | 1. SR092464 2. SR092035
Lancaster 2 - Shisler Road | NY | 636011 | 809279.2 | -173268.2 | -21.41% | 542837.9 | 93173.1 | 17.16% | 1. Site offline from 10/23 and back onine at 08:00AM on 10/25 | 1. SR092465
Fullerton - 200 W Orangethorpe | CA | 86851.375 | 94171.76 | -7320.385 | -7.773% | 99851.99 | -13000.615 | -13.02%
El Paso - 10500 Railroad Drive | TX | 122042.8047 | 149453.3 | -27410.4953 | -18.34% | 124795.5 | -2752.6953 | -2.206% | 1. Inverter 6 is offline on 10/30. 2. Inverter 3 is underperforming approximately 49kW from 10/21 | 1. SR090993 2. SR092377
Friona - 900 Millard Ave | TX | 92571.625 | 93674.19 | -1102.565 | -1.177% | 98836.71 | -6265.085 | -6.339% | 1. Inverter 4 is offline from 08/03 and back online on 10/16. 2. Inverter 7 is having multiple tripping event fom 10/06 and issue resolved on 10/22. 3. Inverter 6 is experiencing multiple tripping from 10/04 | 1. SR090275, SR088579 2. SR091081 3. SR091081, SR092449
Augusta - 13 York Farm Road | ME | 138014.9375 | 143255.2 | -5240.2625 | -3.658% | 130076.1 | 7938.8375 | 6.103% | 1. Inverter 1 is underproducing approximately 15-25kw from 10/04 | 1. SR092361
Santa Ana - 1441 West | CA | 53643.8125 | 18294.74 | 35349.0725 | 193.2% | 63484.7 | -9840.8875 | -15.5% | 1. Weather station is not communicating from 10/11 and later started communication on 10/30. | 1. SR092453
Jessup -7950 Oceano Ave | MD

## Nov
Catalyze |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA
Adelanto - 1 Sheep Creek Road | CA
Blackstone - 83 Federal Street | MA
Charlton - 299 Worcester Road | MA
Wareham - 8 Thatcher Drive | MA
West Yarmouth - 42 Mid Tech | MA
Harrison - 130 Union Street | NY
Staten Island - Ellis Storage | NY
Amherst - 595 Scholles Road | NY
Lancaster 1 - Gunnville Road | NY
Lancaster 2 - Shisler Road | NY
Fullerton - 200 W Orangethorpe | CA
El Paso - 10500 Railroad Drive | TX
Friona - 900 Millard Ave | TX
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Dec
Catalyze |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA
Adelanto - 1 Sheep Creek Road | CA
Blackstone - 83 Federal Street | MA
Charlton - 299 Worcester Road | MA
Wareham - 8 Thatcher Drive | MA
West Yarmouth - 42 Mid Tech | MA
Harrison - 130 Union Street | NY
Staten Island - Ellis Storage | NY
Amherst - 595 Scholles Road | NY
Lancaster 1 - Gunnville Road | NY
Lancaster 2 - Shisler Road | NY
Fullerton - 200 W Orangethorpe | CA
El Paso - 10500 Railroad Drive | TX
Friona - 900 Millard Ave | TX
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD

## Sites
Portfolio: | Catalyze
Site DAS Name | Site | State | Update | DAS
CA Fresno - 3150 Shaw Ave - 19600 | Fresno - 3150 Shaw Ave | CA |  | PowerTrack
Sheep Creek Solar | Adelanto - 1 Sheep Creek Road | CA |  | Aderis
MA Blackstone - 83 Federal St - 18170 | Blackstone - 83 Federal Street | MA | AEF | PowerTrack
MA Charlton - 299 Worcester Rd - 18063 | Charlton - 299 Worcester Road | MA | AEF | PowerTrack
MA Wareham - 8 Thatcher Ln - 1010 | Wareham - 8 Thatcher Drive | MA | AEF | PowerTrack
MA West Yarmouth - 42 Mid-Tech Drive - 17944 | West Yarmouth - 42 Mid Tech | MA | AEF | PowerTrack
NY Harrison - 130 Union Ave - 18141 | Harrison - 130 Union Street | NY | AEF | PowerTrack
NY Staten Island - 1 Ellis St - 18195 | Staten Island - Ellis Storage | NY | AEF | PowerTrack
Amherst Community Solar | Amherst - 595 Scholles Road | NY |  | Aderis
Lancaster 1 - Gunnville Road | Lancaster 1 - Gunnville Road | NY |  | PowerTrack
Lancaster 2 - Shisler Road | Lancaster 2 - Shisler Road | NY |  | PowerTrack
Fullerton - 200 W Orangethorpe - 19603 | Fullerton - 200 W Orangethorpe | CA |  | PowerTrack
TX El Paso - 10500 Railroad Drive - 19648 | El Paso - 10500 Railroad Drive | TX | AEF | PowerTrack
TX Friona - 900 Millard Ave - 19506 | Friona - 900 Millard Ave | TX | AEF | PowerTrack
ME Augusta - 13 York Farm Rd - 18196 | Augusta - 13 York Farm Road | ME | AEF | PowerTrack
CA Santa Ana - 1441 W 17th St - 21198 | Santa Ana - 1441 West | CA |  | PowerTrack
MD Jessup 7950 Oceano Ave - 22337 | Jessup -7950 Oceano Ave | MD |  | PowerTrack