## Year to Date
38 DN |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 34159931.2533 | 36814504.27 | -2654573.0167 | -7.211% | 37469023.93 | -3309092.6767 | -8.832%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 1676761 | 1928818.6 | -252057.6 | -13.07% | 1961527.1 | -284766.1 | -14.52%
Barton Acres | MA | 1378068 | 1502729.34 | -124661.34 | -8.296% | 1402771.03 | -24703.03 | -1.761%
Bowden | MA | 2796303 | 2893693.1 | -97390.1 | -3.366% | 2917676.5 | -121373.5 | -4.16%
Blair Wire Village | MA | 1334623 | 1553075.08 | -218452.08 | -14.07% | 1460898.94 | -126275.94 | -8.644%
Boutilier | MA | 3764897 | 3818598 | -53701 | -1.406% | 3850760.9 | -85863.9 | -2.23%
Cherry Valley | MA | 1298103 | 1496219.72 | -198116.72 | -13.24% | 1413852 | -115749 | -8.187%
Cohasse | MA | 1247416 | 1371717.14 | -124301.14 | -9.062% | 1532098.9 | -284682.9 | -18.58%
ISM Dighton Solar 2 | MA | 2842231 | 2873705.2 | -31474.2 | -1.095% | 2971910.2 | -129679.2 | -4.363%
Dudley River 1 | MA | 1364132 | 1292993.39 | 71138.61 | 5.502% | 1475342.13 | -111210.13 | -7.538%
Dudley River 2 | MA | 1309953 | 1411673.47 | -101720.47 | -7.206% | 1409680.23 | -99727.23 | -7.074%
Dudley River 3 | MA | 1346879 | 1408931.43 | -62052.43 | -4.404% | 1429518.69 | -82639.69 | -5.781%
Flint Pond | MA | 638701.5 | 612612.02 | 26089.48 | 4.259% | 663638.8 | -24937.3 | -3.758%
Incom | MA | 2857329 | 3267765.3 | -410436.3 | -12.56% | 3094273.1 | -236944.1 | -7.658%
JH | MA | 1288585 | 1445468.43 | -156883.43 | -10.85% | 1496951.8 | -208366.8 | -13.92%
Ledeaux | MA | 1189250 | 1321486.57 | -132236.57 | -10.01% | 1452934.59 | -263684.59 | -18.15%
Palombo A | MA | 2698488.0033 | 2966476.9 | -267988.8967 | -9.034% | 3196926 | -498437.9967 | -15.59%
Palombo B | MA | 1343115 | 1311633.75 | 31481.25 | 2.4% | 1458667.69 | -115552.69 | -7.922%
St Josephs Church | MA | 1283220 | 1544966.52 | -261746.52 | -16.94% | 1440925.72 | -157705.72 | -10.94%
Sunset A | MA | 602617 | 711412.17 | -108795.17 | -15.29% | 660439.29 | -57822.29 | -8.755%
Sunset B | MA | 565031.75 | 629828.56 | -64796.81 | -10.29% | 652513.02 | -87481.27 | -13.41%
Woodchuck | MA | 1334228 | 1450699.58 | -116471.58 | -8.029% | 1525717.3 | -191489.3 | -12.55%

## 1st Qtr
38 DN |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 7636294.2 | 9592493.09 | -1956198.89 | -20.39% | 9198970.52 | -1562676.32 | -16.99%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 415423.7 | 380534.1 | 34889.6 | 9.169% | 486118.3 | -70694.6 | -14.54%
Barton Acres | MA | 278903 | 404890.34 | -125987.34 | -31.12% | 310302.93 | -31399.93 | -10.12%
Bowden | MA | 599781 | 699201.8 | -99420.8 | -14.22% | 684239 | -84458 | -12.34%
Blair Wire Village | MA | 295062 | 433211.98 | -138149.98 | -31.89% | 341306.54 | -46244.54 | -13.55%
Boutilier | MA | 827517 | 919550.2 | -92033.2 | -10.01% | 851822.3 | -24305.3 | -2.853%
Cherry Valley | MA | 282016 | 421854.72 | -139838.72 | -33.15% | 328696 | -46680 | -14.2%
Cohasse | MA | 280620 | 396154.94 | -115534.94 | -29.16% | 421760.2 | -141140.2 | -33.46%
ISM Dighton Solar 2 | MA | 659167 | 744891.6 | -85724.6 | -11.51% | 727319.9 | -68152.9 | -9.37%
Dudley River 1 | MA | 310880 | 357948.8 | -47068.8 | -13.15% | 349978.03 | -39098.03 | -11.17%
Dudley River 2 | MA | 301930 | 358799.47 | -56869.47 | -15.85% | 335556.93 | -33626.93 | -10.02%
Dudley River 3 | MA | 323382 | 360473.33 | -37091.33 | -10.29% | 340886.99 | -17504.99 | -5.135%
Flint Pond | MA | 137854.5 | 185295.32 | -47440.82 | -25.6% | 149584.93 | -11730.43 | -7.842%
Incom | MA | 630621 | 833123.3 | -202502.3 | -24.31% | 827050.7 | -196429.7 | -23.75%
JH | MA | 288163 | 402797.43 | -114634.43 | -28.46% | 401279.4 | -113116.4 | -28.19%
Ledeaux | MA | 264616 | 322791.27 | -58175.27 | -18.02% | 380712.19 | -116096.19 | -30.49%
Palombo A | MA | 615329 | 833714 | -218385 | -26.19% | 905621 | -290292 | -32.05%
Palombo B | MA | 291761 | 390903.85 | -99142.85 | -25.36% | 321983.29 | -30222.29 | -9.386%
St Josephs Church | MA | 282762 | 414919.42 | -132157.42 | -31.85% | 362356.82 | -79594.82 | -21.97%
Sunset A | MA | 137863.5 | 205317.53 | -67454.03 | -32.85% | 146090.46 | -8226.96 | -5.631%
Sunset B | MA | 126223.5 | 163159.81 | -36936.31 | -22.64% | 144341.81 | -18118.31 | -12.55%
Woodchuck | MA | 286419 | 362959.88 | -76540.88 | -21.09% | 381962.8 | -95543.8 | -25.01%

## 2nd Qtr
38 DN |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 13517899.3033 | 13851375.37 | -333476.0667 | -2.408% | 14275415.72 | -757516.4167 | -5.306%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 669108.3 | 787267.6 | -118159.3 | -15.01% | 726874.3 | -57766 | -7.947%
Barton Acres | MA | 545310 | 539383.5 | 5926.5 | 1.099% | 560726.7 | -15416.7 | -2.749%
Bowden | MA | 1110105 | 1106578 | 3527 | 0.3187% | 1115432.6 | -5327.6 | -0.4776%
Blair Wire Village | MA | 519157 | 570134.1 | -50977.1 | -8.941% | 559056.2 | -39899.2 | -7.137%
Boutilier | MA | 1478476 | 1482573 | -4097 | -0.2763% | 1539248.5 | -60772.5 | -3.948%
Cherry Valley | MA | 522390 | 540948.9 | -18558.9 | -3.431% | 553860 | -31470 | -5.682%
Cohasse | MA | 499860 | 493690.6 | 6169.4 | 1.25% | 556612.7 | -56752.7 | -10.2%
ISM Dighton Solar 2 | MA | 1117692 | 1088094.3 | 29597.7 | 2.72% | 1141253.5 | -23561.5 | -2.065%
Dudley River 1 | MA | 536212 | 547912 | -11700 | -2.135% | 561943.9 | -25731.9 | -4.579%
Dudley River 2 | MA | 514464 | 540498.3 | -26034.3 | -4.817% | 537337 | -22873 | -4.257%
Dudley River 3 | MA | 530999 | 538683.8 | -7684.8 | -1.427% | 544401.9 | -13402.9 | -2.462%
Flint Pond | MA | 257182.5 | 220092.02 | 37090.48 | 16.85% | 264870.47 | -7687.97 | -2.903%
Incom | MA | 1124910 | 1245264.2 | -120354.2 | -9.665% | 1138926.2 | -14016.2 | -1.231%
JH | MA | 513411 | 524824.3 | -11413.3 | -2.175% | 551769.3 | -38358.3 | -6.952%
Ledeaux | MA | 478457 | 507528.3 | -29071.3 | -5.728% | 542279.8 | -63822.8 | -11.77%
Palombo A | MA | 1077552.0033 | 1080070.6 | -2518.5967 | -0.2332% | 1145758 | -68205.9967 | -5.953%
Palombo B | MA | 545434 | 464438.3 | 80995.7 | 17.44% | 583491.3 | -38057.3 | -6.522%
St Josephs Church | MA | 526463 | 569352.4 | -42889.4 | -7.533% | 546743.8 | -20280.8 | -3.709%
Sunset A | MA | 212868.5 | 230425.94 | -17557.44 | -7.62% | 263997.98 | -51129.48 | -19.37%
Sunset B | MA | 201745 | 219673.91 | -17928.91 | -8.162% | 260827.07 | -59082.07 | -22.65%
Woodchuck | MA | 536103 | 553941.3 | -17838.3 | -3.22% | 580004.5 | -43901.5 | -7.569%

## 3rd Qtr
38 DN |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 13005737.75 | 13370635.81 | -364898.06 | -2.729% | 13994637.69 | -988899.94 | -7.066%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 592229 | 761016.9 | -168787.9 | -22.18% | 748534.5 | -156305.5 | -20.88%
Barton Acres | MA | 553855 | 558455.5 | -4600.5 | -0.8238% | 531741.4 | 22113.6 | 4.159%
Bowden | MA | 1086417 | 1087913.3 | -1496.3 | -0.1375% | 1118004.9 | -31587.9 | -2.825%
Blair Wire Village | MA | 520404 | 549729 | -29325 | -5.334% | 560536.2 | -40132.2 | -7.16%
Boutilier | MA | 1458904 | 1416474.8 | 42429.2 | 2.995% | 1459690.1 | -786.1 | -0.05385%
Cherry Valley | MA | 493697 | 533416.1 | -39719.1 | -7.446% | 531296 | -37599 | -7.077%
Cohasse | MA | 466936 | 481871.6 | -14935.6 | -3.099% | 553726 | -86790 | -15.67%
ISM Dighton Solar 2 | MA | 1065372 | 1040719.3 | 24652.7 | 2.369% | 1103336.8 | -37964.8 | -3.441%
Dudley River 1 | MA | 517040 | 387132.59 | 129907.41 | 33.56% | 563420.2 | -46380.2 | -8.232%
Dudley River 2 | MA | 493559 | 512375.7 | -18816.7 | -3.672% | 536786.3 | -43227.3 | -8.053%
Dudley River 3 | MA | 492498 | 509774.3 | -17276.3 | -3.389% | 544229.8 | -51731.8 | -9.506%
Flint Pond | MA | 243664.5 | 207224.68 | 36439.82 | 17.58% | 249183.4 | -5518.9 | -2.215%
Incom | MA | 1101798 | 1189377.8 | -87579.8 | -7.363% | 1128296.2 | -26498.2 | -2.349%
JH | MA | 487011 | 517846.7 | -30835.7 | -5.955% | 543903.1 | -56892.1 | -10.46%
Ledeaux | MA | 446177 | 491167 | -44990 | -9.16% | 529942.6 | -83765.6 | -15.81%
Palombo A | MA | 1005607 | 1052692.3 | -47085.3 | -4.473% | 1145547 | -139940 | -12.22%
Palombo B | MA | 505920 | 456291.6 | 49628.4 | 10.88% | 553193.1 | -47273.1 | -8.545%
St Josephs Church | MA | 473995 | 560694.7 | -86699.7 | -15.46% | 531825.1 | -57830.1 | -10.87%
Sunset A | MA | 251885 | 275668.7 | -23783.7 | -8.628% | 250350.85 | 1534.15 | 0.6128%
Sunset B | MA | 237063.25 | 246994.84 | -9931.59 | -4.021% | 247344.14 | -10280.89 | -4.157%
Woodchuck | MA | 511706 | 533798.4 | -22092.4 | -4.139% | 563750 | -52044 | -9.232%

## 4th Qtr
38 DN |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
6th St. | CA | 0 | 0 | 0 |  |  | 0
Barton Acres | MA | 0 | 0 | 0 |  |  | 0
Bowden | MA | 0 | 0 | 0 |  |  | 0
Blair Wire Village | MA | 0 | 0 | 0 |  |  | 0
Boutilier | MA | 0 | 0 | 0 |  |  | 0
Cherry Valley | MA | 0 | 0 | 0 |  |  | 0
Cohasse | MA | 0 | 0 | 0 |  |  | 0
ISM Dighton Solar 2 | MA | 0 | 0 | 0 |  |  | 0
Dudley River 1 | MA | 0 | 0 | 0 |  |  | 0
Dudley River 2 | MA | 0 | 0 | 0 |  |  | 0
Dudley River 3 | MA | 0 | 0 | 0 |  |  | 0
Flint Pond | MA | 0 | 0 | 0 |  |  | 0
Incom | MA | 0 | 0 | 0 |  |  | 0
JH | MA | 0 | 0 | 0 |  |  | 0
Ledeaux | MA | 0 | 0 | 0 |  |  | 0
Palombo A | MA | 0 | 0 | 0 |  |  | 0
Palombo B | MA | 0 | 0 | 0 |  |  | 0
St Josephs Church | MA | 0 | 0 | 0 |  |  | 0
Sunset A | MA | 0 | 0 | 0 |  |  | 0
Sunset B | MA | 0 | 0 | 0 |  |  | 0
Woodchuck | MA | 0 | 0 | 0 |  |  | 0

## Jan
38 DN |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1074735.7533 | 1953737.18 | -879001.4267 | -44.99% | 2327559.48 | -1252823.7267 | -53.83%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 124703.5 | 103355.9 | 21347.6 | 20.65% | 146126.1 | -21422.6 | -14.66% | 1. Inverter 28 was offline from 12/14 and back online on 01/25 | 1. SR079280
Barton Acres | MA | 31509 | 84215.44 | -52706.44 | -62.59% | 69453.12 | -37944.12 | -54.63%
Bowden | MA | 69313 | 124922.7 | -55609.7 | -44.52% | 167677.4 | -98364.4 | -58.66%
Blair Wire Village | MA | 38474 | 97645.68 | -59171.68 | -60.6% | 83112.14 | -44638.14 | -53.71% | 1. Relay tripped and site is experiencing an outage on 01/07 at 09:47 and reclosed at 18:30 | 1. SR079999
Boutilier | MA | 104475 | 117645.2 | -13170.2 | -11.19% | 190658.8 | -86183.8 | -45.2%
Cherry Valley | MA | 33861 | 93717.02 | -59856.02 | -63.87% | 77483 | -43622 | -56.3% | 1. Inverter B stopped communicating at 08:15 on 01/23 and technican reset the inverter at 12:00 2. Inverter B stopped communicating on 01/28 at 111:15 and and technician reset the inverter at 12:00. on 01/29 3. Site tripped offline at 10:45 on 01/07 and back online 23:15 same day. | 1. SR080405 2. SR080529 3. SR080002
Cohasse | MA | 37057 | 86836.54 | -49779.54 | -57.33% | 114180.6 | -77123.6 | -67.55% | 1. site tripped offline at 21:00 on 01/09 and back online at 8:30 on 01/10. | 1. SR080109
ISM Dighton Solar 2 | MA | 123864 | 178054.9 | -54190.9 | -30.43% | 195853.9 | -71989.9 | -36.76% | 1. SEL Relay 2 tripped offline at 23:00 on 01/30 and reclosed at 10:45 on 01/31 2. Planned outage on 01/25 at 9:00 and site reclosed at 17:00 on same day. | 1. SR080611 2. SR080054
Dudley River 1 | MA | 43519 | 68762.9 | -25243.9 | -36.71% | 83762.23 | -40243.23 | -48.04%
Dudley River 2 | MA | 44123 | 70139.57 | -26016.57 | -37.09% | 81919.43 | -37796.43 | -46.14%
Dudley River 3 | MA | 47297 | 71573.83 | -24276.83 | -33.92% | 84149.19 | -36852.19 | -43.79%
Flint Pond | MA | 16497.5 | 40276 | -23778.5 | -59.04% | 33543.68 | -17046.18 | -50.82% | 1. site offline on 01/07 at 05:00 and resolved at 07:15 | 1. SR079998
Incom | MA | 83086 | 159872.4 | -76786.4 | -48.03% | 220156.9 | -137070.9 | -62.26% | 1. Site was offline on 01/25 at 04:45 and reclosed at 16:00 | 1. SR080455
JH | MA | 32274 | 86355.93 | -54081.93 | -62.63% | 106218.7 | -73944.7 | -69.62%
Ledeaux | MA | 28537 | 58671.27 | -30134.27 | -51.36% | 98769.99 | -70232.99 | -71.11%
Palombo A | MA | 79689.0033 | 187942.8 | -108253.7967 | -57.6% | 250093 | -170403.9967 | -68.14%
Palombo B | MA | 32703 | 91961.55 | -59258.55 | -64.44% | 71768.39 | -39065.39 | -54.43%
St Josephs Church | MA | 37183 | 87772.32 | -50589.32 | -57.64% | 91531.02 | -54348.02 | -59.38%
Sunset A | MA | 16708.5 | 42789.35 | -26080.85 | -60.95% | 32696.87 | -15988.37 | -48.9% | 1. Relay tripped at 3:50 Am on 01/30 and auto reclosed in minutes | 1. SR080186
Sunset B | MA | 16074.25 | 29669.2 | -13594.95 | -45.82% | 32307.32 | -16233.07 | -50.25% | 1. Relay tripped at 3:50 Am on 01/30 and auto reclosed in minutes | 1. SR080187
Woodchuck | MA | 33788 | 71556.68 | -37768.68 | -52.78% | 96097.7 | -62309.7 | -64.84%

## Feb
38 DN |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2903046.4967 | 3704325.05 | -801278.5533 | -21.63% | 2914295.61 | -11249.1133 | -0.386%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 117799.5 | 104011.7 | 13787.8 | 13.26% | 147623 | -29823.5 | -20.2% | 1. Inverter 25 tripped offline on 02/04/2024 at 13:30 & continued through out the month. 2. Inverter 9 & 29 starts late for the production throught the month. | 1. SR080716
Barton Acres | MA | 108506 | 160669.9 | -52163.9 | -32.47% | 98180.31 | 10325.69 | 10.52% | 1. Inverter 2 Combiner box 5 tripped offline on 02/16/2024 at 12:00 & back online on 02/17/2024 at 13:45. | 1.SR081069
Bowden | MA | 240002 | 273981.2 | -33979.2 | -12.4% | 216873.8 | 23128.2 | 10.66%
Blair Wire Village | MA | 112415 | 166534.2 | -54119.2 | -32.5% | 108186.2 | 4228.8 | 3.909% | 1. SIte tripped offline on 02/21/2024 at 03:15 & back online at 08:40AM 2. Site tripped offline on 02/28/2024 at 11:15 & back online at 13:15 3.Site tripped offline on 02/29/2024 at 12:30 & back online at 15:00 | 1.SR081148 2.SR081408 3.SR081459
Boutilier | MA | 313554 | 390258.3 | -76704.3 | -19.65% | 269518.2 | 44035.8 | 16.34%
Cherry Valley | MA | 104151 | 163924.2 | -59773.2 | -36.46% | 104227 | -76 | -0.07292% | 1. Inverter 2 has intermittent trips on 02/16, 02/17,02/18, 02/19, 02/20 ,back online at 12:20 on 02/20/2024. 2. Inverter 2 tripped offline on 02/06/2024 at 10:40 & back online at 12:05. | 1.SR081049 2.SR080405
Cohasse | MA | 106564 | 153689.6 | -47125.6 | -30.66% | 135758.5 | -29194.5 | -21.5%
ISM Dighton Solar 2 | MA | 245737 | 268185.8 | -22448.8 | -8.371% | 226815.8 | 18921.2 | 8.342% | 1. Site was taken offline on 02/27/2024 from 08:45 to 11:15 for maintenance & 2 back online at 14:00 PM. 2. Inverter 2 is offline from 11:30 to 16:30 on 02/26/2024. | 1.PM3945 2.PM6580
Dudley River 1 | MA | 118831 | 138790 | -19959 | -14.38% | 109903.4 | 8927.6 | 8.123% | 1. Inverter 1 combiner 5 is offline on 02/08/2024 & back online at 12:45 PM on same day. 2.(A) Inverter 1 CB 4 & 5 tripped offline on 02/16/2024 at 13:30 & back online on 02/17/2024 at 16:30. 2.(B) Inverter 1 CB 5 tripped oflfine on 02/20/2024 at 08:00 & back online at 16:15. 3. Inverter 1 CB 5 tripped oflfine on 02/21/2024 at 08:00 & back online at 12:00. 4. Inverter 1 CB 4 tripped offline on 02/29/2024 at 12:45 & back online 03/01/2024 at 08:15. | 1. SR080854. 2. SR081071 3. SR081152 4. SR081467
Dudley River 2 | MA | 114866 | 138292.5 | -23426.5 | -16.94% | 104560.3 | 10305.7 | 9.856% | 1. Inverter 2 CB 4 is offline on 02/17/2024 & back online on 02/20/2024 at 15:15. 2.(A)Inverter 1 was offline on 02/24/2024 & back online at 10:45 on same day. 2.(B) Inverter 1 was offline on 02/25/2024 & back online at 11:45 on same day. | 1. SR081074. 2. SR081288
Dudley River 3 | MA | 128025 | 139249.9 | -11224.9 | -8.061% | 106013.9 | 22011.1 | 20.76%
Flint Pond | MA | 52890 | 75445.3 | -22555.3 | -29.9% | 47473.76 | 5416.24 | 11.41% | 1. SIte tripped offline on 02/19/2024 at 09:45 & back online at 11:15. | 1.SR081103
Incom | MA | 245273 | 327202 | -81929 | -25.04% | 263772.2 | -18499.2 | -7.013% | 1. Site tripped offline on 02/07/2024 at 12:15 & back online at 14:00 | 1.SR080830
JH | MA | 117284 | 160679.3 | -43395.3 | -27.01% | 129552.7 | -12268.7 | -9.47%
Ledeaux | MA | 107690 | 127152.8 | -19462.8 | -15.31% | 121695.2 | -14005.2 | -11.51%
Palombo A | MA | 242837.9967 | 319493.4 | -76655.4033 | -23.99% | 292221 | -49383.0033 | -16.9%
Palombo B | MA | 112113 | 151059 | -38946 | -25.78% | 101907 | 10206 | 10.02%
St Josephs Church | MA | 102403 | 161969.1 | -59566.1 | -36.78% | 115957.7 | -13554.7 | -11.69%
Sunset A | MA | 54854 | 80039.97 | -25185.97 | -31.47% | 46223.21 | 8630.79 | 18.67% | 1. SIte tripped offline on 03/16/2024 at 06:45 & back online at 08:00. | 1.SR081036
Sunset B | MA | 47906 | 62731.88 | -14825.88 | -23.63% | 45670.03 | 2235.97 | 4.896% | 1. SIte tripped offline on 02/16/2024 at 06:45 & back online at 08:00. 2. Site was taken offline by USNE on 02/15/2024 from 08:15 to 13:30. 3. Combiner Box 2 tripped offline on 02/16/2024 at 14:15 & back online on 02/21/2024 at 10:00. | 1.SR081037 2.SR080941 3.SR081070
Woodchuck | MA | 109345 | 140965 | -31620 | -22.43% | 122162.4 | -12817.4 | -10.49% | 1.Inverter 1 Combiner box 4 tripped offline on 02/03/2024 at 12:00 & back online at 14:35. | 1.SR080694

## Mar
38 DN |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3658511.95 | 3934430.86 | -275918.91 | -7.013% | 3957115.43 | -298603.48 | -7.546%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 172920.7 | 173166.5 | -245.8 | -0.1419% | 192369.2 | -19448.5 | -10.11% | 1. Inverter 25 is offline from 02/04/2024 at 13:30. Replaced DC relay board, inverter back online on 03/08 at 10:30am 2. Site tripped offline on 03/03 at 12:00pm and back online on 03/04 at 09:45am 3. Inverter 19 tripped offline on 03/04 at 13:15 and technicans replaced DC relay borads on inverter 2, 3, 9 and 19, all inverters back online around 12:30pm on 03/08. 4. Inverter 24 is offline from 03/24 and back online on 03/27 after replacing inverter | 1. SR080716 2. SR081535 3. SR081568 4. SR082715
Barton Acres | MA | 138888 | 160005 | -21117 | -13.2% | 142669.5 | -3781.5 | -2.651% | 1. Site was taken offline by technician on 03/19 between 09:45 to 11:45. | 1. PM2835
Bowden | MA | 290466 | 300297.9 | -9831.9 | -3.274% | 299687.8 | -9221.8 | -3.077% | 1. Inverters 1 and 2 taken offline by technician between 08:30 to 10:30 and inverters 3 and 4 in between 10;30 to 12:25 | 1. PM4466
Blair Wire Village | MA | 144173 | 169032.1 | -24859.1 | -14.71% | 150008.2 | -5835.2 | -3.89% | 1. Site was offline on 03/19 between 10:00 to 13:00 2. Site was taken offline by technician on 03/21 between 09:45 to 10:33 | 2. PM8461
Boutilier | MA | 409488 | 411646.7 | -2158.7 | -0.5244% | 391645.3 | 17842.7 | 4.556% | 1. Site was taken offline by techniciand on 03/13 between 12:45 to 13:15 and on 03/14 between 09:45 to 11:30 | 1. PM3412
Cherry Valley | MA | 144004 | 164213.5 | -20209.5 | -12.31% | 146986 | -2982 | -2.029% | 1. Inverter 1 was taken offline by technician on 03/4 between 09:00 to 09:45 | 1. PM2589
Cohasse | MA | 136999 | 155628.8 | -18629.8 | -11.97% | 171821.1 | -34822.1 | -20.27% | 1. Site tripped offline on 03/12 at 16:00 and back online on 03/13 at 07:30am | 1. SR081819
ISM Dighton Solar 2 | MA | 289566 | 298650.9 | -9084.9 | -3.042% | 304650.2 | -15084.2 | -4.951% | 1. Inverter 1 module 2 tripped offline on 03/04 at 09:00am and back online on 03/07 2. Inverter 2 modules 1 to 5 taken offline by technician on 03/08 between 08:45 to 09:30 and 11:00 to 12:00 | 1. SR081593 2. PM3945
Dudley River 1 | MA | 148530 | 150395.9 | -1865.9 | -1.241% | 156312.4 | -7782.4 | -4.979% | 1. Inverter 1 combiner box 1 tripped offline on 03/11 at 15:00 and back online on 03/12 at 10:15 2. Site was offline on 03/12 between 15:45 to 16:45 3. Inverter 1 Combiner box 5 tripped offline on 03/19 at 13:15 and back online on 03/20 | 1. SR081778 2. SR081820 3. SR082163
Dudley River 2 | MA | 142941 | 150367.4 | -7426.4 | -4.939% | 149077.2 | -6136.2 | -4.116% | 1. Site was offline on 03/12 between 15:45 to 16:45 2. Inverter 2 was taken offline by tech on 03/15 between 08:25 to 09:20 | 1. SR081823 2. PM2753
Dudley River 3 | MA | 148060 | 149649.6 | -1589.6 | -1.062% | 150723.9 | -2663.9 | -1.767% | 1. Site was offline on 03/12 between 15:45 to 16:45 | 1. SR081821
Flint Pond | MA | 68467 | 69574.02 | -1107.02 | -1.591% | 68567.49 | -100.49 | -0.1466%
Incom | MA | 302262 | 346048.9 | -43786.9 | -12.65% | 343121.6 | -40859.6 | -11.91% | 1. Inverter 1 was taken offline by technician on 03/13 between 11:00 to 13:15 | 1. PM4500
JH | MA | 138605 | 155762.2 | -17157.2 | -11.01% | 165508 | -26903 | -16.25% | 1. Site was taken offline by technician on 03/15 between 11:00 to 11:15 | 1. PM2635
Ledeaux | MA | 128389 | 136967.2 | -8578.2 | -6.263% | 160247 | -31858 | -19.88%
Palombo A | MA | 292802 | 326277.8 | -33475.8 | -10.26% | 363307 | -70505 | -19.41% | 1. Site was taken offline by technician on 03/19 between 10:20 to 12:25pm | 1. PM4502
Palombo B | MA | 146945 | 147883.3 | -938.3 | -0.6345% | 148307.9 | -1362.9 | -0.919%
St Josephs Church | MA | 143176 | 165178 | -22002 | -13.32% | 154868.1 | -11692.1 | -7.55% | 1. Site was offline by technician on 03/18 between 09:45 to 11:30 | 1. PM2755
Sunset A | MA | 66301 | 82488.21 | -16187.21 | -19.62% | 67170.38 | -869.38 | -1.294% | 1. Site was offline by technician on 03/18 between 11:15 to 17:15 and inverter 1 and 2 was taken offline in between 09:15 to 12:00pm | 1. PM2595
Sunset B | MA | 62243.25 | 70758.73 | -8515.48 | -12.03% | 66364.46 | -4121.21 | -6.21% | 1. Site was taken offline by technician on 03/14 between 10:45 to 12:00 and again site taken offline on 03/21 between 09:00 to 13:45 | 1. PM2693
Woodchuck | MA | 143286 | 150438.2 | -7152.2 | -4.754% | 163702.7 | -20416.7 | -12.47% | 1. Inverter 1 was taken offline by technician on 03/15 between 11:00 to 12:15 and site was taken offline on 03/19 between 09:15 to 10:00 | 1. PM2817

## Apr
38 DN |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 3828480.0599 | 4041167 | -212686.9401 | -5.263% | 4290961.43 | -462481.3701 | -10.78%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 220985.3 | 234779 | -13793.7 | -5.875% | 220814.1 | 171.2 | 0.07753%
Barton Acres | MA | 154260 | 159778.8 | -5518.8 | -3.454% | 163604.7 | -9344.7 | -5.712% | 1. Inverter 1 is offline on 04/12 and back online at 11:15am on 04/12 | 1. SR083350
Bowden | MA | 311418 | 314418.7 | -3000.7 | -0.9544% | 332611.5 | -21193.5 | -6.372%
Blair Wire Village | MA | 149056 | 169562.6 | -20506.6 | -12.09% | 167094.8 | -18038.8 | -10.8% | 1. Site tripped offline on 04/16 at 14:00 and back online on 04/17 at 08:00am and again site is offline from 02:00 am on 04/26 to 11:00am on 04/26 2. Inverter 2 was offline from 15:45 on 04/26 to 11:00am on 04/26 | 1. SR083515 2. SR083821
Boutilier | MA | 431826 | 447646.3 | -15820.3 | -3.534% | 449109.5 | -17283.5 | -3.848%
Cherry Valley | MA | 152661 | 165093.3 | -12432.3 | -7.53% | 163486 | -10825 | -6.621%
Cohasse | MA | 143028 | 148253.5 | -5225.5 | -3.525% | 173435.6 | -30407.6 | -17.53%
ISM Dighton Solar 2 | MA | 336392 | 321701.3 | 14690.7 | 4.567% | 338965.1 | -2573.1 | -0.7591%
Dudley River 1 | MA | 156406 | 156601.5 | -195.5 | -0.1248% | 167511.3 | -11105.3 | -6.63%
Dudley River 2 | MA | 150087 | 156204.2 | -6117.2 | -3.916% | 161407.4 | -11320.4 | -7.014%
Dudley River 3 | MA | 154781.0033 | 157088.3 | -2307.2967 | -1.469% | 163247.1 | -8466.0967 | -5.186%
Flint Pond | MA | 75671.5 | 70499.98 | 5171.52 | 7.335% | 78106.22 | -2434.72 | -3.117%
Incom | MA | 276036 | 363748.3 | -87712.3 | -24.11% | 348699 | -72663 | -20.84% | 1. Inverter C is derated 241kW compared to inverter D on 04/08/2024 from 08:00am to 11: 45am 2. Inverters A and B are tripped offline on 04/09 at 08:30 am and back online on 04/17 at 16:30 and Technician deenergised the site to troubleshoot inverters. | 1. SR083171 2. SR083244
JH | MA | 146209 | 157141.2 | -10932.2 | -6.957% | 171272.7 | -25063.7 | -14.63%
Ledeaux | MA | 136748 | 145052.6 | -8304.6 | -5.725% | 166011.9 | -29263.9 | -17.63%
Palombo A | MA | 309094.0066 | 321228.2 | -12134.1934 | -3.777% | 361541 | -52446.9934 | -14.51%
Palombo B | MA | 157158 | 140110.7 | 17047.3 | 12.17% | 170164.9 | -13006.9 | -7.644%
St Josephs Church | MA | 149164 | 168316.4 | -19152.4 | -11.38% | 165493.2 | -16329.2 | -9.867%
Sunset A | MA | 33136.5 | 46425.54 | -13289.04 | -28.62% | 77027.22 | -43890.72 | -56.98% | 1. Site is offline on 04/04 from 05:05 am to 14:35 2. Site was deenergised by technician to change transformer taps. 3. Site is offline from 04/17 to 05/02 due to planned utility outage | 1. SR083058 2. SR083456 3. SR082333
Sunset B | MA | 30996.75 | 36795.88 | -5799.13 | -15.76% | 76102.09 | -45105.34 | -59.27% | 1. Site is offline on 04/04 from 05:05 am to 14:35 2. Site was deenergised by technician to change transformer taps. 3. Site is offline from 04/17 to 05/02 due to planned utility outage | 1. SR083057 2. SR083456 3. SR082334
Woodchuck | MA | 153366 | 160720.7 | -7354.7 | -4.576% | 175256.1 | -21890.1 | -12.49%

## May
38 DN |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 4651336.2108 | 4676991.95 | -25655.7392 | -0.5486% | 4984299.77 | -332963.5592 | -6.68%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 223100 | 257891.6 | -34791.6 | -13.49% | 260430.1 | -37330.1 | -14.33% | 1. Inverter 30 is offline from 07:00AM on 05/10 and back online at 07:00AM on 05/11, inverter is again offline from 07:00AM on 05/26 and back online at 07:00AM on 05/27. | 1. SR084567, SR085167
Barton Acres | MA | 187417.7174 | 184693 | 2724.7174 | 1.475% | 197279.1 | -9861.3826 | -4.999% | 1. Site is offline from 14:09 on 05/31 and back online at 09:59 AM on 06/01. | 1. SR085384
Bowden | MA | 383942 | 382128.5 | 1813.5 | 0.4746% | 385038.1 | -1096.1 | -0.2847%
Blair Wire Village | MA | 169654 | 193455.4 | -23801.4 | -12.3% | 193182.1 | -23528.1 | -12.18% | 1. Site tripped offline at 14:45 on 05/05 and back online at 08:15AM on 05/06. 2. Site tripped offline at 15:30 on 05/20 and back online at on 09:45AM on 05/21. 3. Site tripped offline at 09:15AM to 12:30PM on 05/23. 4. Site tripped offline at 23:15 on 05/24 and back online at 10:00AM on 05/25 and site again is offline from 12:30AM to 09:00AM on 05/26. 5. Site offline from 09:00AM to 10:45AM on 05/28. 6. Site is offline from 04:45AM to 13:15 on 05/31 | 1. SR084276 2. SR084919 3. SR085062 4. SR085145 5. SR085210 6. SR085339
Boutilier | MA | 501700 | 487837.1 | 13862.9 | 2.842% | 541550.9 | -39850.9 | -7.359% | 1. Inverter D is offline from 05:45AM on 05/28. | 1. SR085297
Cherry Valley | MA | 176376 | 184033 | -7657 | -4.161% | 194395 | -18019 | -9.269%
Cohasse | MA | 169138 | 164177.1 | 4960.9 | 3.022% | 193723.8 | -24585.8 | -12.69%
ISM Dighton Solar 2 | MA | 375589 | 358722.2 | 16866.8 | 4.702% | 396437.7 | -20848.7 | -5.259%
Dudley River 1 | MA | 183734 | 185905 | -2171 | -1.168% | 194566 | -10832 | -5.567%
Dudley River 2 | MA | 177414 | 182193.7 | -4779.7 | -2.623% | 185537.3 | -8123.3 | -4.378%
Dudley River 3 | MA | 182698.9967 | 181487.7 | 1211.2967 | 0.6674% | 188053.7 | -5354.7033 | -2.847%
Flint Pond | MA | 86225 | 71405.17 | 14819.83 | 20.75% | 93130.7 | -6905.7 | -7.415%
Incom | MA | 408907 | 424321.8 | -15414.8 | -3.633% | 396541.4 | 12365.6 | 3.118% | 1. Inverter A is derated approximately 300kW on 05/14 and resolved on 05/15. | 1. SR084703
JH | MA | 178088 | 178513.9 | -425.9 | -0.2386% | 192698.1 | -14610.1 | -7.582%
Ledeaux | MA | 166603 | 174417.9 | -7814.9 | -4.481% | 189198.9 | -22595.9 | -11.94%
Palombo A | MA | 363753.9934 | 357461.3 | 6292.6934 | 1.76% | 398271 | -34517.0066 | -8.667% | 1. Site is having brief outage from 13:50 to 14:10 on 05/14. | 1. SR084697
Palombo B | MA | 183170 | 154569.7 | 28600.3 | 18.5% | 205328.2 | -22158.2 | -10.79% | 1. Site is having brief outage from 13:50 to 14:10 on 05/14. | 2. SR084696
St Josephs Church | MA | 182002.0033 | 191312.6 | -9310.5967 | -4.867% | 191319.1 | -9317.0967 | -4.87% | 1. Site is offline from 21:45 to 23:10 on 05/21. | 1. SR084987
Sunset A | MA | 85967.5 | 89017.66 | -3050.16 | -3.426% | 92881.88 | -6914.38 | -7.444%
Sunset B | MA | 81647 | 84768.12 | -3121.12 | -3.682% | 91766.09 | -10119.09 | -11.03%
Woodchuck | MA | 184209 | 188679.5 | -4470.5 | -2.369% | 202970.6 | -18761.6 | -9.244%

## Jun
38 DN |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 5038083.0326 | 5133216.42 | -95133.3874 | -1.853% | 5000154.52 | 37928.5126 | 0.7585%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 225023 | 294597 | -69574 | -23.62% | 245630.1 | -20607.1 | -8.389% | 1. Inverter 9 was offline from 07:00AM on 06/04 and back online at 10:45AM on 06/04 and also Inverter 9 offline from 07:00AM on 06/06 and back online at 09:45 on 06/06 2. Inverter 30 tripped offline from 14:15 on 06/04 and back onlin at 10:15AM on 06/28 | 1. SR085538 2. SR085561
Barton Acres | MA | 203632.2826 | 194911.7 | 8720.5826 | 4.474% | 199842.9 | 3789.3826 | 1.896% | 1. Site was back online from 09:45AM on 06/01 2. Site experienced brief outage from 17:45 to 17:56 on 06/19 3. Relay stopped communicating from 18:22 on 06/19 | 1. SR085384 2. SR086450 3. SR086457
Bowden | MA | 414745 | 410030.8 | 4714.2 | 1.15% | 397783 | 16962 | 4.264% | 1. Site was offline from 12:15 on 06/14 and back online at 13:30 on 06/14 and again site offline from 15:30 on 06/22 and back online at 18:30 on 06/22 | 1. SR086247
Blair Wire Village | MA | 200447 | 207116.1 | -6669.1 | -3.22% | 198779.3 | 1667.7 | 0.839% | 1. Site was offline from 02:30AM on 06/03 and back online at 07:15AM on 06/03 2. Site was offline from 18:00 on 06/04 and back online at 09:30AM on 06/05 and again offline from 14:30 and back online at 16:30 on 06/05. | 1. SR085433 2. SR085563
Boutilier | MA | 544950 | 547089.6 | -2139.6 | -0.3911% | 548588.1 | -3638.1 | -0.6632% | 1. Inverter A was tripped offline from 07:30 on 06/13 and back online at 13:45 on 06/13 2. Inverter D was offline from 06/01 and back online on 06/12 | 1. SR086139 2. SR085297 ,SR085798
Cherry Valley | MA | 193353 | 191822.6 | 1530.4 | 0.7978% | 195979 | -2626 | -1.34%
Cohasse | MA | 187694 | 181260 | 6434 | 3.55% | 189453.3 | -1759.3 | -0.9286%
ISM Dighton Solar 2 | MA | 405711 | 407670.8 | -1959.8 | -0.4807% | 405850.7 | -139.7 | -0.03442% | 1. PE Inverter module 1.5 tripped offline from 17:15 on 06/04 and back online at 10:30AM on 06/06 2. Site was offline from 12:10AM tp 07:45AM on 06/13 3. Site was offline due to utility outage from 10:15AM on 06/14 and back online at 14:15 on 06/15. 3. Site was offline from 06:45AM on 06/27 and back online at 09:15AM on 06/27 | 1. SR085564 2. SR086111 3. SR086230 4. SR087022
Dudley River 1 | MA | 196072 | 205405.5 | -9333.5 | -4.544% | 199866.6 | -3794.6 | -1.899% | 1. Site was offline from 18:45 on 06/11 and back online at 06:45AM on 06/13 | 1. SR086056
Dudley River 2 | MA | 186963 | 202100.4 | -15137.4 | -7.49% | 190392.3 | -3429.3 | -1.801% | 1. Site was offline from 18:45 on 06/11 and back online at 06:45AM on 06/13 | 1. SR086032
Dudley River 3 | MA | 193519 | 200107.8 | -6588.8 | -3.293% | 193101.1 | 417.9 | 0.2164% | 1. Site was offline from 18:45 on 06/11 and back online at 06:45AM on 06/13 | 1. SR086037
Flint Pond | MA | 95286 | 78186.87 | 17099.13 | 21.87% | 93633.55 | 1652.45 | 1.765%
Incom | MA | 439967 | 457194.1 | -17227.1 | -3.768% | 393685.8 | 46281.2 | 11.76% | 1. Inverters A&B are derated to 80% from 06/27 2. Site offline due to planned outage start from 07:15AM on 06/06 and back online at 14:30 on 06/06 | 1. SR086971 2. SR084421
JH | MA | 189114 | 189169.2 | -55.2 | -0.02918% | 187798.5 | 1315.5 | 0.7005%
Ledeaux | MA | 175106 | 188057.8 | -12951.8 | -6.887% | 187069 | -11963 | -6.395%
Palombo A | MA | 404704.0033 | 401381.1 | 3322.9033 | 0.8279% | 385946 | 18758.0033 | 4.86%
Palombo B | MA | 205106 | 169757.9 | 35348.1 | 20.82% | 207998.2 | -2892.2 | -1.39%
St Josephs Church | MA | 195296.9967 | 209723.4 | -14426.4033 | -6.879% | 189931.5 | 5365.4967 | 2.825% | 1. Inverter 2 was derating approximately 280 - 300 kW from 06/02 and resolved on 06/03 | 1. SR085421
Sunset A | MA | 93764.5 | 94982.74 | -1218.24 | -1.283% | 94088.88 | -324.38 | -0.3448% | 1. Utility planned outage start from 06/04 and back online at 08:45 on 06/05 | 1. SR084798
Sunset B | MA | 89101.25 | 98109.91 | -9008.66 | -9.182% | 92958.89 | -3857.64 | -4.15% | 1. Utility planned outage start from 06/04 and back online at 08:45 on 06/05 | 1. SR084799
Woodchuck | MA | 198528 | 204541.1 | -6013.1 | -2.94% | 201777.8 | -3249.8 | -1.611%

## Jul
38 DN |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 4754265.9967 | 4889018.35 | -134752.3533 | -2.756% | 5205397.07 | -451131.0733 | -8.667%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 228805.5 | 300659.9 | -71854.4 | -23.9% | 258461.8 | -29656.3 | -11.47%
Barton Acres | MA | 206045 | 202434.1 | 3610.9 | 1.784% | 209880.4 | -3835.4 | -1.827% | 1.Site was offline from 19:15 of 7/16 to 09:45AM of 7/17 | 1.SR087795
Bowden | MA | 402694 | 402514.3 | 179.7 | 0.04464% | 403575.3 | -881.3 | -0.2184% | 1.Site was offline from 03:47AM to 07:30AM on 7/12 | 1.SR087607
Blair Wire Village | MA | 191619 | 198267.5 | -6648.5 | -3.353% | 201927.5 | -10308.5 | -5.105%
Boutilier | MA | 539456 | 515865.5 | 23590.5 | 4.573% | 576146.2 | -36690.2 | -6.368%
Cherry Valley | MA | 179659 | 189584.3 | -9925.3 | -5.235% | 206366 | -26707 | -12.94%
Cohasse | MA | 173632 | 170023.8 | 3608.2 | 2.122% | 202694.9 | -29062.9 | -14.34%
ISM Dighton Solar 2 | MA | 378895 | 363256.1 | 15638.9 | 4.305% | 394151.3 | -15256.3 | -3.871% | 1.Inverter 1 Module 1 has multiple tripping events from 07/08 2.Site was offline from 04:45AM to 07:15AM on 7/13 and again site was offline from 14:15 to 15:45 on 7/29 | 1.SR087468 2.SR087634
Dudley River 1 | MA | 190017 | 203395.5 | -13378.5 | -6.578% | 203502.1 | -13485.1 | -6.627%
Dudley River 2 | MA | 180465 | 188550.7 | -8085.7 | -4.288% | 192924.9 | -12459.9 | -6.458%
Dudley River 3 | MA | 184594 | 185009.5 | -415.5 | -0.2246% | 195826.1 | -11232.1 | -5.736%
Flint Pond | MA | 89346 | 71133.05 | 18212.95 | 25.6% | 98164.02 | -8818.02 | -8.983%
Incom | MA | 401853 | 433308.5 | -31455.5 | -7.259% | 416485.6 | -14632.6 | -3.513%
JH | MA | 179742 | 180766.8 | -1024.8 | -0.5669% | 201953 | -22211 | -11%
Ledeaux | MA | 166263 | 181159.8 | -14896.8 | -8.223% | 198092.6 | -31829.6 | -16.07%
Palombo A | MA | 357375.9967 | 359261.5 | -1885.5033 | -0.5248% | 414569 | -57193.0033 | -13.8% | 1.Site was offline due to utility outage from 7/20 at 11:30AM and back online on 7/21 at 09:30AM | 1.SR087955
Palombo B | MA | 177890 | 156647.3 | 21242.7 | 13.56% | 218506.6 | -40616.6 | -18.59% | 1.Site was offline due to utility outage from 7/20 at 12:00PM and back online on 7/21 at 09:30AM | 1.SR087955
St Josephs Church | MA | 156805 | 199847.5 | -43042.5 | -21.54% | 201655.6 | -44850.6 | -22.24% | 1.Site was offline from 12:15 to 21:30 on 7/7 and again offline from 08:00 to 22:00 on 7/8 and again offline from 07:30 to 21:45 on 7/9 again site offline from 09:45 to 20:30 on 7/10 again site offline from 7/11 at 10:00 and back online at 07:45 on 7/12 | 1.SR087443
Sunset A | MA | 93225 | 97708.73 | -4483.73 | -4.589% | 98814.91 | -5589.91 | -5.657%
Sunset B | MA | 88999.5 | 92907.27 | -3907.77 | -4.206% | 97627.64 | -8628.14 | -8.838%
Woodchuck | MA | 186885 | 196716.7 | -9831.7 | -4.998% | 214071.6 | -27186.6 | -12.7%

## Aug
38 DN |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 4385096.75 | 4515229.03 | -130132.28 | -2.882% | 4808339.29 | -423242.54 | -8.802%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 206169.5 | 263651.7 | -57482.2 | -21.8% | 264475.3 | -58305.8 | -22.05%
Barton Acres | MA | 178930 | 180723.2 | -1793.2 | -0.9922% | 181468.1 | -2538.1 | -1.399% | 1.Site offline from 8/9 at 14:45 and back online at 08:45 on 8/10 | 1.SR088850
Bowden | MA | 356723 | 359152.2 | -2429.2 | -0.6764% | 392110.6 | -35387.6 | -9.025%
Blair Wire Village | MA | 174451 | 182467.3 | -8016.3 | -4.393% | 197145.4 | -22694.4 | -11.51%
Boutilier | MA | 489664 | 476799.1 | 12864.9 | 2.698% | 498149.7 | -8485.7 | -1.703%
Cherry Valley | MA | 166609 | 175604.3 | -8995.3 | -5.122% | 181160 | -14551 | -8.032%
Cohasse | MA | 154477 | 159019.2 | -4542.2 | -2.856% | 187522.9 | -33045.9 | -17.62%
ISM Dighton Solar 2 | MA | 376685 | 369618.1 | 7066.9 | 1.912% | 376887.9 | -202.9 | -0.05384% | 1.Inverter 2 module 3 tripped offline at 11:00AM on 8/1 back online on 8/7 2.Site offline from 10:00 to 10:45 and 12:00 to 12:30 on 8/9 3.Site offline from 14:35 to 15:00 on 8/10 again offline fro 17:20 to 17:50 on 8/10 4.Site offline from 07:45 to 13:15 on 8/18 | 1.SR088502 2.SR088824 3.SR088876 4.SR089209
Dudley River 1 | MA | 171452 | 146757.9 | 24694.1 | 16.83% | 198232.4 | -26780.4 | -13.51% | 1.Weather station stopped communicating from 8/6 at 21:45 back online on 8/7 at 06:45 and again lost communication from 8/21 back online on 8/25 | 1. SR088708
Dudley River 2 | MA | 163393 | 169048.7 | -5655.7 | -3.346% | 189073 | -25680 | -13.58% | 1.Inverter A is derating approximately 281kW on 8/17 | 1.SR089197
Dudley River 3 | MA | 156699 | 170843.5 | -14144.5 | -8.279% | 191489.6 | -34790.6 | -18.17% | 1.Inverter 2 offline from 8/10 to 8/13 | 1.SR088881
Flint Pond | MA | 82426 | 70678.77 | 11747.23 | 16.62% | 84965.07 | -2539.07 | -2.988%
Incom | MA | 366840 | 393436.5 | -26596.5 | -6.76% | 383875.8 | -17035.8 | -4.438%
JH | MA | 160100 | 170636.1 | -10536.1 | -6.175% | 183763 | -23663 | -12.88%
Ledeaux | MA | 146362 | 161338.3 | -14976.3 | -9.283% | 180042.2 | -33680.2 | -18.71%
Palombo A | MA | 353999 | 370497.6 | -16498.6 | -4.453% | 387151 | -33152 | -8.563% | 1.Site offline from 19:00 on 8/13 and back online on 8/14 at 08:15 | 1.SR088881
Palombo B | MA | 179265 | 158947.5 | 20317.5 | 12.78% | 188793.6 | -9528.6 | -5.047%
St Josephs Church | MA | 169269 | 187694.1 | -18425.1 | -9.817% | 180633.6 | -11364.6 | -6.292%
Sunset A | MA | 83293.5 | 91500.77 | -8207.27 | -8.97% | 85437.62 | -2144.12 | -2.51%
Sunset B | MA | 78206.75 | 80693.39 | -2486.64 | -3.082% | 84411.3 | -6204.55 | -7.35%
Woodchuck | MA | 170083 | 176120.8 | -6037.8 | -3.428% | 191551.2 | -21468.2 | -11.21%
s

## Sep
38 DN |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 3866375.0033 | 3966388.43 | -100013.4267 | -2.522% | 3980901.33 | -114526.3267 | -2.877%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA | 157254 | 196705.3 | -39451.3 | -20.06% | 225597.4 | -68343.4 | -30.29%
Barton Acres | MA | 168880 | 175298.2 | -6418.2 | -3.661% | 140392.9 | 28487.1 | 20.29%
Bowden | MA | 327000 | 326246.8 | 753.2 | 0.2309% | 322319 | 4681 | 1.452% | 1. Site is offline at 19:30 on 09/19/2024 and again back online on 06:30 on 09/20 | 1. SR090873
Blair Wire Village | MA | 154334 | 168994.2 | -14660.2 | -8.675% | 161463.3 | -7129.3 | -4.415% | 1. Meter Phase B voltages dropped to zero on 09/01/2024 , 09/02 & 09/03 which results in meter capturing loss than the inverter production. | 1. SR089809
Boutilier | MA | 429784 | 423810.2 | 5973.8 | 1.41% | 385394.2 | 44389.8 | 11.52%
Cherry Valley | MA | 147429 | 168227.5 | -20798.5 | -12.36% | 143770 | 3659 | 2.545%
Cohasse | MA | 138827 | 152828.6 | -14001.6 | -9.162% | 163508.2 | -24681.2 | -15.09%
ISM Dighton Solar 2 | MA | 309792 | 307845.1 | 1946.9 | 0.6324% | 332297.6 | -22505.6 | -6.773% | 1.Site tripped offline at 8:30 and later back online at 09:30 on 09/13/2024 but 7 modules were offline due to overheating later all equipments are back online 14:45 2.Inverter 1.1 to 1.5 modules tripped offline at 10:45am, later again tripped offline at 13:00 on 09/27/2024 and back online 11:30 on 09/28 and started late production at 12:00 on 0/29 3.Inverter 1.1 to 1.5 tripped offline at 09:15 and back online at 10:45 on 09/30/2024 | 1.SR090351 2.SR091328 3.SR091328
Dudley River 1 | MA | 155571 | 36979.19 | 118591.81 | 320.7% | 161685.7 | -6114.7 | -3.782% | 1.Weather station lost comms at 11:00 AM EDT from 09/06/2024 throughout the month | 1.SR088708
Dudley River 2 | MA | 149701 | 154776.3 | -5075.3 | -3.279% | 154788.4 | -5087.4 | -3.287%
Dudley River 3 | MA | 151205 | 153921.3 | -2716.3 | -1.765% | 156914.1 | -5709.1 | -3.638%
Flint Pond | MA | 71892.5 | 65412.86 | 6479.64 | 9.906% | 66054.31 | 5838.19 | 8.838%
Incom | MA | 333105 | 362632.8 | -29527.8 | -8.143% | 327934.8 | 5170.2 | 1.577% | 1. Relay tripped at 6:38AM and auto-closed at 6:43AM on 09/14/2024 | 1. SR090419
JH | MA | 147169 | 166443.8 | -19274.8 | -11.58% | 158187.1 | -11018.1 | -6.965%
Ledeaux | MA | 133552 | 148668.9 | -15116.9 | -10.17% | 151807.8 | -18255.8 | -12.03%
Palombo A | MA | 294232.0033 | 322933.2 | -28701.1967 | -8.888% | 343827 | -49594.9967 | -14.42%
Palombo B | MA | 148765 | 140696.8 | 8068.2 | 5.734% | 145892.9 | 2872.1 | 1.969%
St Josephs Church | MA | 147921 | 173153.1 | -25232.1 | -14.57% | 149535.9 | -1614.9 | -1.08% | 1. Inverter 1 tripped offline at 12:15 on 09/02 and back online at 09:45 on 09/03 | 1. SR089818
Sunset A | MA | 75366.5 | 86459.2 | -11092.7 | -12.83% | 66098.32 | 9268.18 | 14.02%
Sunset B | MA | 69857 | 73394.18 | -3537.18 | -4.819% | 65305.2 | 4551.8 | 6.97%
Woodchuck | MA | 154738 | 160960.9 | -6222.9 | -3.866% | 158127.2 | -3389.2 | -2.143%

## Oct
38 DN |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA
Barton Acres | MA
Bowden | MA
Blair Wire Village | MA
Boutilier | MA
Cherry Valley | MA
Cohasse | MA
ISM Dighton Solar 2 | MA
Dudley River 1 | MA
Dudley River 2 | MA
Dudley River 3 | MA
Flint Pond | MA
Incom | MA
JH | MA
Ledeaux | MA
Palombo A | MA
Palombo B | MA
St Josephs Church | MA
Sunset A | MA
Sunset B | MA
Woodchuck | MA

## Nov
38 DN |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA
Barton Acres | MA
Bowden | MA
Blair Wire Village | MA
Boutilier | MA
Cherry Valley | MA
Cohasse | MA
ISM Dighton Solar 2 | MA
Dudley River 1 | MA
Dudley River 2 | MA
Dudley River 3 | MA
Flint Pond | MA
Incom | MA
JH | MA
Ledeaux | MA
Palombo A | MA
Palombo B | MA
St Josephs Church | MA
Sunset A | MA
Sunset B | MA
Woodchuck | MA

## Dec
38 DN |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
6th St. | CA
Barton Acres | MA
Bowden | MA
Blair Wire Village | MA
Boutilier | MA
Cherry Valley | MA
Cohasse | MA
ISM Dighton Solar 2 | MA
Dudley River 1 | MA
Dudley River 2 | MA
Dudley River 3 | MA
Flint Pond | MA
Incom | MA
JH | MA
Ledeaux | MA
Palombo A | MA
Palombo B | MA
St Josephs Church | MA
Sunset A | MA
Sunset B | MA
Woodchuck | MA

## Sites
Portfolio: | 38 DN
Site DAS Name | Site | State | Update | DAS
6th St. | 6th St. | CA | AEF | PowerTrack
Barton Acres | Barton Acres | MA | AEF | PowerTrack
Bowden | Bowden | MA | AEF | PowerTrack
Blair Wire Village | Blair Wire Village | MA | AEF | PowerTrack
Boutilier | Boutilier | MA | AEF | PowerTrack
Cherry Valley | Cherry Valley | MA | AEF | PowerTrack
Cohasse | Cohasse | MA | AEF | PowerTrack
ISM Dighton Solar 2 | ISM Dighton Solar 2 | MA | AEF | PowerTrack
Dudley River 1 | Dudley River 1 | MA | AEF | PowerTrack
Dudley River 2 | Dudley River 2 | MA | AEF | PowerTrack
Dudley River 3 | Dudley River 3 | MA | AEF | PowerTrack
Flint Pond | Flint Pond | MA | AEF | PowerTrack
Incom | Incom | MA | AEF | PowerTrack
JH | JH | MA | AEF | PowerTrack
Ledeaux | Ledeaux | MA | AEF | PowerTrack
Palombo A | Palombo A | MA | AEF | PowerTrack
Palombo B | Palombo B | MA | AEF | PowerTrack
St Josephs Church | St Josephs Church | MA | AEF | PowerTrack
Sunset A | Sunset A | MA | AEF | PowerTrack
Sunset B | Sunset B | MA | AEF | PowerTrack
Woodchuck | Woodchuck | MA | AEF | PowerTrack