## Year to Date
City of Flagstaff |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 512042 | 120071.5 | 391970.5 | 326.4% | 0 | 512042 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: COF Aquaplex | AZ | 346270 | 0 | 346270 | 0% | 0 | 346270 | 0%
AZ: COF Sun Bear | AZ | 89034 | 76259.09 | 12774.91 | 16.75% | 0 | 89034 | 0%
AZ: COF Rio de Flag | AZ | 76738 | 43812.41 | 32925.59 | 75.15% | 0 | 76738 | 0%

## 1st Qtr
City of Flagstaff |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 239179 | 120071.5 | 119107.5 | 99.2% | 0 | 239179 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: COF Aquaplex | AZ | 73407 | 0 | 73407 | 0% | 0 | 73407 | 0%
AZ: COF Sun Bear | AZ | 89034 | 76259.09 | 12774.91 | 16.75% | 0 | 89034 | 0%
AZ: COF Rio de Flag | AZ | 76738 | 43812.41 | 32925.59 | 75.15% | 0 | 76738 | 0%

## 2nd Qtr
City of Flagstaff |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 369577 | 198780.92 | 170796.08 | 85.92% | 0 | 369577 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: COF Aquaplex | AZ | 145369 | 0 | 145369 |  |  | 145369
AZ: COF Sun Bear | AZ | 104939 | 100652.72 | 4286.28 | 4.258% |  | 104939
AZ: COF Rio de Flag | AZ | 119269 | 98128.2 | 21140.8 | 21.54% |  | 119269

## 3rd Qtr
City of Flagstaff |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 354671 | 251276.61 | 103394.39 | 41.15% | 0 | 354671 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: COF Aquaplex | AZ | 127494 | 0 | 127494 |  |  | 127494
AZ: COF Sun Bear | AZ | 87346 | 89057.59 | -1711.59 | -1.922% |  | 87346
AZ: COF Rio de Flag | AZ | 139831 | 162219.02 | -22388.02 | -13.8% |  | 139831

## 4th Qtr
City of Flagstaff |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: COF Aquaplex | AZ | 0 | 0 | 0 |  |  | 0
AZ: COF Sun Bear | AZ | 0 | 0 | 0 |  |  | 0
AZ: COF Rio de Flag | AZ | 0 | 0 | 0 |  |  | 0

## Jan
City of Flagstaff |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 72473 | 49976.5 | 22496.5 | 45.01% | 0 | 72473 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 21093 | 0 | 21093 | 0% | 0 | 21093 | 0%
AZ: COF Sun Bear | AZ | 26537 | 24317.09 | 2219.91 | 9.129% | 0 | 26537 | 0%
AZ: COF Rio de Flag | AZ | 24843 | 25659.41 | -816.41 | -3.182% | 0 | 24843 | 0% | 1. Inverter 3 was offline due to a blown 175 AMP fuse on 1/20. The technician replaced the fuse, and the inverter was back online on 02/05 | 1. SR080418

## Feb
City of Flagstaff |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 74421 | 41480 | 32941 | 79.41% | 0 | 74421 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 19187 | 0 | 19187 |  | 0 | 19187
AZ: COF Sun Bear | AZ | 29462 | 24923 | 4539 | 18.21% | 0 | 29462
AZ: COF Rio de Flag | AZ | 25772 | 16557 | 9215 | 55.66% | 0 | 25772 |  | 1. Inverter 3 is offline from 02/12 2. Weather station showing erroneous values | 1. SR080944 2. SR075221

## Mar
City of Flagstaff |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 92285 | 28615 | 63670 | 222.5% | 0 | 92285 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 33127 | 0 | 33127 |  | 0 | 33127
AZ: COF Sun Bear | AZ | 33035 | 27019 | 6016 | 22.27% | 0 | 33035
AZ: COF Rio de Flag | AZ | 26123 | 1596 | 24527 | 1537% | 0 | 26123 |  | 1. Inverter 3 is offline for whole month. 2. Weather station showing erroneous values | 1. SR080944 2. SR075221

## Apr
City of Flagstaff |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 113263 | 34848.95 | 78414.05 | 225% | 0 | 113263 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 45952 | 0 | 45952 |  | 0 | 45952
AZ: COF Sun Bear | AZ | 37075 | 33557.76 | 3517.24 | 10.48% | 0 | 37075
AZ: COF Rio de Flag | AZ | 30236 | 1291.19 | 28944.81 | 2242% | 0 | 30236 |  | 1. Weather station showing erroneous values throughout the month 2.Inverter 3 is offline for whole month. | 1.SR075221 2.SR080944

## May
City of Flagstaff |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 131197 | 72666.11 | 58530.89 | 80.55% | 0 | 131197 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 51600 | 0 | 51600 |  | 0 | 51600
AZ: COF Sun Bear | AZ | 36734 | 35504.09 | 1229.91 | 3.464% | 0 | 36734
AZ: COF Rio de Flag | AZ | 42863 | 37162.02 | 5700.98 | 15.34% | 0 | 42863 |  | 1. Weather station showing erroneous values throughout the month 2.Inverter 3 is back online from 05/14 | 1.SR075221 2.SR080944

## Jun
City of Flagstaff |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 125117 | 91265.86 | 33851.14 | 37.09% | 0 | 125117 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 47817 | 0 | 47817 |  | 0 | 47817
AZ: COF Sun Bear | AZ | 31130 | 31590.87 | -460.87 | -1.459% | 0 | 31130
AZ: COF Rio de Flag | AZ | 46170 | 59674.99 | -13504.99 | -22.63% | 0 | 46170 |  | 1. Weather station showing erroneous values thoroughout the month | 1. SR075221

## Jul
City of Flagstaff |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 119838 | 86397.03 | 33440.97 | 38.71% | 0 | 119838 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 45410 | 0 | 45410 |  | 0 | 45410
AZ: COF Sun Bear | AZ | 28923 | 29642 | -719 | -2.426% | 0 | 28923 |  | 1. Inverter 2 is underperforming approximately 60kW compared to its peers from 07/10 and back to normal operation from 07/16. | 1. SR087561
AZ: COF Rio de Flag | AZ | 45505 | 56755.03 | -11250.03 | -19.82% | 0 | 45505 |  | 1. Inverter charting data does not appear to be valid. It is reporting negative production midday. Meter data does not align with this from 07/17 and resolved on 07/29 | 1. SR087810

## Aug
City of Flagstaff |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 111979 | 78449.19 | 33529.81 | 42.74% | 0 | 111979 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 40285 | 0 | 40285 |  | 0 | 40285
AZ: COF Sun Bear | AZ | 26754 | 26852.92 | -98.92 | -0.3684% | 0 | 26754
AZ: COF Rio de Flag | AZ | 44940 | 51596.27 | -6656.27 | -12.9% | 0 | 44940

## Sep
City of Flagstaff |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 122854 | 86430.39 | 36423.61 | 42.14% | 0 | 122854 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ | 41799 | 0 | 41799 |  | 0 | 41799
AZ: COF Sun Bear | AZ | 31669 | 32562.67 | -893.67 | -2.744% | 0 | 31669
AZ: COF Rio de Flag | AZ | 49386 | 53867.72 | -4481.72 | -8.32% | 0 | 49386

## Oct
City of Flagstaff |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ
AZ: COF Sun Bear | AZ
AZ: COF Rio de Flag | AZ

## Nov
City of Flagstaff |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ
AZ: COF Sun Bear | AZ
AZ: COF Rio de Flag | AZ

## Dec
City of Flagstaff |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: COF Aquaplex | AZ
AZ: COF Sun Bear | AZ
AZ: COF Rio de Flag | AZ

## Sites
Portfolio: | City of Flagstaff
Site DAS Name | Site | State | Update | DAS
AZ: COF Aquaplex | AZ: COF Aquaplex | AZ
AZ: COF Sun Bear | AZ: COF Sun Bear | AZ
AZ: COF Rio de Flag | AZ: COF Rio de Flag | AZ