## Year to Date
Renewable Properties |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 12223773.5 | 12439480.7131 | -215707.2131 | -1.734% | 14026318.114 | -1802544.614 | -12.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 1055939.5 | 956092.603 | 99846.897 | 10.44% | 977274.684 | 78664.816 | 8.049%
Bullis | NY | 6193429 | 6122895.249 | 70533.751 | 1.152% | 7159539.96 | -966110.96 | -13.49%
Rock Island | NY | 4974405 | 5360492.8611 | -386087.8611 | -7.202% | 5889503.47 | -915098.47 | -15.54%
Slayton A & B | NY | 0 | 0 | 0 |  | 0 | 0

## 1st Qtr
Renewable Properties |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1856728 | 1943166.5051 | -86438.5051 | -4.448% | 2565446.45 | -708718.45 | -27.63%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 229797.5 | 205242.876 | 24554.624 | 11.96% | 205591.58 | 24205.92 | 11.77%
Bullis | NY | 1076204 | 1128123.082 | -51919.082 | -4.602% | 1369235.95 | -293031.95 | -21.4%
Rock Island | NY | 550726.5 | 609800.5471 | -59074.0471 | -9.687% | 990618.92 | -439892.42 | -44.41%
Slayton A & B | NY | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Renewable Properties |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 5018618 | 5107908.111 | -89290.111 | -1.748% | 5594569.564 | -575951.564 | -10.29%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 418829 | 374872.33 | 43956.67 | 11.73% | 324449.804 | 94379.196 | 29.09%
Bullis | NY | 2515514 | 2470642.667 | 44871.333 | 1.816% | 2874886.41 | -359372.41 | -12.5%
Rock Island | NY | 2084275 | 2262393.114 | -178118.114 | -7.873% | 2395233.35 | -310958.35 | -12.98%
Slayton A & B | NY | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
Renewable Properties |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 5348427.5 | 5388406.097 | -39978.597 | -0.7419% | 5866302.1 | -517874.6 | -8.828%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 407313 | 375977.397 | 31335.603 | 8.334% | 447233.3 | -39920.3 | -8.926%
Bullis | NY | 2601711 | 2524129.5 | 77581.5 | 3.074% | 2915417.6 | -313706.6 | -10.76%
Rock Island | NY | 2339403.5 | 2488299.2 | -148895.7 | -5.984% | 2503651.2 | -164247.7 | -6.56%
Slayton A & B | NY | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Renewable Properties |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 0 | 0 | 0 |  |  | 0
Bullis | NY | 0 | 0 | 0 |  |  | 0
Rock Island | NY | 0 | 0 | 0 |  |  | 0
Slayton A & B | NY | 0 | 0 | 0 |  |  | 0

## Jan
Renewable Properties |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 149017 | 187289.57 | -38272.57 | -20.43% | 307259.67 | -158242.67 | -51.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 47147 | 40450.07 | 6696.93 | 16.56% | 41873.17 | 5273.83 | 12.59% | 1.Site tripped offline on 01/10/2024 at 01:31 & back online at 08:45 | 1.SR080111
Bullis | NY | 101870 | 146839.5 | -44969.5 | -30.62% | 265386.5 | -163516.5 | -61.61% | 1. Site tripped offline on 01/09/2024 at 14:30 & back online on 01/12/2024 at 17:00. 2. Inverter 2 tripped offline on 01/24/2024 at 14:00 & back online on 01/25 at 10:00 | 1. SR080100 2. SR080446
Rock Island | NY | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site came back online from 02/29/2024 | 1. SR079012
Slayton A & B | NY

## Feb
Renewable Properties |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 471859.25 | 471378.9931 | 480.2569 | 0.1019% | 868712.31 | -396853.06 | -45.68% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 73050.75 | 73781.2 | -730.45 | -0.99% | 55312.41 | 17738.34 | 32.07% | 1. Site tripped offline 2 times on 02/27 due to battery & SEL relay settings and got autoreclosed on same day. | 1. SR080479
Bullis | NY | 398240 | 396786.5 | 1453.5 | 0.3663% | 423644.5 | -25404.5 | -5.997% | 1. Site is underproducing due to broken modules. 23 modules being replaced | 1. SR080479
Rock Island | NY | 568.5 | 811.2931 | -242.7931 | -29.93% | 389755.4 | -389186.9 | -99.85% | 1. Site came back online from 02/29/2024 | 1. SR079138,SR079012
Slayton A & B | NY

## Mar
Renewable Properties |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 1235851.75 | 1284497.942 | -48646.192 | -3.787% | 1389474.47 | -153622.72 | -11.06% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 109599.75 | 91011.606 | 18588.144 | 20.42% | 108406 | 1193.75 | 1.101%
Bullis | NY | 576094 | 584497.082 | -8403.082 | -1.438% | 680204.95 | -104110.95 | -15.31% | 1. Site was offline from 07:00 to 15:15 on 03/20/2024. | 1.SR082491
Rock Island | NY | 550158 | 608989.254 | -58831.254 | -9.66% | 600863.52 | -50705.52 | -8.439% | 1. inverters 22,23,24,25,26,27, and 28 are underproducing from 12 pm to the end of the day on 03/11, 03/12 , 03/13, & continued from 03/24 throughout the month. | 1.SR081903
Slayton A & B | NY

## Apr
Renewable Properties |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 1380687.75 | 1419143.509 | -38455.759 | -2.71% | 1605825.812 | -225138.062 | -14.02% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 131405.25 | 110454.16 | 20951.09 | 18.97% | 118284.372 | 13120.878 | 11.09%
Bullis | NY | 644409 | 637554.677 | 6854.323 | 1.075% | 825963.54 | -181554.54 | -21.98%
Rock Island | NY | 604873.5 | 671134.672 | -66261.172 | -9.873% | 661577.9 | -56704.4 | -8.571% | 1. Site tripped offline at 09:50 on 04/11 & back online 04/12. 2.Inverters 22,23,24,25,26,27, and 28 are underproducing from 12 pm most of the days till 04/16 | 1.SR083325 2.SR081903
Slayton A & B | NY

## May
Renewable Properties |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 1816311.5 | 1852204.102 | -35892.602 | -1.938% | 1909320.652 | -93009.152 | -4.871% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 122900 | 107134.67 | 15765.33 | 14.72% | 49888.032 | 73011.968 | 146.4%
Bullis | NY | 966814 | 954212.39 | 12601.61 | 1.321% | 999785.87 | -32971.87 | -3.298%
Rock Island | NY | 726597.5 | 790857.042 | -64259.542 | -8.125% | 859646.75 | -133049.25 | -15.48% | 1. Site tripped offline at 06:15AM on 05/25 and back online on 05/28 at 08:40 AM. | 1.SR085147
Slayton A & B | NY

## Jun
Renewable Properties |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 1821618.75 | 1836560.5 | -14941.75 | -0.8136% | 2079423.1 | -257804.35 | -12.4% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 164523.75 | 157283.5 | 7240.25 | 4.603% | 156277.4 | 8246.35 | 5.277%
Bullis | NY | 904291 | 878875.6 | 25415.4 | 2.892% | 1049137 | -144846 | -13.81% | 1. Site tripped offline from 22:45 on 06/05 and back online at 08:30 on 06/06 2. Inverters 2,20,21 are underperforming compared to its peers 10 kW each and resolved on 06/27. | 1. SR085608 2. SR086331
Rock Island | NY | 752804 | 800401.4 | -47597.4 | -5.947% | 874008.7 | -121204.7 | -13.87% | 1. Inverter 23 is started to overheat and underperforming 40kW from 10:00AM on 06/17 and resolved on 06/18. 2. Site tripped offline from 02:00AM on 06/24 and back online at 07:30 on 06/25 | 1. SR086327 2. SR086819
Slayton A & B | NY

## Jul
Renewable Properties |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 2077427 | 2106041 | -28614 | -1.359% | 2252977.3 | -175550.3 | -7.792% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 141198 | 129239 | 11959 | 9.253% | 163816.3 | -22618.3 | -13.81%
Bullis | NY | 1063971.5 | 1030113 | 33858.5 | 3.287% | 1120156 | -56184.5 | -5.016% | 1.Inverter 8 has started to derate by approximately 25 kW and also inverter having some rapid tripping events during high irradiance from 07/08. 2.Site tripped offline at 15:00PM on 07/15 and back online at 16:45PM on 07/15. | 1.SR087484 2.SR087726
Rock Island | NY | 872257.5 | 946689 | -74431.5 | -7.862% | 969005 | -96747.5 | -9.984% | 1.Inverter 1 offline from 07/02 and back online on 07/25. | 1.SR087306,SR088250
Slayton A & B | NY

## Aug
Renewable Properties |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 1682098 | 1676510.697 | 5587.303 | 0.3333% | 1992699 | -310601 | -15.59% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 145570 | 134298.697 | 11271.303 | 8.393% | 152692 | -7122 | -4.664%
Bullis | NY | 802772 | 784268 | 18504 | 2.359% | 997314 | -194542 | -19.51% | 1. Site tripped offline at 15:30 on 08/17 and was re-energized at 09:00 on 08/18. Site was offline from morning and back online at 12:00PM on 08/19 2. Inverters started late for production throughout the month. Technician updated the ISO parameters and resolved the issue on 08/28 | 1. SR089200 2. SR089393
Rock Island | NY | 733756 | 757944 | -24188 | -3.191% | 842693 | -108937 | -12.93% | 1. Inverter 24 had tripping event on 08/12,08/15 and was offline from 08/17. Technician replaced connector and inverter is back online at 08:30 on 08/22 | 1. SR088921
Slayton A & B | NY

## Sep
Renewable Properties |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 1588902.5 | 1605854.4 | -16951.9 | -1.056% | 1620625.8 | -31723.3 | -1.957% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 120545 | 112439.7 | 8105.3 | 7.209% | 130725 | -10180 | -7.787% | 1.Inverters 1,5 are offline from 9/20 and back online on 9/21 and also inveretrs 3,4,6,7 are offline from 9/20 back online on 9/22 | 1.SR090992
Bullis | NY | 734967.5 | 709748.5 | 25219 | 3.553% | 797947.6 | -62980.1 | -7.893%
Rock Island | NY | 733390 | 783666.2 | -50276.2 | -6.416% | 691953.2 | 41436.8 | 5.988% | 1.Inverter 17 tripped offline at 07:30 on 9/7 and backonline at 12:30 on 9/20 2.Inverter 15 derating by 30 kW. Inverter 16 derating by 40 kW. Inverter 19 derating by 25 kW. Inverter 20 derating by 5 kW. | 1.SR090012 2. SR090011
Slayton A & B | NY

## Oct
Renewable Properties |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA
Bullis | NY
Rock Island | NY
Slayton A & B | NY

## Nov
Renewable Properties |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA
Bullis | NY
Rock Island | NY
Slayton A & B | NY

## Dec
Renewable Properties |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA
Bullis | NY
Rock Island | NY
Slayton A & B | NY

## Sites
Portfolio: | Renewable Properties
Site DAS Name | Site | State | Update | DAS
60 Cedar Swamp Rd. (Renewable Properties) | Cedar Swamp Rd | MA | AEF | PowerTrack
Bullis | Bullis | NY |  | PowerTrack
Rock Island NY (Renew Prop) | Rock Island | NY | AEF | PowerTrack
Lockport - Slayton A & B | Slayton A & B | NY |  | PowerTrack