## Year to Date
CITI |  |  | PPA Modeled Output | Production VS Acual | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 6069138.76 | 6310607.78 | 96.17% | 6306600.923 | -237462.163 | -3.765% | 6495654.202 | -426515.442 | -6.566%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 181280.25 | 180419.48 | 100.5% | 178633 | 2647.25 | 1.482% | 186240.808 | -4960.558 | -2.664%
CA: Antioch MC CUP - Citi | CA | 629430 | 603657.35 | 104.3% | 597628 | 31802 | 5.321% | 652322.291 | -18801.31 | -2.882%
CA: Clovis - Citi | CA | 258457 | 249205 | 103.7% | 240600 | 17857 | 7.422% | 148306.958 | 37638.94 | 25.38%
CA: Elk Grove MOB - Citi | CA | 395951 | 391143.5 | 101.2% | 387271 | 8680 | 2.241% | 422039.133 | -16876.8 | -3.999%
CA: Elk Grove Promenade - Citi | CA | 212764.75 | 211252.5 | 100.7% | 209190.856 | 3573.894 | 1.708% | 231525.943 | -13241.198 | -5.719%
CA: Fresno Sequioa - Citi | CA | 418722 | 429254.14 | 97.55% | 425090 | -6368 | -1.498% | 460068.994 | -32740.3 | -7.116%
CA: Fresno MOB - Citi | CA | 153174.88 | 173897.84 | 88.08% | 172891 | -19716.12 | -11.4% | 162381.353 | -6133.546 | -3.777%
CA: Modesto Bangs - Citi | CA | 106316.5 | 109402.15 | 97.18% | 108924 | -2607.5 | -2.394% | 77946.852 | -1666.312 | -2.138%
CA: Napa Data Center - Citi | CA | 107517.88 | 124081.8 | 86.65% | 119610 | -12092.12 | -10.11% | 127893.566 | -13452.905 | -10.52%
CA: Petaluma MOB - Citi | CA | 164315 | 236501.38 | 69.48% | 275703 | -111388 | -40.4% | 217545.239 | -25903.39 | -11.91%
CA: Pleasanton Tec Ctr - Citi | CA | 344368.5 | 397952.74 | 86.54% | 393726 | -49357.5 | -12.54% | 404092.516 | -32875.356 | -8.136%
CA: Rancho Cordova - Citi | CA | 634561 | 578154.96 | 109.8% | 572800 | 61761 | 10.78% | 660917.44 | -17879.21 | -2.705%
CA: S Sacramento Wyndham - Citi | CA | 325214 | 337033.67 | 96.49% | 330702 | -5488 | -1.66% | 336117.109 | -1200.123 | -0.3571%
CA: Sacramento Point West - Citi | CA | 632110 | 643933.8 | 98.16% | 640387 | -8277 | -1.292% | 704794.887 | -48001.26 | -6.811%
CA: San Jose FHC - Citi | CA | 122374.75 | 139829.85 | 87.52% | 143317 | -20942.25 | -14.61% | 140115.008 | -13919.124 | -9.934%
CA: San Jose MOB - Citi | CA | 176626 | 225146.84 | 78.45% | 227068 | -50442 | -22.21% | 227023.079 | -33809.864 | -14.89%
CA: Selma - Citi | CA | 125428.62 | 126530.67 | 99.13% | 125163 | 265.62 | 0.2122% | 141485.435 | -11115.291 | -7.856%
CA: Vacaville Hospital | CA | 795151.75 | 879333.11 | 90.43% | 874334 | -79182.25 | -9.056% | 907707.13 | -33523.387 | -3.693%
CA: Manteca - KP Manteca Hospital | CA | 285374.88 | 273877 | 104.2% | 283563.067 | 1811.813 | 0.6389% | 287130.461 | -6367.164 | -2.218%
Sacramento - KP South Sacramento HSP | CA

## 1st Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 3997407.76 | 3960868.14 | 100.9% | 3987723.821 | 9683.939 | 0.2428% | 4290441.327 | -293033.567 | -6.83%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 114367.75 | 115399.63 | 99.11% | 114257 | 110.75 | 0.09693% | 117533.717 | -3165.967 | -2.694%
CA: Antioch MC CUP - Citi | CA | 407599 | 382684.3 | 106.5% | 378862 | 28737 | 7.585% | 426400.31 | -18801.31 | -4.409%
CA: Clovis - Citi | CA | 169263.25 | 152182.5 | 111.2% | 146927 | 22336.25 | 15.2% | 131624.31 | 37638.94 | 28.6%
CA: Elk Grove MOB - Citi | CA | 253724 | 246151.5 | 103.1% | 243714 | 10010 | 4.107% | 270600.8 | -16876.8 | -6.237%
CA: Elk Grove Promenade - Citi | CA | 138337 | 134028.5 | 103.2% | 132731.356 | 5605.644 | 4.223% | 151578.198 | -13241.198 | -8.736%
CA: Fresno Sequioa - Citi | CA | 267893 | 267133.21 | 100.3% | 264542 | 3351 | 1.267% | 300633.3 | -32740.3 | -10.89%
CA: Fresno MOB - Citi | CA | 102206.13 | 107787.71 | 94.82% | 107041 | -4834.87 | -4.517% | 108339.676 | -6133.546 | -5.661%
CA: Modesto Bangs - Citi | CA | 68432.75 | 63424.51 | 107.9% | 63171 | 5261.75 | 8.329% | 70099.062 | -1666.312 | -2.377%
CA: Napa Data Center - Citi | CA | 69031.88 | 78540.47 | 87.89% | 75905 | -6873.12 | -9.055% | 82484.785 | -13452.905 | -16.31%
CA: Petaluma MOB - Citi | CA | 148819.5 | 130900.23 | 113.7% | 174082 | -25262.5 | -14.51% | 174722.89 | -25903.39 | -14.83%
CA: Pleasanton Tec Ctr - Citi | CA | 229990.5 | 252333.64 | 91.15% | 249546 | -19555.5 | -7.836% | 262865.856 | -32875.356 | -12.51%
CA: Rancho Cordova - Citi | CA | 427880 | 377789.61 | 113.3% | 373634 | 54246 | 14.52% | 445759.21 | -17879.21 | -4.011%
CA: S Sacramento Wyndham - Citi | CA | 212055 | 211985.13 | 100% | 209458 | 2597 | 1.24% | 213255.123 | -1200.123 | -0.5628%
CA: Sacramento Point West - Citi | CA | 405840 | 404736.4 | 100.3% | 402651 | 3189 | 0.792% | 453841.26 | -48001.26 | -10.58%
CA: San Jose FHC - Citi | CA | 78955.5 | 90592.39 | 87.15% | 92852 | -13896.5 | -14.97% | 92874.624 | -13919.124 | -14.99%
CA: San Jose MOB - Citi | CA | 115879.25 | 146703.06 | 78.99% | 147955 | -32075.75 | -21.68% | 149689.114 | -33809.864 | -22.59%
CA: Selma - Citi | CA | 82293.5 | 77199.57 | 106.6% | 76362 | 5931.5 | 7.768% | 93408.791 | -11115.291 | -11.9%
CA: Vacaville Hospital | CA | 519252.25 | 553199.78 | 93.86% | 551443 | -32190.75 | -5.838% | 552775.637 | -33523.387 | -6.065%
CA: Manteca - KP Manteca Hospital | CA | 185587.5 | 168096 | 110.4% | 182590.465 | 2997.035 |  | 191954.664 | -6367.164
Sacramento - KP South Sacramento HSP | CA

## 2nd Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 2367366.72 | 2349739.64 | 100.8% | 2349739.64 | 17627.08 | 0.7502% | 48489.618 | 2318877.102 | 4782%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 66912.5 | 65019.85 | 102.9% | 64376 | 2536.5 | 3.94% | 68707.091 | -1794.591 | -2.612%
CA: Antioch MC CUP - Citi | CA | 221831 | 220973.05 | 100.4% | 218766 | 3065 | 1.401% | 225921.981 | -4090.981 | -1.811%
CA: Clovis - Citi | CA | 89193.75 | 97022.5 | 91.93% | 93673 | -4479.25 | -4.782% | 16682.648 | 72511.102 | 434.6%
CA: Elk Grove MOB - Citi | CA | 142227 | 144992 | 98.09% | 143557 | -1330 | -0.9265% | 151438.333 | -9211.333 | -6.083%
CA: Elk Grove Promenade - Citi | CA | 74427.75 | 77224 | 96.38% | 76459.5 | -2031.75 | -2.657% | 79947.745 | -5519.995 | -6.905%
CA: Fresno Sequioa - Citi | CA | 150829 | 162120.93 | 93.03% | 160548 | -9719 | -6.054% | 159435.694 | -8606.694 | -5.398%
CA: Fresno MOB - Citi | CA | 50968.75 | 66110.13 | 77.1% | 65850 | -14881.25 | -22.6% | 54041.677 | -3072.927 | -5.686%
CA: Modesto Bangs - Citi | CA | 37883.75 | 45977.64 | 82.4% | 45753 | -7869.25 | -17.2% | 7847.79 | 30035.96 | 382.7%
CA: Napa Data Center - Citi | CA | 38486 | 45541.33 | 84.51% | 43705 | -5219 | -11.94% | 45408.781 | -6922.781 | -15.25%
CA: Petaluma MOB - Citi | CA | 15495.5 | 105601.15 | 14.67% | 101621 | -86125.5 | -84.75% | 42822.349 | -27326.849 | -63.81%
CA: Pleasanton Tec Ctr - Citi | CA | 114378 | 145619.1 | 78.55% | 144180 | -29802 | -20.67% | 141226.66 | -26848.66 | -19.01%
CA: Rancho Cordova - Citi | CA | 206681 | 200365.35 | 103.2% | 199166 | 7515 | 3.773% | 215158.23 | -8477.23 | -3.94%
CA: S Sacramento Wyndham - Citi | CA | 113159 | 125048.54 | 90.49% | 121244 | -8085 | -6.668% | 122861.986 | -9702.986 | -7.897%
CA: Sacramento Point West - Citi | CA | 226270 | 239197.4 | 94.6% | 237736 | -11466 | -4.823% | 250953.627 | -24683.627 | -9.836%
CA: San Jose FHC - Citi | CA | 43419.25 | 49237.46 | 88.18% | 50465 | -7045.75 | -13.96% | 47240.384 | -3821.134 | -8.089%
CA: San Jose MOB - Citi | CA | 60746.75 | 78443.78 | 77.44% | 79113 | -18366.25 | -23.22% | 77333.965 | -16587.215 | -21.45%
CA: Selma - Citi | CA | 43135.12 | 49331.1 | 87.44% | 48801 | -5665.88 | -11.61% | 48076.644 | -4941.524 | -10.28%
CA: Vacaville Hospital | CA | 275899.5 | 326133.33 | 84.6% | 322891 | -46991.5 | -14.55% | 354931.493 | -79031.993 | -22.27%
CA: Manteca - KP Manteca Hospital | CA | 99787.38 | 105781 | 94.33% | 100972.602 | -1185.222 | -1.174% | 95175.797 | 4611.583
Sacramento - KP South Sacramento HSP | CA | 295635.72 | 0 | #DIV/0! | 0 | 295635.72 |  | 325782 | -30146.28

## 3rd Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Antioch MC CUP - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Clovis - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Elk Grove MOB - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Elk Grove Promenade - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Fresno Sequioa - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Fresno MOB - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Modesto Bangs - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Napa Data Center - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Petaluma MOB - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Pleasanton Tec Ctr - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Rancho Cordova - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: S Sacramento Wyndham - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Sacramento Point West - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: San Jose FHC - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: San Jose MOB - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Selma - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Vacaville Hospital | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Manteca - KP Manteca Hospital | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
Sacramento - KP South Sacramento HSP | CA

## 4th Qtr
CITI |  |  | PPA Modeled Output | Production VS Acual | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | %
CA: Antioch Deer Valley - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Antioch MC CUP - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Clovis - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Elk Grove MOB - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Elk Grove Promenade - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Fresno Sequioa - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Fresno MOB - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Modesto Bangs - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Napa Data Center - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Petaluma MOB - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Pleasanton Tec Ctr - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Rancho Cordova - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: S Sacramento Wyndham - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Sacramento Point West - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: San Jose FHC - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: San Jose MOB - Citi | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Selma - Citi | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Vacaville Hospital | CA | 0 |  | #DIV/0! | 0 | 0 |  | 0 | 0
CA: Manteca - KP Manteca Hospital | CA | 0 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
Sacramento - KP South Sacramento HSP | CA

## Jan
CITI |  |  | PPA Modeled Output | Production VS Acual | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1141760.88 | 909254.01 | 125.6% | 911851.348 | 229909.532 | 25.21% | 1228093.936 | -86333.056 | -7.03% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 35199.75 | 26934.83 | 130.7% | 26668 | 8531.75 | 31.99% | 36723.827 | -1524.077 | -4.15%
CA: Antioch MC CUP - Citi | CA | 107451 | 88103.5 | 122% | 87223 | 20228 | 23.19% | 116934.996 | -9483.996 | -8.11%
CA: Clovis - Citi | CA | 47404.25 | 30338 | 156.3% | 29290 | 18114.25 | 61.84% | 48625.771 | -1221.521 | -2.512% | 1.Inverter 1 tripped offline at 19:45 on 01/27 due to an arc protection fault and remained offline for through out the month. | 1.SR096073
CA: Elk Grove MOB - Citi | CA | 70088 | 55258.5 | 126.8% | 54711 | 15377 | 28.11% | 76608 | -6520 | -8.511%
CA: Elk Grove Promenade - Citi | CA | 39878 | 30505 | 130.7% | 30232.711 | 9645.289 | 31.9% | 44081.56 | -4203.56 | -9.536%
CA: Fresno Sequioa - Citi | CA | 72064.5 | 54436.21 | 132.4% | 53908 | 18156.5 | 33.68% | 83519.138 | -11454.638 | -13.71% | 1.Inverter 2 tripped offline at 18:35 on 12/31/24 due to an arc protection fault. The technician cleared the fault and re-energized the inverter, bringing it back online at 12:10 on 01/03/25. Inverter 2 again tripped offline at 18:45 on 01/07/25 and was being RMA'D. | 1.SR095212,SR095408 | SR095408
CA: Fresno MOB - Citi | CA | 30119.5 | 21917.91 | 137.4% | 21759 | 8360.5 | 38.42% | 33751.72 | -3632.22 | -10.76% | 1.Inverter 5's arc board is being RMA'd to prevent recurring trips. On 01/22, the technician installed the arc board, and then Inverter 5 is producing usually. | 1.SR095363
CA: Modesto Bangs - Citi | CA | 18323.25 | 12108.41 | 151.3% | 12105 | 6218.25 | 51.37% | 18407 | -83.75 | -0.455%
CA: Napa Data Center - Citi | CA | 18167.75 | 18607.37 | 97.64% | 18005 | 162.75 | 0.9039% | 22393.513 | -4225.763 | -18.87% | 1.Inverters 1, 2, 3, 5 and 6 experienced multiple tripping events. On 01/29, the technician arrived and found all inverters producing. Six new strings were installed for inverters 2, 3, and 5 to prevent further insulation faults. | 1.SR093544,SR094968 | SR094968
CA: Petaluma MOB - Citi | CA | 42798.5 | 45402.4 | 94.26% | 43691 | -892.5 | -2.043% | 42214.46 | 584.04 | 1.384% | 1.When the technician was on site to troubleshot Inverter 2 for its previous trip event on 12/17/24, he identified that it was underperforming and initiated an RMA. Inverter 2 has been in RMA since 01/03/25. | 1.SR094669,SR095487 | SR095487
CA: Pleasanton Tec Ctr - Citi | CA | 60053.5 | 61177.84 | 98.16% | 60279 | -225.5 | -0.3741% | 72294.92 | -12241.42 | -16.93% | 1.Inverter 9 tripped offline at 10:10 AM on 01/16/25 and self-resolved, Invereter 9 was back online at 08:30 PM on the same day. | 1.SR095637
CA: Rancho Cordova - Citi | CA | 138722 | 89789.61 | 154.5% | 88802 | 49920 | 56.21% | 146135.825 | -7413.825 | -5.073%
CA: S Sacramento Wyndham - Citi | CA | 61514 | 47416.43 | 129.7% | 46851 | 14663 | 31.3% | 56726.753 | 4787.247 | 8.439%
CA: Sacramento Point West - Citi | CA | 116857 | 90698.8 | 128.8% | 90230 | 26627 | 29.51% | 132201.526 | -15344.526 | -11.61%
CA: San Jose FHC - Citi | CA | 20174.5 | 22811.79 | 88.44% | 23381 | -3206.5 | -13.71% | 25499.26 | -5324.76 | -20.88% | 1.Meter current phase B is 10 amps lower than A and C and further troubleshooting will be needed. | 1.SR092732 , SR094546 | SR094546
CA: San Jose MOB - Citi | CA | 30984.25 | 37719.66 | 82.14% | 38042 | -7057.75 | -18.55% | 41140.37 | -10156.12 | -24.69% | 1.Inverter 1 has a history of multiple tripings and technician set the inverter to isolation mode and reenergized it. Then inverter 1 started producing as expected from 01/02. | 1.SR093725
CA: Selma - Citi | CA | 22758.75 | 15404.17 | 147.7% | 15194 | 7564.75 | 49.79% | 26945.834 | -4187.084 | -15.54%
CA: Vacaville Hospital | CA | 158667 | 130650.58 | 121.4% | 130413 | 28254 | 21.67% | 151623.242 | 7043.758 | 4.646%
CA: Manteca - KP Manteca Hospital | CA | 50535.38 | 29973 | 168.6% | 41066.637 | 9468.743 | 23.06% | 52266.221 | -1730.841 | -3.312%
Sacramento - KP South Sacramento HSP | CA

## Feb
CITI |  |  | PPA Modeled Output | Production VS Acual | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 1161890.88 | 1192644.33 | 97.42% | 1191822.5 | -29931.62 | -2.511% | 1241928.529 | -80037.649 | -6.445% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 32720 | 33837.7 | 96.7% | 33503 | -783 | -2.337% | 33108.406 | -388.406 | -1.173% | 1.The site offline on 02/26 at 12:45. On 02/28, a technician checked in and reported a blown fuse and reenergized the site. | 1.SR097891
CA: Antioch MC CUP - Citi | CA | 117003 | 111655.8 | 104.8% | 110541 | 6462 | 5.846% | 121440.242 | -4437.242 | -3.654%
CA: Clovis - Citi | CA | 49039.75 | 46787.5 | 104.8% | 45172 | 3867.75 | 8.562% | 45847.381 | 3192.369 | 6.963% | 1. Inverter 1 tripped offline at 16:45 from 01/27 due to arc protection fault and back online at 09:30 on 02/05. | 1.SR096073
CA: Elk Grove MOB - Citi | CA | 73432 | 74269 | 98.87% | 73534 | -102 | -0.1387% | 77096.73 | -3664.73 | -4.753%
CA: Elk Grove Promenade - Citi | CA | 39950 | 40582 | 98.44% | 40180.25 | -230.25 | -0.573% | 43579.704 | -3629.704 | -8.329%
CA: Fresno Sequioa - Citi | CA | 78020.5 | 83831.7 | 93.07% | 83019 | -4998.5 | -6.021% | 87819.042 | -9798.542 | -11.16% | 1. Inverter 2 tripped offline at 18:45 on 01/07 due to an arc protection fault and was RMA'd on 02/17. | 1.SR095408
CA: Fresno MOB - Citi | CA | 29859.88 | 33738.1 | 88.5% | 33456 | -3596.12 | -10.75% | 29656.131 | 203.749 | 0.687% | 1. Inverter 7 tripped offline at 19:35 on 02/14 due to an isolation fault and is now under RMA'd. | 1. SR097152
CA: Modesto Bangs - Citi | CA | 19801.5 | 20447.6 | 96.84% | 20348 | -546.5 | -2.686% | 20554.278 | -752.778 | -3.662%
CA: Napa Data Center - Citi | CA | 20347.88 | 22694.3 | 89.66% | 21965 | -1617.12 | -7.362% | 23987.7 | -3639.82 | -15.17% | 1. Inverter 1 tripped offline at 07:00 AM on 02/01 and back online at 16:55 on 02/02. It tripped offline again at 07:00 AM on 02/13 and back online at 12:40 on 02/14 due to an isolation fault. 2. Inverter 5 tripped offline at 07:00AM on 02/25 and back online at 16:55 on 02/25. | 1. SR096910 2. SR097715 | SR097715
CA: Petaluma MOB - Citi | CA | 45669.5 | 52699.23 | 86.66% | 50713 | -5043.5 | -9.945% | 52104.259 | -6434.759 | -12.35% | 1. When the technician was on site to troubleshot Inverter 2 for its previous trip event on 12/17/24, he identified that it was underperforming and initiated an RMA. Inverter 2 has been in RMA since 01/03/25. Inverter produced normally on 2/26 technician swapped with new inverter. 2.Inverter 14 has experienced multiple tripping events since 02/09 and is reporting 'PV abnormal input.' On 02/19, the technician removed the jumper bus bar and switched the input mode to 'independent' as per Chint's request, and it resumed normal operation. 3.Inverter 13 has reoccurring late starts, reporting insulation resistance low. This inverter has a history. On 02/26 technician swapped with new inverter and produced normallly. | 1. SR094669,SR095487 2. SR096553 3. SR92736 , SR095488 | SR095487 | SR096553 | SR92736 | SR095488
CA: Pleasanton Tec Ctr - Citi | CA | 64678 | 71770 | 90.12% | 70963 | -6285 | -8.857% | 73511.443 | -8833.443 | -12.02%
CA: Rancho Cordova - Citi | CA | 123056 | 116944 | 105.2% | 115658 | 7398 | 6.396% | 126414.863 | -3358.863 | -2.657%
CA: S Sacramento Wyndham - Citi | CA | 62431 | 63883.2 | 97.73% | 63122 | -691 | -1.095% | 61291.02 | 1139.98 | 1.86%
CA: Sacramento Point West - Citi | CA | 117073 | 122199 | 95.81% | 121584 | -4511 | -3.71% | 131537.929 | -14464.929 | -11% | 1. Inverter 5.4 tripped offline at 10:30 AM on 02/22 due to ARC protection and water in the wire box, so a new wire box is needed for replacement to get back the inverter. | 1. SR097653
CA: San Jose FHC - Citi | CA | 21935.75 | 25812.8 | 84.98% | 26457 | -4521.25 | -17.09% | 26911.372 | -4975.622 | -18.49% | 1.Meter current phase B is 10 amps lower than A and C and further troubleshooting will be needed. 2. The site was offline from 12:05 to 13:35 on 02/28 due to the technician being on site to work on the solar system. | 1. SR092732 , SR094546 2. SR094546 | SR094546 | SR094546
CA: San Jose MOB - Citi | CA | 34046.5 | 41783.9 | 81.48% | 42140 | -8093.5 | -19.21% | 43555.535 | -9509.035 | -21.83% | 1. Inverter 10 has a multiple tripings from 02/27 and technician set the inverter to isolation mode and reenergized it. 2. Inverter 2 is derating by 6 kW, likely due to overheating, and is now under RMA'd. 3. Inverter 12 may have a string down (~3 kW), and inverter 8 may have several strings down (~13 kW). | 1. SR097893 2. SR097777 3. SR097778 | SR097777 | SR097778
CA: Selma - Citi | CA | 23596.12 | 23766.7 | 99.28% | 23523 | 73.12 | 0.3108% | 27065.457 | -3469.337 | -12.82%
CA: Vacaville Hospital | CA | 157387 | 157634.8 | 99.84% | 157886 | -499 | -0.3161% | 160526.898 | -3139.898 | -1.956%
CA: Manteca - KP Manteca Hospital | CA | 51843.5 | 48307 | 107.3% | 58058.25 | -6214.75 | -10.7% | 55920.139 | -4076.639 | -7.29%
Sacramento - KP South Sacramento HSP | CA

## Mar
CITI |  |  | PPA Modeled Output | Production VS Acual | Q1 Production Vs PPA | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 1693756 | 1858969.8 | 91.11% | 100.5% | 1884049.973 | -190293.973 | -10.1% | 1820418.862 | -126662.862 | -6.958% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 46448 | 54627.1 | 85.03% | 99.11% | 54086 | -7638 | -14.12% | 47701.484 | -1253.484 | -2.628% | 1.Site was ofline from 03:45 pm on 02/26 to 11:50 am on 03/07. On 03/07 a technician has checked in site and they replaced the blown fuse and reenergized the site. | 1.SR097891
CA: Antioch MC CUP - Citi | CA | 183145 | 182925 | 100.1% | 106.5% | 181098 | 2047 | 1.13% | 188025.072 | -4880.072 | -2.595%
CA: Clovis - Citi | CA | 72819.25 | 75057 | 97.02% | 111.2% | 72465 | 354.25 | 0.4889% | 37151.158 | 35668.092 | 96.01% | 1.Inverter 1 is being RMA'D from 02/25 due to its communication and tripping issues.On 03/19,technician swapped the powerhead on inverter 1 .Inverter 1 is back online after technician troubleshoot the inverter. Additionally, technician completed Preventative Maintenance Inspection for the day (PM8554). 2. The weather station has been reporting erroneous values. Its graph shows continuous fluctuations throughout the day, indicating inconsistent readings. 3. The forecasted energy values are too low for the site. | 1.SR096008 2. SR099622 | SR099622
CA: Elk Grove MOB - Citi | CA | 110204 | 116624 | 94.5% | 103.1% | 115469 | -5265 | -4.56% | 116896.07 | -6692.07 | -5.725%
CA: Elk Grove Promenade - Citi | CA | 58509 | 62941.5 | 92.96% | 103.2% | 62318.395 | -3809.395 | -6.113% | 63916.934 | -5407.934 | -8.461% | 1. Inverter 1.4 is underperforming by 3 kW and is in independent mode | 1.SR099434
CA: Fresno Sequioa - Citi | CA | 117808 | 128865.3 | 91.42% | 100.3% | 127615 | -9807 | -7.685% | 129295.12 | -11487.12 | -8.884% | 1.Inverter 2 was being RMA'D from 02/17 due to repeated Arc Protection Faults causing it to drop offline.On 03/28, a technician has replaced Inverter 2 and it is online and producing from 01:00 pm on 03/28. | 1.SR095408
CA: Fresno MOB - Citi | CA | 42226.75 | 52131.7 | 81% | 94.82% | 51826 | -9599.25 | -18.52% | 44931.825 | -2705.075 | -6.02% | 1.Inverter 7 is being RMA'D from 02/17.On 03/25 technicians checked into the site and mentioned that Inverter 7 required further troubleshooting, as it was only producing about 3 kW. An technician later returned to replace Inverter 7, which is back online at 12:25pm on 03/25 and inverter 7 is underperforming by 30 kW from 03/25. | 1.SR097152, SR099432 | SR099432
CA: Modesto Bangs - Citi | CA | 30308 | 30868.5 | 98.18% | 107.9% | 30718 | -410 | -1.335% | 31137.784 | -829.784 | -2.665%
CA: Napa Data Center - Citi | CA | 30516.25 | 37238.8 | 81.95% | 87.89% | 35935 | -5418.75 | -15.08% | 36103.572 | -5587.322 | -15.48% | 1.Inverter 5 has experienced multiple tripping events throughout the month due to an insulation fault. 2. Inverters 1 and 2 tripped offline at 07:00 AM on 03/17 due to 'Insulation Resistance Low' and later self-resolved at 14:55 on 03/17. | 1. SR097715 2. SR098674 | SR098674
CA: Petaluma MOB - Citi | CA | 60351.5 | 32798.6 | 184% | 113.7% | 79678 | -19326.5 | -24.26% | 80404.171 | -20052.671 | -24.94% | 1. The phase B and C CTs of the meter have each been 40 amps lower than the phase A CT Since 03/21. There is a 5% variance between the meter and total inverter power. After the technician swapped the phase A and B CTs, it was confirmed to be a CT issue and need to be replace. Additionally, the meter has been reporting negative values since 03/27. | 1.SR098872, SR099542 | SR099542
CA: Pleasanton Tec Ctr - Citi | CA | 105259 | 119385.8 | 88.17% | 91.15% | 118304 | -13045 | -11.03% | 117059.493 | -11800.493 | -10.08% | 1. Inverter 3 tripped offline at 18:20 on 03/31 and reporting Insulation Resistance Low. | 1. SR099235
CA: Rancho Cordova - Citi | CA | 166102 | 171056 | 97.1% | 113.3% | 169174 | -3072 | -1.816% | 173208.522 | -7106.522 | -4.103% | 1. Inverter 5-3 was derated to a maximum of 13.8 kW on 03/17 and later self-resolved on 03/19. | 1. SR098684
CA: S Sacramento Wyndham - Citi | CA | 88110 | 100685.5 | 87.51% | 100% | 99485 | -11375 | -11.43% | 95237.35 | -7127.35 | -7.484%
CA: Sacramento Point West - Citi | CA | 171910 | 191838.6 | 89.61% | 100.3% | 190837 | -18927 | -9.918% | 190101.805 | -18191.805 | -9.57% | 1. Inverter 5.4 tripped offline at 10:30 AM on 02/22 due to ARC protection and water in the wire box, so a new wire box is needed for replacement to get back the inverter. 2. Inverter 1.3 is underperforming by about 10 kW compared to its peers due to a string being offline for an isolated module check. | 1. SR097653 2. SR098986 | SR098986
CA: San Jose FHC - Citi | CA | 36845.25 | 41967.8 | 87.79% | 87.15% | 43014 | -6168.75 | -14.34% | 40463.992 | -3618.742 | -8.943% | 1 The meter's phase B CT is 25 amps lower than the phase A and C CTs. There is a 3% variance between the meter and total inverter power. After the technician arrived, it was confirmed that the meter's CTs need to be replaced. | 1. SR098874, SR092732 | SR092732
CA: San Jose MOB - Citi | CA | 50848.5 | 67199.5 | 75.67% | 78.99% | 67773 | -16924.5 | -24.97% | 64993.209 | -14144.709 | -21.76% | 1. Inverter 10 experienced multiple trippings from 02/27. The technician set the inverter to isolation mode and re-energized it on 03/03. After the technician confirmed that the inverter settings were modified to temporarily improve conditions, it is now under RMA. 2. Inverter 2 is derating by 6 kW, likely due to overheating, and is now under RMA. Additionally, after the technician's arrival, the inverter has been offline at 12:25 PM on 03/18 and remains offline throughout the month. | 1. SR097893 2. SR097777, SR099041 | SR097777 | SR099041
CA: Selma - Citi | CA | 35938.63 | 38028.7 | 94.5% | 106.6% | 37645 | -1706.37 | -4.533% | 39397.5 | -3458.87 | -8.779%
CA: Vacaville Hospital | CA | 203198.25 | 264914.4 | 76.7% | 93.86% | 263144 | -59945.75 | -22.78% | 240625.497 | -37427.247 | -15.55% | 1. Inverters 2 to 4, 7, 8 , 10, 12, 13, 15, 20, 25 and 33 had shading issue during 7:00AM to 11:00AM. | 1. SR099626
CA: Manteca - KP Manteca Hospital | CA | 83208.62 | 89816 | 92.64% | 110.4% | 83465.578 | -256.958 | -0.3079% | 83768.304 | -559.684 | -0.6681%
Sacramento - KP South Sacramento HSP | CA

## Apr
CITI |  |  | PPA Modeled Output | Production VS Acual | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 2367366.72 | 2349739.64 | 100.8% | 2318877.102 | 48489.618 | 2.091% | 2530994.875 | -163628.155 | -6.465%
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA | 66912.5 | 65019.85 | 102.9% | 64376 | 2536.5 | 3.94% | 68707.091 | -1794.591 | -2.612%
CA: Antioch MC CUP - Citi | CA | 221831 | 220973.05 | 100.4% | 218766 | 3065 | 1.401% | 225921.981 | -4090.981 | -1.811%
CA: Clovis - Citi | CA | 89193.75 | 97022.5 | 91.93% | 93673 | -4479.25 | -4.782% | 16682.648 | 72511.102 | 434.6% | 1. Weather station showing erratic data with continuous fluctuations. On 04/29/25, tech checked DAS cabinet—24VDC present, connections good. Contacted AlsoEnergy; they confirmed data issues. Checked sensor terminal voltages and reported back. Sent emails with photos and readings. AlsoEnergy unable to ping sensors—recommended replacement. Tech contacting AlsoEnergy sales for irradiance and temp sensor quotes 2. Inverter 7 underperforming by ~4kW vs peers. On 04/29/25, tech found voltages and fuses OK. Called CPS—no site access. AlsoEnergy confirmed Inverter 7 producing ~2kW vs 8 & 9. Tech will follow up with CPS to check settings. 3. Forcasted values are too low compared to actual values it indicates there is an issue with forcasted values. | 1. SR099622, SR099968 2. SR100881, SR099968
CA: Elk Grove MOB - Citi | CA | 142227 | 144992 | 98.09% | 143557 | -1330 | -0.9265% | 151438.333 | -9211.333 | -6.083%
CA: Elk Grove Promenade - Citi | CA | 74427.75 | 77224 | 96.38% | 76459.5 | -2031.75 | -2.657% | 79947.745 | -5519.995 | -6.905% | 1. Inverter 1.4 is underperforming by 3 kW and is in independent mode, possibly relates to MPPTs being unbalanced. | 1. SR099434
CA: Fresno Sequioa - Citi | CA | 150829 | 162120.93 | 93.03% | 160548 | -9719 | -6.054% | 159435.694 | -8606.694 | -5.398%
CA: Fresno MOB - Citi | CA | 50968.75 | 66110.13 | 77.1% | 65850 | -14881.25 | -22.6% | 54041.677 | -3072.927 | -5.686% | 1.Inverter 7 is underperforming by 30 kW from 03/25. On 04/03/25, tech onsite to investigate canopy damage. One module visibly damaged; Inverter 7 underperforming by 30 kW but still online with no errors. Tech isolated string with bad module. Likely due to ongoing isolations—Ameresco to verify on return visit. | 1. SR099369, SR097152 & SR099432
CA: Modesto Bangs - Citi | CA | 37883.75 | 45977.64 | 82.4% | 45753 | -7869.25 | -17.2% | 7847.79 | 30035.96 | 382.7% | 1. Weather station has been reporting erroneous values since 04/07 at 13:45, with continuous fluctuations on the graph indicating inconsistent readings throughout the day. 2. Forcasted values are too low compared to actual values it indicates there is an issue with forcasted values. | 1. SR099861
CA: Napa Data Center - Citi | CA | 38486 | 45541.33 | 84.51% | 43705 | -5219 | -11.94% | 45408.781 | -6922.781 | -15.25% | 1.Inverter 4 was offline from 04/01 to 16:45 on 04/02 and started delayed for production at 15:15 on 04/27.This inverter has previously exhibited a pattern of delayed startups. | 1.SR098674,SR097715
CA: Petaluma MOB - Citi | CA | 15495.5 | 105601.15 | 14.67% | 101621 | -86125.5 | -84.75% | 42822.349 | -27326.849 | -63.81% | 1.Since 03/21, Phase B and C CTs have read 40A lower than Phase A, causing a 5% variance. The CT issue was confirmed after swapping, with replacement needed. The meter has reported negative values since 03/27. On 04/24, technicians found incorrect power factor values, affecting production readings. After swapping phases, the meter showed the correct value. 2.Inverters 5 and 14 are underperforming by 3 kW from 03/28 and are in independent mode 3.Weather station is currently reading inaccurately | 1.SR098872,SR099542 2.SR099433 3.SR100933
CA: Pleasanton Tec Ctr - Citi | CA | 114378 | 145619.1 | 78.55% | 144180 | -29802 | -20.67% | 141226.66 | -26848.66 | -19.01% | 1.Meter phase B CT is 170 amps lower than A and C phase CTs. There is a 7% variance, meter vs inv total power.Meter is being RMAD from 03/27 2.Inverters 1, 3, and 5 remained offline throughout the month. On 04/01, the technician indicated that further troubleshooting is required and the inverters will remain offline until necessary repairs are completed.Issue did not resolve | 1.SR098873 2.SR099231,SR099235,SR099339
CA: Rancho Cordova - Citi | CA | 206681 | 200365.35 | 103.2% | 199166 | 7515 | 3.773% | 215158.23 | -8477.23 | -3.94% | 1.Inverter 5-3 was derated to a maximum of 13.8 kW starting from 03/17. On 04/22, a technician inspected the site and found no abnormalities. The technician has contacted the inverter manufacturer for further assistance, as the issue persisted despite inverter troubleshooting. | 1.SR098684,SR100658
CA: S Sacramento Wyndham - Citi | CA | 113159 | 125048.54 | 90.49% | 121244 | -8085 | -6.668% | 122861.986 | -9702.986 | -7.897%
CA: Sacramento Point West - Citi | CA | 226270 | 239197.4 | 94.6% | 237736 | -11466 | -4.823% | 250953.627 | -24683.627 | -9.836% | 1.Inverter 5.4 remained offline throughout the month due to arc protection faults and water ingress in the wire box. A new wire box is needed, and further troubleshooting is required 2.. Inverter 1.3 is underperforming by about 10 kW compared to its peers due to a string being offline | 1.SR097653 2.SR098986
CA: San Jose FHC - Citi | CA | 43419.25 | 49237.46 | 88.18% | 50465 | -7045.75 | -13.96% | 47240.384 | -3821.134 | -8.089% | 1.The meter's phase B CT is 25 amps lower than the phase A and C CTs. There is a 3% variance between the meter and total inverter power. On 04/03, After the technician arrived, it was confirmed that the meter's CTs need to be replaced. | 1.SR098874
CA: San Jose MOB - Citi | CA | 60746.75 | 78443.78 | 77.44% | 79113 | -18366.25 | -23.22% | 77333.965 | -16587.215 | -21.45% | 1.Inverter 2 and under RMA for its derating issue caused by overheating and remains offline throughout the month. 2. Inverter 1 is underperforming by 3 kW and is independent mode from 03/07 | 1.SR099041 2.SR099435
CA: Selma - Citi | CA | 43135.12 | 49331.1 | 87.44% | 48801 | -5665.88 | -11.61% | 48076.644 | -4941.524 | -10.28% | 1. Inverters 3 and 4 are experiencing shading from morning to midday, while Inverter 1 is experiencing shading from midday to evening. | 1. SR101090
CA: Vacaville Hospital | CA | 275899.5 | 326133.33 | 84.6% | 322891 | -46991.5 | -14.55% | 354931.493 | -79031.993 | -22.27% | 1.Meter 2 phase A current is about 65 amps lower than phase B and C currents. 18 % variance in total inv power and meter power 2. Inverters 2 to 4, 7, 8 , 10, 12, 13, 15, 20, 25 and 33 had shading issue during 7:00AM to 11:00AM. 3.Multiple inverters are reporting lower-than-expected production, possibly due to incorrect system drawings or the need for a firmware update | 1.SR100428 2.SR099626 3.SR100428
CA: Manteca - KP Manteca Hospital | CA | 99787.38 | 105781 | 94.33% | 100972.602 | -1185.222 | -1.174% | 95175.797 | 4611.583 | 4.845% | 1. Weather station is heavily shaded until around 10am each morning.Dispatch is scheduled on 05/08. | 1.SR099704
Sacramento - KP South Sacramento HSP | CA | 295635.72 | N/A |  | N/A |  |  | 325782 | -30146.28 | -9.254% | 1.Inverter 10.1 was offline from 04/01 ,technician Opened up inverter and found wire box to be water damaged and corroded, requires further trubleshooting.on 04/16,technician replacd the wirebox for inverter.Inverter 10.1 was back online on 04/16 but production cannot be seen through DAS. 2.Inverter 1.3 was offline from 04/01 .Technician Opened combiner box and noticed visual signs of corrosion, causing the inverter to run on standby mode.Inverter 1.3 was being RMAD from 01/02.Inverter 1.3 was back online at 19:05 on 04/17 3.Inverter 5.3 was reporting production data in Locus portal.As mentioned by the technician the comms card is not plugged in.On 04/14,technician troubleshoot the inverter 5.3 and bringed it back online onsite on same day.it requires additional troubleshooting.Production cannot be seen through DAS 4.Inverter 6.4 was intermittently derating. The issue was resolved on 04/17 after a technician conducted troubleshooting and indicated that the derating was likely caused by nearby trees 5. 11.1, 11.2, and 11.3 were offline throughout the month.Production cannot be seen through DAS | 1.SR095613 2.SR090290,SR095613,SR098811 3.SR095613,SR098811 4.SR099818,SR100096 5.SR099875,SR095613

## May
CITI |  |  | PPA Modeled Output | Production VS Acual | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Jun
CITI |  |  | PPA Modeled Output | Production VS Acual | Q2 Production Vs PPA | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 89% | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Jul
CITI |  |  | PPA Modeled Output | Production VS Acual | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Aug
CITI |  |  | PPA Modeled Output | Production VS Acual | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Sep
CITI |  |  | PPA Modeled Output | Production VS Acual | Q3 Production Vs PPA | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 89% | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Oct
CITI |  |  | PPA Modeled Output | Production VS Acual | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Nov
CITI |  |  | PPA Modeled Output | Production VS Acual | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Dec
CITI |  |  | PPA Modeled Output | Production VS Acual | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | #DIV/0! | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual |  |  | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CA: Antioch Deer Valley - Citi | CA |  |  | #DIV/0!
CA: Antioch MC CUP - Citi | CA |  |  | #DIV/0!
CA: Clovis - Citi | CA |  |  | #DIV/0!
CA: Elk Grove MOB - Citi | CA |  |  | #DIV/0!
CA: Elk Grove Promenade - Citi | CA |  |  | #DIV/0!
CA: Fresno Sequioa - Citi | CA |  |  | #DIV/0!
CA: Fresno MOB - Citi | CA |  |  | #DIV/0!
CA: Modesto Bangs - Citi | CA |  |  | #DIV/0!
CA: Napa Data Center - Citi | CA |  |  | #DIV/0!
CA: Petaluma MOB - Citi | CA |  |  | #DIV/0!
CA: Pleasanton Tec Ctr - Citi | CA |  |  | #DIV/0!
CA: Rancho Cordova - Citi | CA |  |  | #DIV/0!
CA: S Sacramento Wyndham - Citi | CA |  |  | #DIV/0!
CA: Sacramento Point West - Citi | CA |  |  | #DIV/0!
CA: San Jose FHC - Citi | CA |  |  | #DIV/0!
CA: San Jose MOB - Citi | CA |  |  | #DIV/0!
CA: Selma - Citi | CA |  |  | #DIV/0!
CA: Vacaville Hospital | CA |  |  | #DIV/0!
CA: Manteca - KP Manteca Hospital | CA |  |  | #DIV/0!
Sacramento - KP South Sacramento HSP | CA

## Sites
Portfolio: | CITI
Site DAS Name | Site | State | Update | DAS
KP6 - Antioch Deer Valley - CN5701 | CA: Antioch Deer Valley - Citi | CA
KP6 - Antioch MC CUP - CN5701 | CA: Antioch MC CUP - Citi | CA
Clovis MOB | CA: Clovis - Citi | CA
Elk Grove MOB - CN73727 | CA: Elk Grove MOB - Citi | CA
Elk Grove Promenade - CN 6950 | CA: Elk Grove Promenade - Citi | CA
Fresno Sequioa Hospital | CA: Fresno Sequioa - Citi | CA
Fresno Medical Offices - CN7201 | CA: Fresno MOB - Citi | CA
Modesto Bangs MOB | CA: Modesto Bangs - Citi | CA
KP - Napa Data Center - CN2250 | CA: Napa Data Center - Citi | CA
Kaiser - Petaluma Medical Office - CN2001 | CA: Petaluma MOB - Citi | CA
Pleasanton PTC - Bldg B - CN470B | CA: Pleasanton Tec Ctr - Citi | CA
Rancho Cordova - Groundmount | CA: Rancho Cordova - Citi | CA
South Sacramento Wyndham CN6014 | CA: S Sacramento Wyndham - Citi | CA
Sacramento Point West MOB | CA: Sacramento Point West - Citi | CA
KP6 - San Jose FHC - CN6320 | CA: San Jose FHC - Citi | CA
KP6 - San Jose MOB - CN6310 | CA: San Jose MOB - Citi | CA
KP6 - Selma Medical Offices - CN8450 | CA: Selma - Citi | CA
Vacaville Hospital - CN6701 | CA: Vacaville Hospital | CA
Kaiser, KP6 - Manteca Hospital | CA: Manteca - KP Manteca Hospital | CA
KP6-South Sacramento Hospital | Sacramento - KP South Sacramento HSP | CA