## Year to Date
Catalyze |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 36714375.4258 | 42271097.963 | -5556722.5372 | -13.15% | 43204273.002 | -6489897.5762 | -15.02%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 743942.5 | 740507.48 | 3435.02 | 0.4639% | 848966.96 | -105024.46 | -12.37%
Adelanto - 1 Sheep Creek Road | CA | 4408458 | 3307369.873 | 1101088.127 | 33.29% | 1729663.74 | -142320.74 | -8.228%
Blackstone - 83 Federal Street | MA | 4948873.2022 | 5450484.7 | -501611.4978 | -9.203% | 5831804.8 | -882931.5978 | -15.14%
Charlton - 299 Worcester Road | MA | 411036.75 | 447080.27 | -36043.52 | -8.062% | 455160.38 | -44123.63 | -9.694%
Wareham - 8 Thatcher Drive | MA | 129187.9375 | 136124.548 | -6936.6105 | -5.096% | 139428.33 | -10240.3925 | -7.345%
West Yarmouth - 42 Mid Tech | MA | 115713.8443 | 130544.02 | -14830.1757 | -11.36% | 137069.167 | -21355.3227 | -15.58%
Harrison - 130 Union Street | NY | 156913.8125 | 196744.97 | -39831.1575 | -20.25% | 193787.11 | -36873.2975 | -19.03%
Staten Island - Ellis Storage | NY | 423065.25 | 382872.01 | 40193.24 | 10.5% | 447054.79 | -23989.54 | -5.366%
Amherst - 595 Schoelles Road | NY | 5981454 | 6730384 | -748930 | -11.13% | 6972975.1 | -991521.1 | -14.22%
Lancaster 1 - Gunnville Road | NY | 4391906 | 5188117 | -796211 | -15.35% | 5535387.7 | -1143481.7 | -20.66%
Lancaster 2 - Shisler Road | NY | 4845061 | 5545872.7 | -700811.7 | -12.64% | 6061553.8 | -1216492.8 | -20.07%
Fullerton - 200 W Orangethorpe | CA | 828721.5 | 860009.08 | -31287.58 | -3.638% | 948173.44 | -119451.94 | -12.6%
El Paso - 10500 Railroad Drive | TX | 567848.25 | 532299.83 | 35548.42 | 6.678% | 637061.5 | -69213.25 | -10.86%
Friona - 900 Millard Ave | TX | 449914.625 | 644238.13 | -194323.505 | -30.16% | 795608.5 | -345693.875 | -43.45%
Augusta - 13 York Farm Road | ME | 1121083.025 | 1313481.7 | -192398.675 | -14.65% | 1369597.4 | -248514.375 | -18.15%
Santa Ana - 1441 West | CA | 526580.8125 | 523244.491 | 3336.3215 | 0.6376% | 583050.953 | -56470.1405 | -9.685%
Jessup -7950 Oceano Ave | MD | 1644969.3501 | 1643215.012 | 1754.3381 | 0.1068% | 1925587.082 | -280617.7319 | -14.57%
TX: Fort Worth - 5200 Gold Spike Dr | TX | 1248879 | 4101136.728 | -2852257.728 | -69.55% | 4199066.01 | -2950187.01 | -70.26%
NY: Clifton Springs - Ontario 2 (21597) | NY | 2536602 | 2702570.9 | -165968.9 | -6.141% | 2457073.8 | 79528.2 | 3.237%
CA: Oxnard - 2600 Sakioka - System A | CA | 316571.8494 | 381593.5 | -65021.6506 | -17.04% | 362300.5 | -45728.6506 | -12.62%
CA: Oxnard - 2600 Sakioka - System B | CA | 4710.0503 | 349355.8 | -344645.7497 | -98.65% | 368582 | -363871.9497 | -98.72%
NY: Fonda - Montgomery 1 (21601) | NY | 912882.667 | 963851.221 | -50968.554 | -5.288% | 1205319.94 | -292437.273 | -24.26%

## 1st Qtr
Catalyze |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 8269951.4125 | 10417124.418 | -2147173.0055 | -20.61% | 10616412.677 | -2346461.2645 | -22.1%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 191319.25 | 182900.39 | 8418.86 | 4.603% | 210362.36 | -19043.11 | -9.053%
Adelanto - 1 Sheep Creek Road | CA | 1587343 | 1054002.04 | 533340.96 | 50.6% | 1729663.74 | -142320.74 | -8.228%
Blackstone - 83 Federal Street | MA | 1187392.8 | 1690571.4 | -503178.6 | -29.76% | 1569257.1 | -381864.3 | -24.33%
Charlton - 299 Worcester Road | MA | 106801.75 | 132014.25 | -25212.5 | -19.1% | 122312.49 | -15510.74 | -12.68%
Wareham - 8 Thatcher Drive | MA | 31580.9375 | 35070.628 | -3489.6905 | -9.95% | 36936.37 | -5355.4325 | -14.5%
West Yarmouth - 42 Mid Tech | MA | 24674.2087 | 29517.25 | -4843.0413 | -16.41% | 30853.657 | -6179.4483 | -20.03%
Harrison - 130 Union Street | NY | 45554.375 | 54840.16 | -9285.785 | -16.93% | 46386.63 | -832.255 | -1.794%
Staten Island - Ellis Storage | NY | 107385.75 | 111143.44 | -3757.69 | -3.381% | 101748.88 | 5636.87 | 5.54%
Amherst - 595 Schoelles Road | NY | 980445 | 1472428.2 | -491983.2 | -33.41% | 1409205.8 | -428760.8 | -30.43%
Lancaster 1 - Gunnville Road | NY | 994031 | 1280756.5 | -286725.5 | -22.39% | 1213137.7 | -219106.7 | -18.06%
Lancaster 2 - Shisler Road | NY | 1018864 | 1447535.4 | -428671.4 | -29.61% | 1320331.3 | -301467.3 | -22.83%
Fullerton - 200 W Orangethorpe | CA | 233829 | 248271.58 | -14442.58 | -5.817% | 267643.14 | -33814.14 | -12.63%
El Paso - 10500 Railroad Drive | TX | 336379.75 | 316832.5 | 19547.25 | 6.17% | 329629.5 | 6750.25 | 2.048%
Friona - 900 Millard Ave | TX | 261826.125 | 251426.81 | 10399.315 | 4.136% | 257416.8 | 4409.325 | 1.713%
Augusta - 13 York Farm Road | ME | 249165.875 | 430137 | -180971.125 | -42.07% | 370860.9 | -121695.025 | -32.81%
Santa Ana - 1441 West | CA | 149317.3412 | 147455.37 | 1861.9712 | 1.263% | 171259.21 | -21941.8688 | -12.81%
Jessup -7950 Oceano Ave | MD | 468523.25 | 510687.1 | -42163.85 | -8.256% | 480450.7 | -11927.45 | -2.483%
TX: Fort Worth - 5200 Gold Spike Dr | TX | 295518 | 1021534.4 | -726016.4 | -71.07% | 948956.4 | -653438.4 | -68.86%
NY: Clifton Springs - Ontario 2 (21597) | NY | 0 | 0 | 0 |  | 0 | 0
CA: Oxnard - 2600 Sakioka - System A | CA | 0 | 0 | 0 |  | 0 | 0
CA: Oxnard - 2600 Sakioka - System B | CA | 0 | 0 | 0 |  | 0 | 0
NY: Fonda - Montgomery 1 (21601) | NY | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Catalyze |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 15350624.4917 | 14934047.5259 | 416576.9658 | 2.789% | 16198515.895 | -847891.4033 | -5.234%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 346396 | 339259.99 | 7136.01 | 2.103% | 378908 | -32512 | -8.58%
Adelanto - 1 Sheep Creek Road | CA | 2238750 | 1160367.1549 | 1078382.8451 | 92.93% | 0 | 0
Blackstone - 83 Federal Street | MA | 1984775.1022 | 2078573.1 | -93797.9978 | -4.513% | 2479544.1 | -494768.9978 | -19.95%
Charlton - 299 Worcester Road | MA | 166857.25 | 170294.03 | -3436.78 | -2.018% | 202020.58 | -35163.33 | -17.41%
Wareham - 8 Thatcher Drive | MA | 55670.5625 | 57321.73 | -1651.1675 | -2.881% | 62112.17 | -6441.6075 | -10.37%
West Yarmouth - 42 Mid Tech | MA | 52233.1682 | 58112.09 | -5878.9218 | -10.12% | 63067.37 | -10834.2018 | -17.18%
Harrison - 130 Union Street | NY | 66585.875 | 77963.94 | -11378.065 | -14.59% | 86720.98 | -20135.105 | -23.22%
Staten Island - Ellis Storage | NY | 173769.875 | 148187.32 | 25582.555 | 17.26% | 205349.19 | -31579.315 | -15.38%
Amherst - 595 Schoelles Road | NY | 2774532 | 2888555.8 | -114023.8 | -3.947% | 3248259.3 | -473727.3 | -14.58%
Lancaster 1 - Gunnville Road | NY | 2095567 | 2148098.3 | -52531.3 | -2.445% | 2535076.7 | -439509.7 | -17.34%
Lancaster 2 - Shisler Road | NY | 2266198 | 2268322.7 | -2124.7 | -0.09367% | 2781914 | -515716 | -18.54%
Fullerton - 200 W Orangethorpe | CA | 355166.875 | 351640.1 | 3526.775 | 1.003% | 392681.7 | -37514.825 | -9.553%
El Paso - 10500 Railroad Drive | TX | 231468.5 | 215467.33 | 16001.17 | 7.426% | 307432 | -75963.5 | -24.71%
Friona - 900 Millard Ave | TX | 184410 | 176485.52 | 7924.48 | 4.49% | 263310.4 | -78900.4 | -29.96%
Augusta - 13 York Farm Road | ME | 496871.775 | 484552.8 | 12318.975 | 2.542% | 577791.8 | -80920.025 | -14.01%
Santa Ana - 1441 West | CA | 217337.1587 | 218090.081 | -752.9223 | -0.3452% | 239339.813 | -22002.6543 | -9.193%
Jessup -7950 Oceano Ave | MD | 690674.3501 | 666041.512 | 24632.8381 | 3.698% | 857702.282 | -167027.9319 | -19.47%
TX: Fort Worth - 5200 Gold Spike Dr | TX | 953361 | 1426714.028 | -473353.028 | -33.18% | 1517285.51 | -563924.51 | -37.17%
NY: Clifton Springs - Ontario 2 (21597) | NY | 0 | 0 | 0 |  | 0 | 0
CA: Oxnard - 2600 Sakioka - System A | CA | 0 | 0 | 0 |  | 0 | 0
CA: Oxnard - 2600 Sakioka - System B | CA | 0 | 0 | 0 |  | 0 | 0
NY: Fonda - Montgomery 1 (21601) | NY | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
Catalyze |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 13093799.5216 | 16919926.0191 | -3826126.4975 | -22.61% | 16389344.43 | -3295544.9084 | -20.11%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 206227.25 | 218347.1 | -12119.85 | -5.551% | 259696.6 | -53469.35 | -20.59%
Adelanto - 1 Sheep Creek Road | CA | 582365 | 1093000.6781 | -510635.6781 | -46.72% | 0 | 0
Blackstone - 83 Federal Street | MA | 1776705.3 | 1681340.2 | 95365.1 | 5.672% | 1783003.6 | -6298.3 | -0.3532%
Charlton - 299 Worcester Road | MA | 137377.75 | 144771.99 | -7394.24 | -5.108% | 130827.31 | 6550.44 | 5.007%
Wareham - 8 Thatcher Drive | MA | 41936.4375 | 43732.19 | -1795.7525 | -4.106% | 40379.79 | 1556.6475 | 3.855%
West Yarmouth - 42 Mid Tech | MA | 38806.4674 | 42914.68 | -4108.2126 | -9.573% | 43148.14 | -4341.6726 | -10.06%
Harrison - 130 Union Street | NY | 44773.5625 | 63940.87 | -19167.3075 | -29.98% | 60679.5 | -15905.9375 | -26.21%
Staten Island - Ellis Storage | NY | 141909.625 | 123541.25 | 18368.375 | 14.87% | 139956.72 | 1952.905 | 1.395%
Amherst - 595 Schoelles Road | NY | 2226477 | 2369400 | -142923 | -6.032% | 2315510 | -89033 | -3.845%
Lancaster 1 - Gunnville Road | NY | 1302308 | 1759262.2 | -456954.2 | -25.97% | 1787173.3 | -484865.3 | -27.13%
Lancaster 2 - Shisler Road | NY | 1559999 | 1830014.6 | -270015.6 | -14.75% | 1959308.5 | -399309.5 | -20.38%
Fullerton - 200 W Orangethorpe | CA | 239725.625 | 260097.4 | -20371.775 | -7.832% | 287848.6 | -48122.975 | -16.72%
El Paso - 10500 Railroad Drive | TX | 0 | 0 | 0 |  | 0 | 0
Friona - 900 Millard Ave | TX | 3678.5 | 216325.8 | -212647.3 | -98.3% | 274881.3 | -271202.8 | -98.66%
Augusta - 13 York Farm Road | ME | 375045.375 | 398791.9 | -23746.525 | -5.955% | 420944.7 | -45899.325 | -10.9%
Santa Ana - 1441 West | CA | 159926.3125 | 157699.04 | 2227.2725 | 1.412% | 172451.93 | -12525.6175 | -7.263%
Jessup -7950 Oceano Ave | MD | 485771.75 | 466486.4 | 19285.35 | 4.134% | 587434.1 | -101662.35 | -17.31%
TX: Fort Worth - 5200 Gold Spike Dr | TX | 0 | 1652888.3 | -1652888.3 | -100% | 1732824.1 | -1732824.1 | -100%
NY: Clifton Springs - Ontario 2 (21597) | NY | 2536602 | 2702570.9 | -165968.9 | -6.141% | 2457073.8 | 79528.2 | 3.237%
CA: Oxnard - 2600 Sakioka - System A | CA | 316571.8494 | 381593.5 | -65021.6506 | -17.04% | 362300.5 | -45728.6506 | -12.62%
CA: Oxnard - 2600 Sakioka - System B | CA | 4710.0503 | 349355.8 | -344645.7497 | -98.65% | 368582 | -363871.9497 | -98.72%
NY: Fonda - Montgomery 1 (21601) | NY | 912882.667 | 963851.221 | -50968.554 | -5.288% | 1205319.94 | -292437.273 | -24.26%

## 4th Qtr
Catalyze |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Fresno - 3150 Shaw Ave | CA | 0 | 0 | 0 |  | 0 | 0
Adelanto - 1 Sheep Creek Road | CA | 0 | 0 | 0 |  | 0 | 0
Blackstone - 83 Federal Street | MA | 0 | 0 | 0 |  | 0 | 0
Charlton - 299 Worcester Road | MA | 0 | 0 | 0 |  | 0 | 0
Wareham - 8 Thatcher Drive | MA | 0 | 0 | 0 |  | 0 | 0
West Yarmouth - 42 Mid Tech | MA | 0 | 0 | 0 |  | 0 | 0
Harrison - 130 Union Street | NY | 0 | 0 | 0 |  | 0 | 0
Staten Island - Ellis Storage | NY | 0 | 0 | 0 |  | 0 | 0
Amherst - 595 Schoelles Road | NY | 0 | 0 | 0 |  | 0 | 0
Lancaster 1 - Gunnville Road | NY | 0 | 0 | 0 |  | 0 | 0
Lancaster 2 - Shisler Road | NY | 0 | 0 | 0 |  | 0 | 0
Fullerton - 200 W Orangethorpe | CA | 0 | 0 | 0 |  | 0 | 0
El Paso - 10500 Railroad Drive | TX | 0 | 0 | 0 |  | 0 | 0
Friona - 900 Millard Ave | TX | 0 | 0 | 0 |  | 0 | 0
Augusta - 13 York Farm Road | ME | 0 | 0 | 0 |  | 0 | 0
Santa Ana - 1441 West | CA | 0 | 0 | 0 |  | 0 | 0
Jessup -7950 Oceano Ave | MD | 0 | 0 | 0 |  | 0 | 0
TX: Fort Worth - 5200 Gold Spike Dr | TX | 0 | 0 | 0 |  | 0 | 0
NY: Clifton Springs - Ontario 2 (21597) | NY | 0 | 0 | 0 |  | 0 | 0
CA: Oxnard - 2600 Sakioka - System A | CA | 0 | 0 | 0 |  | 0 | 0
CA: Oxnard - 2600 Sakioka - System B | CA | 0 | 0 | 0 |  | 0 | 0
NY: Fonda - Montgomery 1 (21601) | NY | 0 | 0 | 0 |  | 0 | 0

## Jan
Catalyze |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1684623.4914 | 2378878.936 | -694255.4446 | -29.18% | 2175549.66 | -490926.1686 | -22.57% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 53422.875 | 50400.42 | 3022.455 | 5.997% | 49997 | 3425.875 | 6.852% | 1.Inverter 5 has experienced tripping events on alternate days throughout the month due to water intrusion in the connectors. According to the technician's notes, further troubleshooting is required | 1. SR094993
Adelanto - 1 Sheep Creek Road | CA | 434343 | 163616.27 | 270726.73 | 165.5% | 479912.62 | -45569.62 | -9.495% | 1. The weather station stopped communicating on 01/08. A technician onsite for inverter and weather station issues contacted SMA and updated five inverters. Communication was restored on 01/21 but again lost on 01/27. On 01/28, the technician contacted Aderis and re-established communication, but it dropped again at 15:00. It was restored at 10:00 on 01/29 while the technician was updating inverter firmware. 2. Inverter 7 was offline from 01/23. The technician investigated the issue and replaced the L2 fuse, bringing the inverter back online on 01/28. 3. The site was offline on 01/28 at 08:00am and later remotely closed by catalyze at 09:00am. | 1. SR092431, SR095414 2. SR096016 3. SR096049 | SR095414 | SR096016 | SR096049
Blackstone - 83 Federal Street | MA | 221322 | 519101.6 | -297779.6 | -57.36% | 384369.8 | -163047.8 | -42.42% | 1.Inverter 1 tripped offline at 12:45 PM on 01/15. According to the received information, SMA was on-site working on the inverter on the same day, and Inverter 1 was back online at 02:30 PM on 01/15. 2.Inverter 1 is constantly producing 193kW even during non-production hours on 01/16. Issue got self resolved at 10:00 PM on 01/16. 3.Inverter 1 failed to start on 01/21. SMA technicians suspected a communication board issue. After further troubleshooting on 01/22, the inverter 1 was back online at 10:30 AM on 01/22. 4.The site experienced reduced production from 01/20 to 01/24 due to snow cover. On 01/25/25, production dropped to 62kW at 08:30 due to snow buildup. The technician reset the Indie control box, restoring PV production on 01/25. 5. The site tripped offline due to a utility outage at 12:45 PM on 01/28. After the technician reset the recloser, the site was back online at 1:45 PM on 01/29. | 1.SR095598 2.SR095641 3.SR095796 4.SR095973 5.SR096060, SR096061 | SR095641 | SR095796 | SR095973 | SR096060 | SR096061
Charlton - 299 Worcester Road | MA | 23675 | 33780.06 | -10105.06 | -29.91% | 31670.95 | -7995.95 | -25.25% | 1.Low generation due to weather/snow.
Wareham - 8 Thatcher Drive | MA | 7554.0625 | 9317.288 | -1763.2255 | -18.92% | 8974.43 | -1420.3675 | -15.83% | 1.Low generation due to weather/snow.
West Yarmouth - 42 Mid Tech | MA | 5192.6952 | 6591.808 | -1399.1128 | -21.23% | 6769.91 | -1577.2148 | -23.3% | 1. Irradiance sensor has been replaced on 01/22. | 1. SR086960, SR095896 | SR095896
Harrison - 130 Union Street | NY | 9045.625 | 14196.66 | -5151.035 | -36.28% | 10694.18 | -1648.555 | -15.42% | 1.Low generation due to weather/snow.
Staten Island - Ellis Storage | NY | 22396.625 | 27928.2 | -5531.575 | -19.81% | 22865 | -468.375 | -2.048% | 1.Low generation due to weather/snow.
Amherst - 595 Schoelles Road | NY | 176317 | 351737 | -175420 | -49.87% | 279121.6 | -102804.6 | -36.83% | 1.The site tripped offline at 01:15 AM on 01/22. On 01/23, after the utility closed their recloser, the technician reset the recloser, bringing the site back online and into production at 5:00 PM on 01/23. | 1.SR095842
Lancaster 1 - Gunnville Road | NY | 167972 | 298839.7 | -130867.7 | -43.79% | 191771 | -23799 | -12.41% | 1.Low generation due to weather/snow.
Lancaster 2 - Shisler Road | NY | 146912 | 352791.9 | -205879.9 | -58.36% | 204880 | -57968 | -28.29% | 1. Inverters 3.5 to 3.7 and 3.9 tripped offline at 15:45 and self-resolved at 16:15 on 01/09. A technician was dispatched and found inverter voltages out of range. Terminations were re-tightened. 2. Inverters 3.1 to 3.10 experienced multiple tripping events throughout the month, self-resolving on alternate days. | 1. SR095454 2. SR095996, SR096058, SR096170 | SR095996 | SR096058 | SR096170
Fullerton - 200 W Orangethorpe | CA | 63628.5463 | 73372.12 | -9743.5737 | -13.28% | 74894 | -11265.4537 | -15.04% | 1.Low generation due to weather/snow.
El Paso - 10500 Railroad Drive | TX | 93351.5 | 90713.1 | 2638.4 | 2.909% | 95865 | -2513.5 | -2.622%
Friona - 900 Millard Ave | TX | 69688.25 | 68867.83 | 820.42 | 1.191% | 72736 | -3047.75 | -4.19% | 1. Inverter 6 has been experiencing multiple tripping events throughout the month. The issue, caused by VARS (Volt-Ampere Reactive power) from the utility, scheduled to be addressed in Q3 2025. | 1.SR093503
Augusta - 13 York Farm Road | ME | 69027.875 | 131266.3 | -62238.425 | -47.41% | 92474 | -23446.125 | -25.35% | 1.Low generation due to weather/snow.
Santa Ana - 1441 West | CA | 36286.8125 | 40826.68 | -4539.8675 | -11.12% | 47186.47 | -10899.6575 | -23.1% | 1.Low generation due to weather/snow.
Jessup -7950 Oceano Ave | MD | 84487.625 | 145532 | -61044.375 | -41.95% | 121367.7 | -36880.075 | -30.39% | 1. Inverter 9 is underproducing compared to its peers due to four faulty optimizers affecting two strings | 1.SR096047
TX: Fort Worth - 5200 Gold Spike Dr | TX
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Feb
Catalyze |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2290649.9231 | 3115852.362 | -825202.4389 | -26.48% | 3274320.207 | -983670.2839 | -30.04% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 55837 | 53033.79 | 2803.21 | 5.286% | 57896.36 | -2059.36 | -3.557% | 1. Inverter 5 has experienced tripping events on alternate days since 12/30 due to Fault to stop DC wrong polarity. Further troubleshooting is required. 2. Inverter 2 tripped offline at 10:45AM on 02/16 and later self resolved inverter back online at 15:30 on 02/16. | 1. SR096333, SR094993 2. SR097172 | SR094993 | SR097172
Adelanto - 1 Sheep Creek Road | CA | 539830 | 415542.92 | 124287.08 | 29.91% | 569668.74 | -29838.74 | -5.238% | 1. Inverter 8 was offline since 01/31 and inverter 7 was offline throughtout the month. 2. Inverter 21 was offline intermittently throughout the month. On 02/28 technician was onsite replaced fuses bringing inverter back but it is in night mode. | 1. SR096178, SR096016 2. SR097916 | SR096016 | SR097916
Blackstone - 83 Federal Street | MA | 344694.9 | 508146.2 | -163451.3 | -32.17% | 491267.1 | -146572.2 | -29.84% | 1. Inverter was offline intermittently from 02/09 to 02/13 due to snow. | 1. SR096554
Charlton - 299 Worcester Road | MA | 27164.5 | 42025.38 | -14860.88 | -35.36% | 31343.27 | -4178.77 | -13.33% | 1. Inverter 13 experienced tripping events on high irradiance days reporting PV Abnormal Input - Protect0260. On 02/26 technician was onsite replaced inverter 1. As per solectria advice the bus board on inverter 13 has been removed. If the inverter faults again, will know that the issue lies with the inverter. | 1. SR081303
Wareham - 8 Thatcher Drive | MA | 9151.0625 | 10698.21 | -1547.1475 | -14.46% | 11033.87 | -1882.8075 | -17.06% | 1. Low generation due to weather/snow.
West Yarmouth - 42 Mid Tech | MA | 7255.8318 | 9324.202 | -2068.3702 | -22.18% | 9379.757 | -2123.9252 | -22.64% | 1. Low generation due to weather/snow.
Harrison - 130 Union Street | NY | 13226.875 | 16424.34 | -3197.465 | -19.47% | 14212.59 | -985.715 | -6.936% | 1.Low generation due to weather/snow.
Staten Island - Ellis Storage | NY | 31295.875 | 32267.16 | -971.285 | -3.01% | 30624.97 | 670.905 | 2.191%
Amherst - 595 Schoelles Road | NY | 232611 | 417742.3 | -185131.3 | -44.32% | 401280.1 | -168669.1 | -42.03% | 1. Site tripped offline at 08:30AM on 02/01 and later back online at 11:30AM on 02/02 after technician re-energized. 2. Site tripped offline at 3:30AM, technician closed the recloser. Site back online at 11:10AM on 02/18. 3. Site tripped offline at 14:00 on 02/26 back online at 16:30 on 02/27 after technician re-energized. | 1. SR096212 2. SR097208 3. SR097837 | SR097208 | SR097837
Lancaster 1 - Gunnville Road | NY | 227486 | 352750.8 | -125264.8 | -35.51% | 379774.4 | -152288.4 | -40.1% | 1. Low generation due to weather/snow.
Lancaster 2 - Shisler Road | NY | 223663 | 402516.6 | -178853.6 | -44.43% | 410691.2 | -187028.2 | -45.54% | 1.Inverters 3.1 to 3.10 experienced tripping events on 02/04, 02/05, 02/07 and 02/10. On 02/11 USNE was onsite and replaced Bay-O-net fuses. | 1. SR096170
Fullerton - 200 W Orangethorpe | CA | 73626.9537 | 75409.94 | -1782.9863 | -2.364% | 81220.44 | -7593.4863 | -9.349%
El Paso - 10500 Railroad Drive | TX | 105996.5 | 100797.2 | 5199.3 | 5.158% | 101055 | 4941.5 | 4.89%
Friona - 900 Millard Ave | TX | 81985 | 72229.98 | 9755.02 | 13.51% | 78972.4 | 3012.6 | 3.815% | 1. Inverter 6 has been experienced tripping event on 02/08 and 02/09. The issue, caused by VARS (Volt-Ampere Reactive power) from the utility, scheduled to be addressed in Q3 2025. | 1. SR093503
Augusta - 13 York Farm Road | ME | 43748.5 | 150180.8 | -106432.3 | -70.87% | 115391.9 | -71643.4 | -62.09% | 1. Low generation due to weather/snow.
Santa Ana - 1441 West | CA | 47461.375 | 45475.04 | 1986.335 | 4.368% | 53286.01 | -5824.635 | -10.93%
Jessup -7950 Oceano Ave | MD | 143523.25 | 137903.3 | 5619.95 | 4.075% | 143903.7 | -380.45 | -0.2644% | 1. Inverter 9 underperformance has self-resolved since 02/01 and producing in line with peers. | 1. SR096047
TX: Fort Worth - 5200 Gold Spike Dr | TX | 82092.3 | 273384.2 | -191291.9 | -69.97% | 293318.4 | -211226.1 | -72.01% | 1. Inverters 1.1, 1.2 are not communicating since 02/13 and inverter 3.4 stopped communicating on 02/24 and possibly offline. Client mentioned these inverters are still under EPC warranty so they are currently handling the RMA process. 2. The meters L1, L2, and L3 stopped communicating at 12:45 AM on 02/28. After communication was regained, only the L3 voltage started updating, while the L1 and L2 voltages dropped to zero. Possibly that the breakers have tripped. | 1. SR097878, SR097940 2. SR097900 | SR097940 | SR097900
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Mar
Catalyze |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 4294677.9979 | 4922393.12 | -627715.1221 | -12.75% | 5166542.81 | -871864.8121 | -16.88% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 82059.375 | 79466.18 | 2593.195 | 3.263% | 102469 | -20409.625 | -19.92% | 1.Inverter 5 has experienced multiple tripping events since 12/30 due to a "Fault to Stop DC Wrong Polarity"; on 03/11, a technician replaced two blown optimizers, and on 03/12, six hotspot modules were identified for replacement. 2.Site was taken offline from 7AM to 9AM on 03/07 due to technician checked in to drain the roof. | 1.SR096333,SR098835. 2.SR097877 | SR098835 | SR097877
Adelanto - 1 Sheep Creek Road | CA | 613170 | 474842.85 | 138327.15 | 29.13% | 680082.38 | -66912.38 | -9.839% | 1.Inverter 7 was offline on 03/03 in SMA portal, after techician checked in and replaced faulty fuse at L3 inverter back online on same day. 2. CB 14 was offline for whole month and being replaced but technician recieved wrong parts on 03/18. 3.Inverter 2 went offline on 03/13 in the SMA portal and back online on 03/14. 4.On 03/18 technician found inverter 5 was offline and after replacing AC line two blown fuse on 03/18, the Inverter back online on 03/18 at 12:15pm. 5.Adheris was doing backend work. No inverter data on Aderis from 03/27. | 1.SR097992 2. PM5513, SR089076, SR098032 3.SR098553 4.SR098032, SR098706 5.SR098752 | SR089076 | SR098032 | SR098553 | SR098032 | SR098706 | SR098752
Blackstone - 83 Federal Street | MA | 621375.9 | 663323.6 | -41947.7 | -6.324% | 693620.2 | -72244.3 | -10.42% | 1.Meter was capturing 50 -250Kw less than Inverter active power during peak hours since 02/18/23. | 1.SR084901, SR099181, SR098032 | SR099181 | SR098032
Charlton - 299 Worcester Road | MA | 55962.25 | 56208.81 | -246.56 | -0.4387% | 59298.27 | -3336.02 | -5.626% | 1. Inverters 6, 7, and 8 were power cycling midday during peak hours on high irradiance days due to "PV Abnormal Input - Protect0260". On 03/10, the technician followed Solectria’s advice, removed the parallel bar, and set dipswitches to independent. Inverters have been producing normally since 03/11. 2.Inverter 7 has experienced multiple trippings on 03/24 due to PV Abnormal Input fault. | 1.SR097972,SR098257 2.SR098919 | SR098257 | SR098919
Wareham - 8 Thatcher Drive | MA | 14875.8125 | 15055.13 | -179.3175 | -1.191% | 16928.07 | -2052.2575 | -12.12% | 1. Site production was low on 03/05, 03/06, 03/17, 03/24 and 03/29 to 03/31 due to weather event.
West Yarmouth - 42 Mid Tech | MA | 12225.6817 | 13601.24 | -1375.5583 | -10.11% | 14703.99 | -2478.3083 | -16.85% | 1. Site production was low on 03/05, 03/06, 03/17, 03/24 and 03/29 to 03/31 due to weather event.
Harrison - 130 Union Street | NY | 23281.875 | 24219.16 | -937.285 | -3.87% | 21479.86 | 1802.015 | 8.389%
Staten Island - Ellis Storage | NY | 53693.25 | 50948.08 | 2745.17 | 5.388% | 48258.91 | 5434.34 | 11.26%
Amherst - 595 Schoelles Road | NY | 571517 | 702948.9 | -131431.9 | -18.7% | 728804.1 | -157287.1 | -21.58% | 1.Site tripped offline at 14:07 on 03/14 and back online at 10AM on 03/15 after technician closed relay and re-energized the site. Again tripped offline at 18:45 on 03/15 back online at 8AM on 03/17. Site again tripped offline at 10:45 on 03/22 and back online at 8:45 on 03/24. Again tripped offline at 17:00 on 03/25 due to utility outage and back online at 11:30 on 03/27. Again tripped offline at 14:45 on 03/28 and back online at 8:15AM on 03/31. | 1.SR098595, SR098886, SR098982 & SR099115. | SR098886 | SR098982 | SR099115
Lancaster 1 - Gunnville Road | NY | 598573 | 629166 | -30593 | -4.862% | 641592.3 | -43019.3 | -6.705% | 1.Inverter 1.1 was derated at 165KW between 12PM to 16:30 on 03/10, 03/13, 03/14, 03/18 and 03/19. | 1.SR098345
Lancaster 2 - Shisler Road | NY | 648289 | 692226.9 | -43937.9 | -6.347% | 704760.1 | -56471.1 | -8.013% | 1. Inverter 3.4 with 12 strings, Inverter 3.5 with 12 strings, Inverter 3.6 with 12 strings, Inverter 3.7 with 7 strings, Inverter 3.8 with 4 and 10 strings, Inverter 3.9 with 7 strings, and Inverter 3.10 with 9 strings are overall underperforming by 250KW. | 1. SR098941
Fullerton - 200 W Orangethorpe | CA | 96573.5 | 99489.52 | -2916.02 | -2.931% | 111528.7 | -14955.2 | -13.41% | 1Inverter 5 was offline for multiple days on 03/03, 03/05, 03/07, 03/08, 03/12, and started late on 03/19 due to a Fault to Stop AFCI Fault. After a technician performed a power cycle on both the AC and DC sides, the inverter performance improved. | 1. SR098011
El Paso - 10500 Railroad Drive | TX | 137031.75 | 125322.2 | 11709.55 | 9.344% | 132709.5 | 4322.25 | 3.257% | 1.Inverter 6 experienced tripping events on 03/01, 03/05, 03/07 to 03/13, and 03/16. The issue, caused by VARS (Volt-Ampere Reactive power) from the utility, persisted and worsened in February. After the technician performed wire management, the inverter performance improved, and an RMA was initiated for the inverter. | 1.SR098406
Friona - 900 Millard Ave | TX | 110152.875 | 110329 | -176.125 | -0.1596% | 105708.4 | 4444.475 | 4.204% | 1.Inverter 1 was offline on 03/04 due to "fault to stop ground fault" later self resolve and was back online at 07:00 AM on 03/05. 2.Inverter 6 experienced multiple trippings starting from 03/12 due to 'Fault to Stop The Grid Interference Protection,' continuing throughout the month. Additionally, it was derated to 45KW. 3. The site tripped offline at 11:00 AM on 03/14 and was back online at 13:00 on 03/16 due to a utility outage. | 1.SR098064 2.SR098463 3.SR098579 | SR098463 | SR098579
Augusta - 13 York Farm Road | ME | 136389.5 | 148689.9 | -12300.4 | -8.273% | 162995 | -26605.5 | -16.32% | 1. Site production was low on 03/05, 03/06, 03/17, 03/24 and 03/29 to 03/31 due to weather event.
Santa Ana - 1441 West | CA | 65569.1537 | 61153.65 | 4415.5037 | 7.22% | 70786.73 | -5217.5762 | -7.371%
Jessup -7950 Oceano Ave | MD | 240512.375 | 227251.8 | 13260.575 | 5.835% | 215179.3 | 25333.075 | 11.77% | 1. Inverter 4 tripped offline at 08:30 AM on 03/31 due to generic fault. 2. Inverter 11 is underperforming by 33KW. After the technician troubleshooted the inverter, the central unit is offline and it's under RMA'd. | 1. SR099184 2. SR098878 | SR098878
TX: Fort Worth - 5200 Gold Spike Dr | TX | 213425.7 | 748150.2 | -534724.5 | -71.47% | 655638 | -442212.3 | -67.45% | 1. Pads 1 and 2 were tripped offline on 03/04 at 04:30am and back online at 09:00am on 03/04 However, inverters 1.2, 1.4, 2.4, 2.7, 2.9, 2.10, 2.16, and 3.1 remain offline due to a Fault to Stop Ground and inverters 3.1, 3.3, 3.8 started late for production on 03/04 and again pad 1 and 2 are tripped offline at 22:00 on 03/04 and back online at 09:00am on 03/05 2. Inverter 3.3 was offline for multiple days in month 3.Inverter 2.15 was offline on 03/28 due to "Fault to stop Ground Fault" and was back online on 03/29. 4.Inverter 3.6 tripped offline at 14:30 from 02/24 due to "Fault to stop DC Bus Over Voltage" and was back online on 03/27. 5.Inverter 3.2 was offline from 03/06 due to "Fault to stop Ground Fault"and was back online on 03/08. 6. All 3 meters are only capturing about a 1/3rd of the site's inverters' production. 7. Pad 1 & 2 inverters were tripped offline on 09/22 at 10:00am due to "Fault to stop grid" and back online on 03/27 at 07:00am. 8. Inverters 2.4, 2.7, 2.13, 2.16, 2.17, 3.2, and 3.3 are tripped offline due to ground fault on 03/07 at 15:00 and Inverters 2.4, 2.13 & 3.3 are back online on 03/08 at 07:00 and inverters 2.7, 2.16, 2.17, 3.2 are back online on 03/10. Site tripped offline at 15:00on 03/07 and back online on 03/08 at 07:00am. Inverter 1.9 wasoffline for whole day on 03/12 and back one on 03/12 at 07:00am and again inverter 1.9 tripped offline on 03/13 at 15:00 and back online at 03/14 at 07:00am. Inverter 1.5 was offline from 10:00 am to 11:00am on 03/13. Inverters 1.5, 2.4 are underproducing approximatly 30kW since 03/14. Inverters 1.1, 2.6, 2.7 are uderproducing 10kW compared to their peers. 9. Technician was on site for PM event on 03/11 due to that Inverter 2.14 was offline from 09:00am to 11:00am on 03/11 and inverter 3.1 was offline from 11:00am to 03:00pm on 03/11. | 1. SR097900 2. SR098236, SR097900 3.SR099098 4.SR098953 5.SR098236 6. SR097879 7. SR098887 8. SR098236 9. SR097911, PM13161 | SR098236 | SR097900 | SR099098 | SR098953 | SR098236 | SR097879 | SR098887 | SR098236 | SR097911
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Apr
Catalyze |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 5163386.488 | 4823758.6475 | 339627.8405 | 7.041% | 5200347.03 | -36960.542 | -0.7107% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 100611 | 98633.69 | 1977.31 | 2.005% | 109007.3 | -8396.3 | -7.703% | 1. Inverter 5 has experienced multiple tripping events since 12/30 due to a "Fault to Stop DC Wrong Polarity". Sourcing panel need to be replaced. | 1. SR098835
Adelanto - 1 Sheep Creek Road | CA | 786306 | 174230.6475 | 612075.3525 | 351.3% |  |  |  | 1. Inverter 3 tripped offline at 12:00PM on 04/19. On 04/23 technician troubleshooted and found A Phase fuse blown and will need to be replaced. 2. Inverter 5 was offline on 04/16. On 04/23 technician troubleshooted and found A Phase fuse blown and will need to be replaced. 3. Inverter 18 was offline on 04/23. Technician troubleshooted and found A Phase fuse blown and will need to be replaced. 4. No forcasted data available from 03/27 as Aderis was doing backend work. | 1. SR100019 2. SR099884 3. SR100199 | SR099884 | SR100199
Blackstone - 83 Federal Street | MA | 490582.5 | 697581.8 | -206999.3 | -29.67% | 768668.8 | -278086.3 | -36.18% | 1. The site was offline from 8:30AM to 17:45 on 04/02 due to USNE was onsite to investigate the transformer leak. 2. Inverter did not come back online on 04/03 after the completion of work on 04/02. A technician investigated and reset the Indie EMS controller, and the inverter came back online at 10:00 AM on 04/03. 3. Invertertripped offline at 11:45 AM on 04/09. An SMA technician updated the firmware for the inverters and DPS, and the inverter came back online at 6:30 PM on 04/10. 4. Site tripped offline at 11:00AM on 04/21 and back online at 12:30PM on 04/23 due to S3 power was onsite working on testing CT's. 5. Inverter was offline from 9:30 AM to 10:00 AM on 04/24 due to S3 Power being onsite. They found that the sensor output was too high and replaced the wire between the RIK unit and the meter with a thicker one to correct the issue. 6. Inverter tripped offline at 1:30 PM on 04/29 due to the Catalyze team was onsite working on the batteries and left the inverter offline for pending work | 1. SR099297 2. SR099335, SR099350 3. SR099592 4. SR100086 5. SR100086 6. SR100654 | SR099335 | SR099350 | SR099592 | SR100086 | SR100086 | SR100654
Charlton - 299 Worcester Road | MA | 59872.5 | 60825.16 | -952.66 | -1.566% | 69479.32 | -9606.82 | -13.83% | 1. Inverter 02 was underperforming by 30%. Will be investigated while next time onsite. | 1. SR099076
Wareham - 8 Thatcher Drive | MA | 17115.3125 | 17134.03 | -18.7175 | -0.1092% | 20513.51 | -3398.1975 | -16.57% | 1. Site production was low on 04/03, 04/07, 04/12, 04/26 due to weather event.
West Yarmouth - 42 Mid Tech | MA | 15407.1106 | 16609.13 | -1202.0194 | -7.237% | 19005.69 | -3598.5794 | -18.93% | 1. Site production was low on 04/07, 04/26 due to weather event.
Harrison - 130 Union Street | NY | 25339.3125 | 25779.61 | -440.2975 | -1.708% | 26043.9 | -704.5875 | -2.705%
Staten Island - Ellis Storage | NY | 55255.625 | 49684.37 | 5571.255 | 11.21% | 60526.2 | -5270.575 | -8.708%
Amherst - 595 Schoelles Road | NY | 812218.5 | 838338.8 | -26120.3 | -3.116% | 916083.3 | -103864.8 | -11.34% | 1. Tracker position 2 has stuck at 1.38degrees from 04/13. Will investigate next time onsite. | 1. SR100051
Lancaster 1 - Gunnville Road | NY | 667894 | 658923.3 | 8970.7 | 1.361% | 743810.8 | -75916.8 | -10.21% | 1. Inverters 1.1 and 2.6 experienced derating issues on 04/04, 04/07, 04/13, 04/14, 04/20, and 04/22. On 04/24, a technician replaced both inverters. Inverter 1.1 returned to normal operating condition, but inverter 2.6 was not communicating, although production was confirmed at the site. 2. Inverters lost communication at 13:30 on 04/23 and restored at 14:30 on 04/24 due to technician was onsite working on replacement of inverters 1.1, 2.6. | 1. SR099487, SR098345 2. SR099487, SR098345 | SR098345 | SR099487 | SR098345
Lancaster 2 - Shisler Road | NY | 701885 | 723030.1 | -21145.1 | -2.925% | 817032.2 | -115147.2 | -14.09% | 1. Inverter 3.4 with 12 strings, Inverter 3.5 with 12 strings, Inverter 3.6 with 12 strings, Inverter 3.7 with 7 strings, Inverter 3.8 with 4 and 10 strings, Inverter 3.9 with 7 strings, and Inverter 3.10 with 9 strings are overall underperforming by 250KW. Followed up with Catalyze, need to be investigate. 2. Site tripped offline at 12:00PM on 04/09. Technician has installed the new fuse at the pole and closed the recloser. Site back onlien at 16:30 on 04/10. | 1. SR098941 2. SR099590 | SR099590
Fullerton - 200 W Orangethorpe | CA | 111484.625 | 112078.2 | -593.575 | -0.5296% | 121425.9 | -9941.275 | -8.187%
El Paso - 10500 Railroad Drive | TX | 153942.5 | 135732.4 | 18210.1 | 13.42% | 147311.9 | 6630.6 | 4.501% | 1. Inverter 6 is underperforming by 5kW during peak hours from 04/08. Waiting for response for dispatch. | 1. SR099965
Friona - 900 Millard Ave | TX | 121081 | 109536.6 | 11544.4 | 10.54% | 124471.2 | -3390.2 | -2.724% | 1. Inverter 6 experienced multiple trippings starting from 03/12 due to 'Fault to Stop The Grid Interference Protection,' continuing throughout the month | 1. SR098463
Augusta - 13 York Farm Road | ME | 162062.75 | 162237.4 | -174.65 | -0.1077% | 179807.8 | -17745.05 | -9.869%
Santa Ana - 1441 West | CA | 61971.8462 | 67920.71 | -5948.8638 | -8.759% | 77132.41 | -15160.5638 | -19.66% | 1. Site tripped offline at 14:15 on 04/20. On 04/23, a technician re-energized the site, and it came back online at 11:15 AM. Additionally, the technician found that Inverter 1 and some PV strings had sustained thermal damage. The affected inverter and PV strings were isolated, and Inverter 1 needs to be replaced. | 1. SR100043
Jessup -7950 Oceano Ave | MD | 210761.9061 | 220062.8 | -9300.8939 | -4.226% | 259363.5 | -48601.5939 | -18.74% | 1. Inverter 11 central unit has been RMA'd from 03/31. Pending shipment - case 5655526. 2. Inverter 4 tripped offline at 8:30AM on 03/31 due to generic fault. Inverter back online at 9:30AM on 04/21. SolarEdge RMAing 100A fuse. 3. Inverter 5 tripped offline at 16:45 on 04/10. On 04/21 technician troubleshooted and it is back online at 9:00AM. Inverter right unit has been RMA'd from 04/15. 4. Inverters 3 and 6 tripped offline at 18:00 on 04/16 due to high AC voltage. On 04/20, both inverters self-recovered and resumed production; however, the right units of both inverters remained offline. On 04/21, a technician replaced the AC fuses and re-energized the system. The right unit of Inverter 6 was RMA'd on 04/21. | 1. SR098878 2. SR099184 3. SR099672 4. SR099915 | SR099184 | SR099672 | SR099915
TX: Fort Worth - 5200 Gold Spike Dr | TX | 609595 | 655419.9 | -45824.9 | -6.992% | 740663.3 | -131068.3 | -17.7% | 1. Inverter 3-2 did not start production on 04/05 and 04/19 but self-resolved on the following days. 2. Inverter 3-3 was derated during peak hours on 04/11 and 04/13. Additionally, both Inverters 3-3 and 3-2 experienced derating on 04/20 and 04/21, but the issue self-resolved on the following days 3. Inverter 2.15 started late for production at 10:30 due to ground fault on 04/23. 4. Inverter 2-17 didnot started for production on 04/24 and self resolved at 17:00 on 04/27. However on 04/28 inverter again didn't started and self-resolved at 13:00 on 04/30. | 1. SR099447 2. SR099716 3. SR100205 4. SR100364 | SR099716 | SR100205 | SR100364
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## May
Catalyze |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 5303468.4408 | 5160859.0474 | 142609.3934 | 2.763% | 6003345.272 | -699876.8312 | -11.66% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 130416.75 | 121464.5 | 8952.25 | 7.37% | 135280 | -4863.25 | -3.595%
Adelanto - 1 Sheep Creek Road | CA | 887612 | 504761.4074 | 382850.5926 | 75.85% |  |  |  | 1. Inverter 12 was tripped offline on 05/13 at 09:00 due to blown fuse on 05/13 the technician replaced a fuse on phase B of inverter 12. 2. Inverter 20 was tripped offline on 05/05 at 11:00 due to blown fuse on phase A on 05/13 technician replaced fuse on phase A. 3. Inverters 3, 5, 18 were offline from 05/01 due to blown fuse on phase A of inverters, on 05/13 technician replaced the fuse on A phase. 4. No forcasted data available from 03/27 as Aderis was doing backend work. | 1. SR101370 2. SR101027 3. SR100199 | SR101027 | SR100199
Blackstone - 83 Federal Street | MA | 720855.5022 | 634671.8 | 86183.7022 | 13.58% | 847935.1 | -127079.5978 | -14.99% | 1.Inverter 1 was reading no production from 13:30 on 05/01 and was showing proper production from 05/02 at 16:45 EDT. Issue got self resolved. 2. Site tripped offline at 13:30 on 04/29 as technicians are on site to troubleshoot the BESS system and site was back online at 16:30 on 05/02 after the utility power was restored. 3. Inverter 1 tripped offline at 12:45 on 05/09. Later self resolved and back online at 13:00 on 05/10 | 1.SR100654,SR100896 2.SR100654,PM 8020 3.SR101246 | SR100896 | SR100654 | SR101246
Charlton - 299 Worcester Road | MA | 44041 | 45788.82 | -1747.82 | -3.817% | 68502.44 | -24461.44 | -35.71% | 1.Site remained offline from 17:45 on 05/08 to 08:30 on 05/13 .Site was back online after the technician has reset the relay and main breaker on 05/13. 2.The site was offline from 12:30 to 13:30 on 05/27 due to technicians being onsite for preventive maintenance. 3. Inverter 10 has a history of late start ups. | 1.SR101207 2.PM7960
Wareham - 8 Thatcher Drive | MA | 18896.6875 | 19480.04 | -583.3525 | -2.995% | 21158.03 | -2261.3425 | -10.69% | 1.Site was offline from 05:00 to 09:30 on 05/31. Site was back online after the utility power has been restored. | 1.SR102215
West Yarmouth - 42 Mid Tech | MA | 17967.3446 | 19926.91 | -1959.5654 | -9.834% | 21988.85 | -4021.5054 | -18.29% | 1. Site production was low on 05/09, 05/22, 05/23 and 05/29 due to rain.
Harrison - 130 Union Street | NY | 21616.625 | 24650.15 | -3033.525 | -12.31% | 30159.71 | -8543.085 | -28.33% | 1. Inverter 3 right unit has been offline since 15:00 EDT on 05/01, resulting in an approximate production loss of 10 kW. On 05/29 technician found that the right unit needs to be replaced, and an RMA case has been initiated with the OEM, and mentioned that Inverter 3 will remain offline until the right unit is replaced. | 1.SR100950
Staten Island - Ellis Storage | NY | 57266.75 | 48791.45 | 8475.3 | 17.37% | 71362.38 | -14095.63 | -19.75% | 1.The site has been experiencing brief outages at short intervals on multiple days. Energy values of inverters are reporting at constant value of 0 on 05/10 and 05/29
Amherst - 595 Schoelles Road | NY | 904020.5 | 903508 | 512.5 | 0.05672% | 1145964 | -241943.5 | -21.11% | 1. Tracker position 2 has stuck at 1.38degrees from 04/13. Will investigate next time onsite. | 1. SR100051
Lancaster 1 - Gunnville Road | NY | 680597 | 667291.2 | 13305.8 | 1.994% | 890932.6 | -210335.6 | -23.61% | 1.Inverter 2.6 is not communicating following replacement. All settings and RS485 connections were verified, and no issues were identified. A follow-up visit to the site will be required for further investigation 2.Inverter 2.9 was offline from 06:15 to 11:45 on 05/03. Issue got self resolved. 3.Inverter 2.6 was offline through out the month.Required further troubleshooting 4.Inverter 2.4 is derated by 32.35kW from 12:30 to 15:10 on 05/26 and reporting "Fault (Inverter current imbalance)" in CPS portal.Issue got self resolved on 05/27 | 1.SR100368 2.SR100507 3.SR100837 4.SR101937 | SR100507 | SR100837 | SR101937
Lancaster 2 - Shisler Road | NY | 749610 | 696616.4 | 52993.6 | 7.607% | 977951.1 | -228341.1 | -23.35% | 1. Inverter 3.4 with 12 strings, Inverter 3.5 with 12 strings, Inverter 3.6 with 12 strings, Inverter 3.7 with 7 strings, Inverter 3.8 with 4 and 10 strings, Inverter 3.9 with 7 strings, and Inverter 3.10 with 9 strings are overall underperforming by 250KW. Followed up with Catalyze, need to be investigate. | 1.SR098941
Fullerton - 200 W Orangethorpe | CA | 119409.375 | 115839.1 | 3570.275 | 3.082% | 134722 | -15312.625 | -11.37% | 1.Inverter 1 tripped offline at 12:15 on 05/10 and back online on 05/11.Inverter 1 was again offline from 05/12 to 12:00 on 05/14.Inverter 1 was back online after the technician has cleared arc fault and reset the inverter and he mentioned i string is isolated for further investigation. 2.Inverter 5 was down a string. Technicians checked into the site on 05/13 to address the issue but failed to do so due to bad weather conditions. This issue requires further troubleshooting 3.Inverter 7 is underperforming by 10 kW, and the MPPTs are unbalanced. On 05/14, technicians attended the site and found that Inverter 7 was reading normally, but Inverter 5 was reading 10 kW lower than the other inverters. The issue was followed up with the Solis technical support team, and we are currently awaiting their response. | 1.SR099959,SR101259 2.SR099959 3.SR100904 | SR101259 | SR099959 | SR100904
El Paso - 10500 Railroad Drive | TX | 77526 | 79734.93 | -2208.93 | -2.77% | 160120.1 | -82594.1 | -51.58% | 1.Site tripped offline at 12:45 on 05/15 and remained offline for rest of the month.The Operations team received information that the site was scheduled for shutdown and will remain offline until further notice | 1.SR101516
Friona - 900 Millard Ave | TX | 63329 | 66948.92 | -3619.92 | -5.407% | 138839.2 | -75510.2 | -54.39% | 1.Inverter 6 experiencing multiple tripping events throughout the month and reporting "Fault to stop The Grid Interference Protection. Waiting on Catalyze response. 2.Site tripped offline at 13:30 on 05/15 and remained offline for rest of the month.The Operations team received information that the site was scheduled for shutdown and will remain offline until further notice | 1.SR098463 2.SR101517 | SR101517
Augusta - 13 York Farm Road | ME | 160743.125 | 150116.7 | 10626.425 | 7.079% | 200843 | -40099.875 | -19.97% | 1. Site production was low on 05/02, 05/04, 05/06, 05/09, 05/10 due to rain.
Santa Ana - 1441 West | CA | 75553.9375 | 72601.38 | 2952.5575 | 4.067% | 81082.77 | -5528.8325 | -6.819% | 1.On 04/23, the technician identified thermal damage to Inverter 1 and several PV strings. The affected inverter and PV strings were isolated. Inverter 1 was replaced on 05/09, and has been performing as expected since the replacement 2.Inverter 3 is producing less power between 11:00 to 14:30 starting from 05/08/25 possibly due to shading on some of the panels.Waiting for the client approval to dispatch | 1.SR100043 2.SR101794 | SR101794
Jessup -7950 Oceano Ave | MD | 230240.844 | 217373.212 | 12867.632 | 5.92% | 299881.782 | -69640.938 | -23.22% | 1.Inverter 7 middle unit tripped offline at 09:00 on 05/12 and reporting an " Ground Current - RCD "and was back online at 07:00 on 05/21. Its right unit was tripped off at 12:15 on 05/22,technician checked in on 05/23 and stated that there was 1 blown fuse in the right unit and replaced it after that it was back online at 12:15 on 05/23. 2.Inverter 6 was offline since 05/23/25 after technician checked in he stated that it will remain offline untill the parts are replaced. 3.Inverter 3 right unit was tripped offline at 12:15 on 05/22 after technician checked in on 05/23 he replaced the Rma'd right now after which all the units are producing as they should. 4. Inverter 11 central unit has been RMA'd from 03/31. Pending shipment - case 5655526 and the provided RMA number is R2025041717074141. | 1.SR101758 2.SR099915 3.SR099672 4.SR098878 | SR099915 | SR099672 | SR098878
TX: Fort Worth - 5200 Gold Spike Dr | TX | 343766 | 771294.128 | -427528.128 | -55.43% | 776622.21 | -432856.21 | -55.74% | 1.Site tripped offline at 12:30 on 05/15, meter 2 voltages dropped to zero but meter 1 voltages are available remained same through out the month 2.Inverter 3.3 is intermittently derating by 20 kW since 05/03 3. Inverters 1.7 and 2.7 were offline at 16:37 on 05/10 and were back online at 10:15 on 05/11 4. Site tripped offline at 16:38 on 05/10, meter voltages dropped to zero. Recloser voltages are available and was back online at 18:00 CDT on the same day. | 1.SR101493 2.SR101392 3.SR101275 4.SR101271 | SR101392 | SR101275 | SR101271
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Jun
Catalyze |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 4883769.5629 | 4949429.831 | -65660.2681 | -1.327% | 4994823.593 | -111054.0301 | -2.223% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 115368.25 | 119161.8 | -3793.55 | -3.184% | 134620.7 | -19252.45 | -14.3% | 1. Inverter 5 has experienced multiple tripping events since 12/30 due to a "Fault to Stop DC Wrong Polarity". Sourcing panel need to be replaced. | 1.SR102597, SR098835 | SR098835
Adelanto - 1 Sheep Creek Road | CA | 564832 | 481375.1 | 83456.9 | 17.34% |  |  |  | 1. Inverter 1 is underperforming by ~10kW and is not communicating to SMA portal. Inverter 21 underperforming by ~10kW consistently and ~20kW during high irradiance days. Site was shut down on 06/18 at 10:15am due to transformer issue till the date 2. inverter 5 tripped offline on 6/15/25 at 13:00 through out the month 3. No forcasted data available from 03/27 as Aderis was doing backend work. | 1.SR102554 2.SR103010 | SR103010
Blackstone - 83 Federal Street | MA | 773337.1 | 746319.5 | 27017.6 | 3.62% | 862940.2 | -89603.1 | -10.38% | 1. Site tripped offline at 13:00 on 06/20 and later back online at 10:15 on 06/21 2.Site tripped offline at 12:00pm on 06/23 and later back online by remote reset at 16:00 on 06/24 3. Technician de-energised the site on 06/16 from 09:00 am to 10:45am to clean the filters 4. CB 2 String 9, CB 4 Strings 5 & 6, CB8 Strings 9 &11, CB20 String 2 were offline from 06/01 to 06/03 and CB 2 String 3 remained offline | 1.SR103231 2.SR103350 3. SR102941 4. SR102312, SR102586 | SR103350 | SR102941 | SR102312 | SR102586
Charlton - 299 Worcester Road | MA | 62943.75 | 63680.05 | -736.3 | -1.156% | 64038.82 | -1095.07 | -1.71% | 1.Inverter 10 is starting up late. Reporting PV abnormal input - Protect0260 through out the month and inverter 10 was offline on 06/26. 2.Inverter 7 is tripping on and offline on 06/01 later back to normal operation on 06/03 | 1.SR103596 2.SR102260 | SR102260
Wareham - 8 Thatcher Drive | MA | 19658.5625 | 20707.66 | -1049.0975 | -5.066% | 20440.63 | -782.0675 | -3.826%
West Yarmouth - 42 Mid Tech | MA | 18858.7129 | 21576.05 | -2717.3371 | -12.59% | 22072.83 | -3214.1171 | -14.56% | 1. Low production/generation due to low irradiance on 06/07, 06/09, 06/10, 06/14, 06/17, 06/18, 06/26
Harrison - 130 Union Street | NY | 19629.9375 | 27534.18 | -7904.2425 | -28.71% | 30517.37 | -10887.4325 | -35.68% | 1.Inverter 3 right unit is offline from 05/01 at 15:00, inverter was kept offline from 05/29 at 13:00 and being RMA'd. through out the month | 1.SR100950
Staten Island - Ellis Storage | NY | 61247.5 | 49711.5 | 11536 | 23.21% | 73460.61 | -12213.11 | -16.63% | 1. Low production/generation due to low irradiance on 06/07, 06/09, 06/10, 06/14, 06/17, 06/18, 06/26, 06/27
Amherst - 595 Schoelles Road | NY | 1058293 | 1146709 | -88416 | -7.71% | 1186212 | -127919 | -10.78% | 1.CB (DC zones 2 and 3) are showing 0 values from 06/16 2.SEL relay tripped open at 22:45 0n 06/05 and back online at 09:00 on 06/06 and again tripped offline between 01:15 to 08:45 on 06/07 and again tripped offline at 18:45 on 06/07 and back online at 08:00 on 06/08 and again tripped offline at 17:30 on 06/14 and back online at 10:15 on 06/16 3. Tracker position 2 has been stuck at 0.99 degrees from 06/06 | 1.SR102452 2.SR102558 3.SR102830, SR103022 | SR102558 | SR102830 | SR103022
Lancaster 1 - Gunnville Road | NY | 747076 | 821883.8 | -74807.8 | -9.102% | 900333.3 | -153257.3 | -17.02% | 1. All inverters went offline at 20:45 on 06/05 due to a "Fault: Loss of Main - GridV.OutLim" and came back online at 15:30 on 06/06. 2. Inverter 1.5 has been derating at 32.6 kW since 11:45 on 06/10 due to an "Inverter Current Imbalance" and resumed normal production along with its peers at 15:00 on 06/24. 3. Site tripped offline at 11:15 on 06/11 and later came back online at 16:39 on 06/12. 4.Inverter 2.6 has been constantly derating at 2.90 kW since 06/14, and the inverter is being RMA’d. | 1. SR102589 2. SR102778 3. SR102827 4. SR100368, SR102999, SR103566 | SR102778 | SR102827 | SR100368 | SR102999 | SR103566
Lancaster 2 - Shisler Road | NY | 814703 | 848676.2 | -33973.2 | -4.003% | 986930.7 | -172227.7 | -17.45% | 1. All inverters went offline at 20:45 on 06/05 due to a "Fault: Loss of Main - GridV.OutLim" and came back online at 15:30 on 06/06. 2. Site tripped offline at 11:32 on 06/11 and later came back online at 16:42 on 06/12. 3. Inverters 4.6 and 4.8 have been offline since 06/26 due to "Fault Bus Sum High Fault - Fault0130". | 1. SR102588 2. SR102828 3. SR103584 | SR102828 | SR103584
Fullerton - 200 W Orangethorpe | CA | 124272.875 | 123722.8 | 550.075 | 0.4446% | 136533.8 | -12260.925 | -8.98% | 1. Inverter 7 was underproduced 10 kW lower than the other inverters from 05/02 to 06/26. | 1. SR100904
El Paso - 10500 Railroad Drive | TX | 0 | 0 | 0 |  | 0 | 0 |  | 1. The site tripped offline at 12:45 on 05/15 and will remain offline until further notice. | 1. SR101516
Friona - 900 Millard Ave | TX | 0 | 0 | 0 |  | 0 | 0 |  | 1. The site tripped offline at 13:30 on 05/15 and will remain offline until further notice. | 1. SR101517
Augusta - 13 York Farm Road | ME | 174065.9 | 172198.7 | 1867.2 | 1.084% | 197141 | -23075.1 | -11.7% | 1. Site was offline from 14:00 on 06/22 to 10:00 on 06/23. 2. Site was offline from 23:00 on 06/27 to 15:00 on 06/30. | 1. SR103278 2. PM8453, SR103928 | SR103928
Santa Ana - 1441 West | CA | 79811.375 | 77567.991 | 2243.384 | 2.892% | 81124.633 | -1313.258 | -1.619% | 1. Inverter 3 is producing less power between 11:00 to 14:30 starting from 05/08. | 1. SR101794, SR103308 | SR103308
Jessup -7950 Oceano Ave | MD | 249671.6 | 228605.5 | 21066.1 | 9.215% | 298457 | -48785.4 | -16.35% | 1. Inverter 11 central unit has been RMA'd from 03/31. 2. Inverter 6 had been offline since 05/23 and came back online, resuming production from 06/24 after a firmware update. 3. The middle unit of Inverter 7 has been experiencing frequent trip events since 05/15 and is currently being RMA’d. 4. Inverter 1 went offline on 06/14 due to a "Grid Voltage" issue and came back online at 13:15 on 06/21 and inverter was underproduced 35kW from 06/21 to 06/23. 5. Inverter 7 center unit was being RMA'd. | 1. SR098878 2. SR099915 3. SR101758 4. SR102980 5. SR101758 | SR099915 | SR101758 | SR102980 | SR101758
TX: Fort Worth - 5200 Gold Spike Dr | TX | 0 | 0 | 0 |  | 0 | 0 |  | 1.The site tripped offline at 12:30 on 05/15 and will remain offline until further notice. | 1. SR101493
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Jul
Catalyze |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 5941708.1352 | 7773446.54 | -1831738.4048 | -23.56% | 7522355.17 | -1580647.0348 | -21.01% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 105481.5 | 116640.3 | -11158.8 | -9.567% | 129527.9 | -24046.4 | -18.56% | 1. Inverter 5 has experienced multiple tripping events since 12/30 due to a "Fault to Stop DC Wrong Polarity". Inverter being RMA'D | 1.SR102597
Adelanto - 1 Sheep Creek Road | CA | 0 | 499964 | -499964 | -100% |  |  |  | 1. Site was shut down on 06/18 at 10:15am due to transformer issue till the date 2. No forcasted data available from 03/27 after Aderis has done some backend work. | 1.SR102554
Blackstone - 83 Federal Street | MA | 873092 | 817809.3 | 55282.7 | 6.76% | 921306.5 | -48214.5 | -5.233% | 1. Inverter tripped offline at 17:15 on 07/27 and later backonline at 08:30 on 07/28 | 1.SR105137
Charlton - 299 Worcester Road | MA | 67250.5 | 71010.96 | -3760.46 | -5.296% | 66359.28 | 891.22 | 1.343%
Wareham - 8 Thatcher Drive | MA | 20666.6875 | 21644.77 | -978.0825 | -4.519% | 20765.72 | -99.0325 | -0.4769%
West Yarmouth - 42 Mid Tech | MA | 19231.3944 | 21683.27 | -2451.8756 | -11.31% | 22774.39 | -3542.9956 | -15.56% | 1. Low production/generation due to low irradiance on 07/09, 07/10, 07/27
Harrison - 130 Union Street | NY | 22933.3125 | 32350.12 | -9416.8075 | -29.11% | 32205.39 | -9272.0775 | -28.79% | 1. Inverter 3 was kept offline from 05/29 at 13:00 and being RMA'd. | 1.SR100950
Staten Island - Ellis Storage | NY | 73787.5 | 63480.86 | 10306.64 | 16.24% | 73833.38 | -45.88 | -0.06214%
Amherst - 595 Schoelles Road | NY | 1201793 | 1273216 | -71423 | -5.61% | 1219682 | -17889 | -1.467% | 1.Tracker 2 is currently stuck at 1.25 DEG from 06/13 | 1.SR103022
Lancaster 1 - Gunnville Road | NY | 768592 | 909610.4 | -141018.4 | -15.5% | 927008.5 | -158416.5 | -17.09% | 1.Inverter 2.6 has tripping offline since 06/11, and the inverter is being RMA’d. Inverter 2.4 has been experiencing mid-morning/early afternoon trip events and staying offline since 6/28 2.Site tripped offline at 09:11AM on 07/06 and back online 08:45 on 07/07 | 1.SR103842 2.SR104049 | SR104049
Lancaster 2 - Shisler Road | NY | 840379 | 935735.2 | -95356.2 | -10.19% | 1015648 | -175269 | -17.26% | 1.Site tripped offline at 09:11AM on 07/06 and back online 08:45 on 07/07 2.Inverters 4.6 and 4.8 have been offline since 06/26 due to "Fault Bus Sum High Fault - Fault0130". 3.Inverter 4.9 has mutliple tripping event from 07/26 4.Inverter 4.3 is derating at 35kW from 07/28 at 11:00 and offline on 07/20 | 1.SR104050 2.SR103584 3.SR105109 4.SR105181 | SR103584 | SR105109 | SR105181
Fullerton - 200 W Orangethorpe | CA | 127781.375 | 133872.2 | -6090.825 | -4.55% | 145971 | -18189.625 | -12.46%
El Paso - 10500 Railroad Drive | TX | - | 0 | 0 |  | 0 | 0 |  | 1. The site tripped offline at 12:45 on 05/15 and will remain offline until further notice. | 1.SR101516,SR104969 | SR104969
Friona - 900 Millard Ave | TX | 3678.5 | 112331.1 | -108652.6 | -96.73% | 142280.5 | -138602 | -97.41% | 1. The site tripped offline at 13:30 on 05/15 and will remain offline until further notice. | 1.SR101517,SR104968 | SR104968
Augusta - 13 York Farm Road | ME | 168888.375 | 173690.8 | -4802.425 | -2.765% | 216032.7 | -47144.325 | -21.82% | 1.Site tripped offline at 14:29 on 07/04 and back online at 13:15 on 07/06 2.Site tripped offline at 05:00 on 07/08 and back online at 06:30 on 07/09 3.Site tripped offline at 12:30 on 07/20 and back online at 12:15 on 07/21 | 1.SR104026 2.SR104133 3.SR104663 | SR104133 | SR104663
Santa Ana - 1441 West | CA | 82976.9908 | 81541.26 | 1435.7308 | 1.761% | 87849.61 | -4872.6192 | -5.547%
Jessup -7950 Oceano Ave | MD | 249524 | 239145 | 10379 | 4.34% | 311235.3 | -61711.3 | -19.83% | 1.Inverter 3 middle unit and right unit tripped offline on 07/01 at 16:00 and back online on 07/14 2.Inverter 10 tripped offline at 14:30 on 07/17 and offline throught the month 3. Inverter 7 tripped offline at 06:30 on 07/21 and back online on 07/27 4. inverter 4 unit 4.2 was tripped offline on 04/13 at 12:15 and back online at 11:00 on 07/29 5. Inverter 11 center unit was offline from 03/31 to 12:30 on 07/29. Since 07/29 inverter 11 was underperforming due to string 3 of the left unit requires additional troubleshooting | 1.SR104022 2.SR104573 3.SR104743 4.SR105104 5. SR098878, SR104573 | SR104573 | SR104743 | SR105104 | SR098878 | SR104573
TX: Fort Worth - 5200 Gold Spike Dr | TX | 0 | 869530.1 | -869530.1 | -100% | 895796.2 | -895796.2 | -100% | 1.The site tripped offline at 12:30 on 05/15 and will remain offline until further notice. | 1.SR101493
NY: Clifton Springs - Ontario 2 (21597) | NY | 1315652 | 1400190.9 | -84538.9 | -6.038% | 1294078.8 | 21573.2 | 1.667%
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Aug
Catalyze |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 7152091.3865 | 9146479.4791 | -1994388.0926 | -21.8% | 8866989.26 | -1714897.8735 | -19.34%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA | 100745.75 | 101706.8 | -961.05 | -0.9449% | 130168.7 | -29422.95 | -22.6% | 1. Inverter 5 was offline from 10:00 on 07/21 to 13:00 on 08/06. | 1. SR102597
Adelanto - 1 Sheep Creek Road | CA | 582365 | 593036.6781 | -10671.6781 | -1.799% | N/A |  |  | 1. Inverter 8 was offline from 06:00 on 08/12 to 18:00 on 08/13 and inverter 12 was offline from 12:10 on 08/12 to 18:00 on 08/13 2. Site was offline from 08/01 to 08/10 at 06:00, but on 08/11 inverter 17 didn't start for production later on 08/13 technician brought the inverter 17 back online at 16:00 3. No forcasted data available from 03/27 after Aderis has done some backend work. | 1. SR106140 2. SR103751, SR105980, SR103010 | SR103751 | SR105980 | SR103010
Blackstone - 83 Federal Street | MA | 903613.3 | 863530.9 | 40082.4 | 4.642% | 861697.1 | 41916.2 | 4.864% | 1. Inverter 1 was offline from 09:45 to 11:45 on 08/14 and again offline from 15:30 to 17:45 on 08/17. | 1. SR106259
Charlton - 299 Worcester Road | MA | 70127.25 | 73761.03 | -3633.78 | -4.926% | 64468.03 | 5659.22 | 8.778%
Wareham - 8 Thatcher Drive | MA | 21269.75 | 22087.42 | -817.67 | -3.702% | 19614.07 | 1655.68 | 8.441%
West Yarmouth - 42 Mid Tech | MA | 19575.073 | 21231.41 | -1656.337 | -7.801% | 20373.75 | -798.677 | -3.92%
Harrison - 130 Union Street | NY | 21840.25 | 31590.75 | -9750.5 | -30.87% | 28474.11 | -6633.86 | -23.3% | 1. Inverter 3 was offline for whole month. | 1. SR100950
Staten Island - Ellis Storage | NY | 68122.125 | 60060.39 | 8061.735 | 13.42% | 66123.34 | 1998.785 | 3.023%
Amherst - 595 Schoelles Road | NY | 1024684 | 1096184 | -71500 | -6.523% | 1095828 | -71144 | -6.492% | 1. Site was offline from 07:00 to 08:10 on 08/28. | 1. SR107065
Lancaster 1 - Gunnville Road | NY | 533716 | 849651.8 | -315935.8 | -37.18% | 860164.8 | -326448.8 | -37.95% | 1. Site was offline from 14:15 on 08/17 to 16:00 on 08/26 and inverter 1.9 was LOTO'd for whole month and being RMA'd 2. Inverter 2.6 was offline for whole month and being RMA'd. Inverter 2.4 was offline from 08/01 to16:00 on 08/26 | 1. SR106396, SR100507 2. SR103842 | SR100507 | SR103842
Lancaster 2 - Shisler Road | NY | 719620 | 894279.4 | -174659.4 | -19.53% | 943660.5 | -224040.5 | -23.74% | 1. Inverters 4.6 and 4.8 were offline form 08/01 to 08/04 and inverters were offline from 08/13 to 08:15. Inverters 3.1, 3.3, 3.4, 3.7,3.9,3.10 and 4.9 were offline from 13:15 on 08/18 to 07:15 on 08/20 and again they are offline from 14:00 on 08/21 to 08:00 on 08/22. Inverters 3.1 to 3.3, 3.5 , 3.7, 4.6 and 4.9 were offline from 17:45 on 08/24 to 07:15 on 08/26. Inverters 3.4, 3.6 - 3.10, and 4.1 - 4.3 were offline from 08/27 at 08:00 to End of month. 2. Site was offline from 14:15 on 08/17 to 08:45 on 08/18 3. PAD 4 inverters tripped offline at 16:00 on 08/01 and back online at 06:00 on 08/02. | 1. SR103584 2. SR106397 3. SR105521 | SR106397 | SR105521
Fullerton - 200 W Orangethorpe | CA | 111944.25 | 126225.2 | -14280.95 | -11.31% | 141877.6 | -29933.35 | -21.1% | 1.Inverter 5 was underperforming by 6kW due to shading at afternoon hours | 1.SR099959
El Paso - 10500 Railroad Drive | TX | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was offline for whole month due to TIGO issues. | 1. SR104969
Friona - 900 Millard Ave | TX | 0 | 103994.7 | -103994.7 | -100% | 132600.8 | -132600.8 | -100% | 1. Site was offline for whole month due to TIGO issues. | 1. SR104968
Augusta - 13 York Farm Road | ME | 206157 | 225101.1 | -18944.1 | -8.416% | 204912 | 1245 | 0.6076% | 1. Inverter 4 tripped offline at 09:30 on 08/27 and back online at 06:00 on 08/28 and again inverter 4 was offline from 09:00 on 08/28 to 2. Site was offline from 17:30 on 08/17 to 08:30 on 08/18. 3. Site was offline from 18:45 on 08/14 to 10:00 on 08/15. | 1. SR107030 2. SR106401 3. SR106315 | SR106401 | SR106315
Santa Ana - 1441 West | CA | 76949.3217 | 76157.78 | 791.5417 | 1.039% | 84602.32 | -7652.9983 | -9.046%
Jessup -7950 Oceano Ave | MD | 236247.75 | 227341.4 | 8906.35 | 3.918% | 276198.8 | -39951.05 | -14.46% | 1. Inverter 7 middle and center units were offline from 06/24 to end of the month and inverter 7 right unit was offline from 06:00 on 08/09 to end of the month. 2. Inverter 4 unit 4.1 was offline from 11:00 on 08/23 to end of the month. 3. Inverter 6 was offline from 06:00 on 08/04 to 10:00 on 08/08 4. Inverter 2 was tripped offline on 08/26 at 18:00 5. Inverter 8 unit 8.6 was offline from 09:15 on 08/18 to end of the month. 6. Inverter 11 had string 3 down. | 1. SR104743, SR101758 2. SR106796 3. SR105582 4. SR106973 5. SR107165 6. SR098747 | SR101758 | SR106796 | SR105582 | SR106973 | SR107165 | SR098747
TX: Fort Worth - 5200 Gold Spike Dr | TX | 0 | 783358.2 | -783358.2 | -100% | 837027.9 | -837027.9 | -100% | 1. Site was offline for whole month due to TIGO issues. | 1. SR101493
NY: Clifton Springs - Ontario 2 (21597) | NY | 1220950 | 1302380 | -81430 | -6.252% | 1162995 | 57955 | 4.983% | 1. Site was offline for whole month due to TIGO issues. | 1. SR106827
CA: Oxnard - 2600 Sakioka - System A | CA | 316571.8494 | 381593.5 | -65021.6506 | -17.04% | 362300.5 | -45728.6506 | -12.62% | 1. Inverter 9 was underproducing by 6kW due to afternoon shading.
CA: Oxnard - 2600 Sakioka - System B | CA | 4710.0503 | 349355.8 | -344645.7497 | -98.65% | 368582 | -363871.9497 | -98.72% | 1. Site was curtailed to to 12 kW, despite having a capacity of 1600 kW. | 1. SR105503
NY: Fonda - Montgomery 1 (21601) | NY | 912882.667 | 963851.221 | -50968.554 | -5.288% | 1205319.94 | -292437.273 | -24.26% | 1.Site was offline from 08/14 at 15:15 and it came back online at 17:30 on 08/19 | 1.SR106073

## Sep
Catalyze |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA
Adelanto - 1 Sheep Creek Road | CA
Blackstone - 83 Federal Street | MA
Charlton - 299 Worcester Road | MA
Wareham - 8 Thatcher Drive | MA
West Yarmouth - 42 Mid Tech | MA
Harrison - 130 Union Street | NY
Staten Island - Ellis Storage | NY
Amherst - 595 Schoelles Road | NY
Lancaster 1 - Gunnville Road | NY
Lancaster 2 - Shisler Road | NY
Fullerton - 200 W Orangethorpe | CA
El Paso - 10500 Railroad Drive | TX
Friona - 900 Millard Ave | TX
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD
TX: Fort Worth - 5200 Gold Spike Dr | TX
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Oct
Catalyze |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA
Adelanto - 1 Sheep Creek Road | CA
Blackstone - 83 Federal Street | MA
Charlton - 299 Worcester Road | MA
Wareham - 8 Thatcher Drive | MA
West Yarmouth - 42 Mid Tech | MA
Harrison - 130 Union Street | NY
Staten Island - Ellis Storage | NY
Amherst - 595 Schoelles Road | NY
Lancaster 1 - Gunnville Road | NY
Lancaster 2 - Shisler Road | NY
Fullerton - 200 W Orangethorpe | CA
El Paso - 10500 Railroad Drive | TX
Friona - 900 Millard Ave | TX
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD
TX: Fort Worth - 5200 Gold Spike Dr | TX
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Nov
Catalyze |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA
Adelanto - 1 Sheep Creek Road | CA
Blackstone - 83 Federal Street | MA
Charlton - 299 Worcester Road | MA
Wareham - 8 Thatcher Drive | MA
West Yarmouth - 42 Mid Tech | MA
Harrison - 130 Union Street | NY
Staten Island - Ellis Storage | NY
Amherst - 595 Schoelles Road | NY
Lancaster 1 - Gunnville Road | NY
Lancaster 2 - Shisler Road | NY
Fullerton - 200 W Orangethorpe | CA
El Paso - 10500 Railroad Drive | TX
Friona - 900 Millard Ave | TX
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD
TX: Fort Worth - 5200 Gold Spike Dr | TX
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Dec
Catalyze |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Fresno - 3150 Shaw Ave | CA
Adelanto - 1 Sheep Creek Road | CA
Blackstone - 83 Federal Street | MA
Charlton - 299 Worcester Road | MA
Wareham - 8 Thatcher Drive | MA
West Yarmouth - 42 Mid Tech | MA
Harrison - 130 Union Street | NY
Staten Island - Ellis Storage | NY
Amherst - 595 Schoelles Road | NY
Lancaster 1 - Gunnville Road | NY
Lancaster 2 - Shisler Road | NY
Fullerton - 200 W Orangethorpe | CA
El Paso - 10500 Railroad Drive | TX
Friona - 900 Millard Ave | TX
Augusta - 13 York Farm Road | ME
Santa Ana - 1441 West | CA
Jessup -7950 Oceano Ave | MD
TX: Fort Worth - 5200 Gold Spike Dr | TX
NY: Clifton Springs - Ontario 2 (21597) | NY
CA: Oxnard - 2600 Sakioka - System A | CA
CA: Oxnard - 2600 Sakioka - System B | CA
NY: Fonda - Montgomery 1 (21601) | NY

## Sites
Portfolio: | Catalyze
Site DAS Name | Site | State | Update | DAS
CA Fresno - 3150 Shaw Ave - 19600 [T0275] | Fresno - 3150 Shaw Ave | CA | AEF | PowerTrack
Sheep Creek Solar | Adelanto - 1 Sheep Creek Road | CA |  | Aderis
MA Blackstone - 83 Federal St - 18170 | Blackstone - 83 Federal Street | MA | AEF | PowerTrack
MA Charlton - 299 Worcester Rd - 18063 | Charlton - 299 Worcester Road | MA | AEF | PowerTrack
MA Wareham - 8 Thatcher Ln - 1010 | Wareham - 8 Thatcher Drive | MA | AEF | PowerTrack
MA West Yarmouth - 42 Mid-Tech Drive - 17944 | West Yarmouth - 42 Mid Tech | MA | AEF | PowerTrack
NY Harrison - 130 Union Ave - 18141 | Harrison - 130 Union Street | NY | AEF | PowerTrack
NY Staten Island - 1 Ellis St - 18195 | Staten Island - Ellis Storage | NY | AEF | PowerTrack
NY AMHERST 595 SCHOELLES RD - 18208 | Amherst - 595 Schoelles Road | NY | AEF | Aderis
NY LANCASTER GUNNVILLE RD - SHISLER RD Site 1 - 18237 | Lancaster 1 - Gunnville Road | NY | AEF | PowerTrack
NY LANCASTER GUNNVILLE RD - SHISLER RD Site 2 - 18238 | Lancaster 2 - Shisler Road | NY | AEF | PowerTrack
CA Fullerton - 200 W Orangethorpe - 19603 [T1418] | Fullerton - 200 W Orangethorpe | CA | AEF | PowerTrack
TX El Paso - 10500 Railroad Drive - 19648 | El Paso - 10500 Railroad Drive | TX | AEF | PowerTrack
TX Friona - 900 Millard Ave - 19506 | Friona - 900 Millard Ave | TX | AEF | PowerTrack
ME Augusta - 13 York Farm Rd - 18196 | Augusta - 13 York Farm Road | ME | AEF | PowerTrack
CA Santa Ana - 1441 W 17th St - 21198 [T1936] | Santa Ana - 1441 West | CA | AEF | PowerTrack
MD Jessup 7950 Oceano Ave - 22337 | Jessup -7950 Oceano Ave | MD | AEF | PowerTrack
TX Ft Worth - 5200 Goldspike Drive - 19599 | TX: Fort Worth - 5200 Gold Spike Dr | TX | AEF | PowerTrack
NY: Clifton Springs - Ontario 2 (21597) | NY: Clifton Springs - Ontario 2 (21597) | NY |  | PowerTrack
CA Oxnard - 2600 Sakioka Dr System A - 18249 | CA: Oxnard - 2600 Sakioka - System A | CA | AEF | PowerTrack
CA Oxnard - 2600 Sakioka Dr System B - 21387 | CA: Oxnard - 2600 Sakioka - System B | CA | AEF | PowerTrack
NY FONDA 182 BOSHART RD - Montgomery 1 (21601) | NY: Fonda - Montgomery 1 (21601) | NY |  | PowerTrack