## Year to Date
AB CarVal |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 68768374.4815 | 82825795.7974 | -14057421.3159 | -16.97% | 88537661.6 | -19769287.1185 | -22.33%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 3151077 | 3700216.1863 | -549139.1863 | -14.84% | 3694907.6 | -543830.6 | -14.72%
Bakersfield - 100 Basic School Rd | CA | 12939874.4662 | 13266702.906 | -326828.4398 | -2.464% | 14375545.29 | -1435670.8238 | -9.987%
Fresno - 2685 Cornelia Ave | CA | 17383394 | 27393303.829 | -10009909.829 | -36.54% | 29263308.45 | -11879914.45 | -40.6%
San Juaquin - S. Placer & W. Adams | CA | 9501752.7083 | 10401643.1 | -899890.3917 | -8.651% | 10764363.56 | -1262610.8517 | -11.73%
Charlemont - 0 Tea St | MA | 3160322 | 4478290.1141 | -1317968.1141 | -29.43% | 4333809.7 | -1173487.7 | -27.08%
Amherst - 740 Belchertown Rd | MA | 4476971 | 4686777.2679 | -209806.2679 | -4.477% | 5070950 | -593979 | -11.71%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 10115510.307 | 10007205.337 | 108304.97 | 1.082% | 11361156 | -1245645.693 | -10.96%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 8039473 | 8891657.0571 | -852184.0571 | -9.584% | 9673621 | -1634148 | -16.89%

## 1st Qtr
AB CarVal |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 12232640.7034 | 15942459.6079 | -3709818.9045 | -23.27% | 16168749.4 | -3936108.6966 | -24.34%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 775506 | 810337.697 | -34831.697 | -4.298% | 726216.9 | 49289.1 | 6.787%
Bakersfield - 100 Basic School Rd | CA | 2749226.4665 | 2476003.6 | 273222.8665 | 11.03% | 2623010.6 | 126215.8665 | 4.812%
Fresno - 2685 Cornelia Ave | CA | 2561171 | 4716317 | -2155146 | -45.7% | 5078948 | -2517777 | -49.57%
San Juaquin - S. Placer & W. Adams | CA | 1857715.7083 | 2062015.1 | -204299.3917 | -9.908% | 1834917.4 | 22798.3083 | 1.242%
Charlemont - 0 Tea St | MA | 181386 | 940745.9592 | -759359.9592 | -80.72% | 864647.5 | -683261.5 | -79.02%
Amherst - 740 Belchertown Rd | MA | 769133 | 994560.4431 | -225427.4431 | -22.67% | 936702 | -167569 | -17.89%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 2117077.5286 | 2051748.2212 | 65329.3074 | 3.184% | 2226965 | -109887.4714 | -4.934%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 1221425 | 1890731.5875 | -669306.5875 | -35.4% | 1877342 | -655917 | -34.94%

## 2nd Qtr
AB CarVal |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 21328300.4714 | 27313404.6971 | -5985104.2256 | -21.91% | 29484755.31 | -8156454.8386 | -27.66%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 969450 | 1087459.4871 | -118009.4871 | -10.85% | 1153678.3 | -184228.3 | -15.97%
Bakersfield - 100 Basic School Rd | CA | 4362648 | 4437573.31 | -74925.31 | -1.688% | 4772310.17 | -409662.17 | -8.584%
Fresno - 2685 Cornelia Ave | CA | 4485335 | 9902411.12 | -5417076.12 | -54.7% | 9976377.4 | -5491042.4 | -55.04%
San Juaquin - S. Placer & W. Adams | CA | 3445332 | 3554965.66 | -109633.66 | -3.084% | 3688073.34 | -242741.34 | -6.582%
Charlemont - 0 Tea St | MA | 1025472 | 1286738.1917 | -261266.1917 | -20.3% | 1390750.1 | -365278.1 | -26.26%
Amherst - 740 Belchertown Rd | MA | 1393688 | 1330791.436 | 62896.564 | 4.726% | 1634563 | -240875 | -14.74%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 3148674.4714 | 2919110.1082 | 229564.3632 | 7.864% | 3647860 | -499185.5286 | -13.68%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 2497701 | 2794355.3841 | -296654.3841 | -10.62% | 3221143 | -723442 | -22.46%

## 3rd Qtr
AB CarVal |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 24160166.3066 | 27930690.7199 | -3770524.4133 | -13.5% | 29028669.44 | -4868503.1334 | -16.77%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 1199528 | 1186264.7698 | 13263.2302 | 1.118% | 1178052.2 | 21475.8 | 1.823%
Bakersfield - 100 Basic School Rd | CA | 3944243.9996 | 4359711.66 | -415467.6604 | -9.53% | 4554811.24 | -610567.2404 | -13.4%
Fresno - 2685 Cornelia Ave | CA | 7202166 | 9753868.65 | -2551702.65 | -26.16% | 9706557.61 | -2504391.61 | -25.8%
San Juaquin - S. Placer & W. Adams | CA | 2777741 | 3336240.81 | -558499.81 | -16.74% | 3515280.89 | -737539.89 | -20.98%
Charlemont - 0 Tea St | MA | 1339634 | 1469085.8061 | -129451.8061 | -8.812% | 1414475.5 | -74841.5 | -5.291%
Amherst - 740 Belchertown Rd | MA | 1574519 | 1491706.8107 | 82812.1893 | 5.552% | 1692726 | -118207 | -6.983%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 3072341.307 | 3346118.2224 | -273776.9154 | -8.182% | 3758808 | -686466.693 | -18.26%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 3049993 | 2987693.9909 | 62299.0091 | 2.085% | 3207958 | -157965 | -4.924%

## 4th Qtr
AB CarVal |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 11047267.0001 | 11639240.7725 | -591973.7725 | -5.086% | 13855487.45 | -2808220.4499 | -20.27%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 206593 | 616154.2324 | -409561.2324 | -66.47% | 636960.2 | -430367.2 | -67.57%
Bakersfield - 100 Basic School Rd | CA | 1883756.0001 | 1993414.336 | -109658.3359 | -5.501% | 2425413.28 | -541657.2799 | -22.33%
Fresno - 2685 Cornelia Ave | CA | 3134722 | 3020707.059 | 114014.941 | 3.774% | 4501425.44 | -1366703.44 | -30.36%
San Juaquin - S. Placer & W. Adams | CA | 1420964 | 1448421.53 | -27457.53 | -1.896% | 1726091.93 | -305127.93 | -17.68%
Charlemont - 0 Tea St | MA | 613830 | 781720.1571 | -167890.1571 | -21.48% | 663936.6 | -50106.6 | -7.547%
Amherst - 740 Belchertown Rd | MA | 739631 | 869718.5781 | -130087.5781 | -14.96% | 806959 | -67328 | -8.343%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 1777417 | 1690228.7852 | 87188.2148 | 5.158% | 1727523 | 49894 | 2.888%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 1270354 | 1218876.0947 | 51477.9053 | 4.223% | 1367178 | -96824 | -7.082%

## Jan
AB CarVal |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 3950905.2386 | 4602075.2571 | -651170.0185 | -14.15% | 3574033.6 | 376871.6386 | 10.54%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 212302 | 243217.7892 | -30915.7892 | -12.71% | 174518.6 | 37783.4 | 21.65%
Bakersfield - 100 Basic School Rd | CA | 876708.0303 | 547801 | 328907.0303 | 60.04% | 621297.8 | 255410.2303 | 41.11% | 1.The weather station stopped communicating from 12:30 AM on 01/16/25 due to the SCADA server and Watchdog not running on the server end,later back online at 10:00 AM on 01/27/25. 2. Inverter 1.2 has been derating by 80 kW at 13:30 on 01/28/25 and has self resolved at 6:30am on 01/29/25 due to Internal fan fault | 1. SR095612 2. SR096082 | SR096082
Fresno - 2685 Cornelia Ave | CA | 1178944 | 1571662 | -392718 | -24.99% | 1030154 | 148790 | 14.44% | 1. The site experienced frequent outages throughout the month due to PG&E curtailments. 2. Tracker controller 3, tracker set position 2 reporting erroneous value and tracker position motor 2 was stuck at 50.76 Degrees. Tracker need New encoder. 3. Site was offline from 13:00 to 14:30 on 01/16 4.Combiner boxes 1.19, 1.21, 1.23, 1.25, 1.27, 3.20, 3.22, 3.24, 3.26, 3.28, are underperforming from 12/23/24. Will Investigate during PM inspection 5. Inverter 3 is started late and reporting reversed branch overcurrent on 01/02, 01/03 , 01/17 | 1.SR095240 2. SR094675 3.SR095640 4. SR095229 5. SR094991 | SR094675 | SR095640 | SR095229 | SR094991
San Juaquin - S. Placer & W. Adams | CA | 522765.2083 | 599049.6 | -76284.3917 | -12.73% | 380972.2 | 141793.0083 | 37.22% | 1. Inverter 6 is being RMA'd due to internal board failure. 2. Site was tripped offline on 12/31/24 at 14:00 and came back online on 01/02/25 at 12:00 after the technician re-energized the site and corrected the incorrect Grid Connect rule for Inverter 1. 3. Inverter 1 is started late for production at 8:30AM on 01/17 due to an momentary Isolation Error. | 1.SR095174, SR095112 2. SR095204 3. SR095076 | SR095112 | SR095204 | SR095076
Charlemont - 0 Tea St | MA | 99864 | 266325.2017 | -166461.2017 | -62.5% | 193054 | -93190 | -48.27% | 1. Site was brought back online at 1:15PM on 01/08/25 after the SMA technician repalced the AC control board. 2. Inverter tripped offline at 14:25 on 01/30 later remotely closed at 16:00 on 01/30 | 1.SR093625 2.SR096136 | SR096136
Amherst - 740 Belchertown Rd | MA | 189777 | 290332.7247 | -100555.7247 | -34.63% | 205706 | -15929 | -7.744% | 1.Low generation due to weather/snow.
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 582212 | 571527.0279 | 10684.9721 | 1.87% | 539970 | 42242 | 7.823% | 1. Site was tripped offline at 10:30AM on 01/02/2025. It was brought back online at 2:35PM on same day after technician closing the SEL relay. | 1. SR095236
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 288333 | 512159.9137 | -223826.9137 | -43.7% | 428361 | -140028 | -32.69% | 1. Site was offline at 8:40 AM on 01/15/25. It was brought back online, and communication was restored at 7:05 AM on 01/16/25 after the technician power-cycled the Dell Data Processor on 01/18/25. 2. Inverters have been offline since 01/23/25 and PE brought all DC converters online by replacing the softcharge contactors on 01/24/25. 3. Inverter 2 tripped offline at 15:50 on 01/29 due to loose fiber optic cable causing a false F25 fault which opens the AC breaker and was brought back online on 01/30/25 after the technician charged the main AC breaker. | 1. SR095594 2. SR095883 3. SR096095 | SR095883 | SR096095

## Feb
AB CarVal |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 3635954.5 | 4695270.9438 | -1059316.4438 | -22.56% | 4970555.5 | -1334601 | -26.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 239618 | 252478.3854 | -12860.3854 | -5.094% | 233283.2 | 6334.8 | 2.715%
Bakersfield - 100 Basic School Rd | CA | 814344 | 819337.6 | -4993.6 | -0.6095% | 818347.8 | -4003.8 | -0.4893% | 1. Inverter 1.2 was derated by 80KW on 02/21 due to Intermal fan fault error and is being RMA'D by CES. 2.Inverters 1.1, 2.4, 2.5, 2.6 have consistent late starts on multiple days of the Month due to Isolation or ground fault. On 02/20 technician arrived and stated that multiple modules were broken and need to be replaced. 3.Site stopped communicating from 12:15PM to 17:45PM on 02/27. Energy data was not backfilled. | 1.SR096082 2.SR096248 3.SR097890 | SR096248 | SR097890
Fresno - 2685 Cornelia Ave | CA | 785248 | 1206122 | -420874 | -34.89% | 1544081 | -758833 | -49.14% | 1. The site experienced frequent outages throughout the month due to PG&E curtailments. 2. Inverter 3 tracker controller 3 motor 2 position stuck at 50.76 Degrees. Tracker need New encoder. On 02/07 Tech replaced encoder on tracker 2. After replacing encoder, tech logged into PLC and cleared encoder fault. Array began tracking correctly. Tech also found tracker 3 motor 4 array to be stuck in the east position. Tech troubleshot motor control box and cleared fault 3.Inverter 3 has multiple tripping events through out the month due to Reverse Branch Overcurrent fault and tripped offline from 02/24 at 14:30 due to DC over current fault. On 02/25 tech checked in and stated that Ground fault fuses needed. 4.Tracker 3 motor 4 is stuck at 51.83 degrees; setpoint is -52 degrees from 02/02 due to Critical torque tube failure and encoder needs to be replaced. 5.Site has stopped communicating at 14:15 on 02/26 due to ground fuse blown and after tech turned DC and AC power back on and aux cabinet power returned, and communications restored at 11:30 on 02/27. | 1.SR095240 2.SR094675 3.SR094991, SR097738 & SR097867 4.SR096704 5.SR097845 | SR094675 | SR094991 | SR097738 | SR097867 | SR096704 | SR097845
San Juaquin - S. Placer & W. Adams | CA | 527379.5 | 594082.8 | -66703.3 | -11.23% | 562070.1 | -34690.6 | -6.172% | 1.Inverter 6 is being RMA'd due to internal board failure since 12/27/24 and back online at 14:45 on 02/27/25 after tech replaced RMA'd Inverter with new inverter. 2.Site tripped offline at 8:45AM on 02/05 and back online at 11:45AM on 02/07 after tech closed the reclouser and re-enerzised the site. | 1.SR095174, SR095112 2.SR096337 | SR095112 | SR096337
Charlemont - 0 Tea St | MA | 18183 | 294907.1728 | -276724.1728 | -93.83% | 262008.4 | -243825.4 | -93.06% | 1. Inverter was tripping on/off on 02/01 & 02/02 due to contact fault in the DCs.Site was taken offline from 09:50 to 10:20 on 02/04 due to technician checked-in to perform hard resets of all SMA devices,power cycled the inverter at the start/stop switch, all DC/DC combiners were power cycled at the start/stop switch and internal AC breaker later meter stopped communicating from 02/06 to 02/08 but production can be confirmed at inverter level, due to that Actual energy was low. Inverter was offline from 02/13 and back online at 14:05 on 02/19. Site was taken offline from 13:40 to 15:00 on 02/20 due to technician on site to repair the Inverter. Again tripped offline from 02/20 at 15:30 due to AC Separating Point fault till date. 2.Site was offline on 02/18 due to utility outage and back online at 14:05 on 02/19 after technician re-enerzised. | 1.SR096224 2.SR097244
Amherst - 740 Belchertown Rd | MA | 189719 | 310307.2138 | -120588.2138 | -38.86% | 282634 | -92915 | -32.87% | 1.The underperformance is due to a weather event, and no outage events were observed during the month of February.
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 662855 | 626007.4576 | 36847.5424 | 5.886% | 692519 | -29664 | -4.283% | 1. Inverter 2 was taken offline from 3:20 PM to 4:55 PM on 02/19/25 by the PE technician to inspect the PE retrofit snow kit. | 1. SR097528
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 398608 | 592028.3142 | -193420.3142 | -32.67% | 575612 | -177004 | -30.75% | 1. Site was taken offline by Eversource for maintenance work from 02/03/25 to 02/06/25. The utility restored the system each afternoon and took it offline again the next day during this period. 2. Inverter 1 & 2 tripped offline at 02:30PM on 02/06/25 due to a F154:Fb DC Breaker 2 fault. On 02/07/25, the technician went through the recommended PE reset procedure of keying off the inverter, the inverter was keyed back on at 03:15 and was able to clear the fault and begin producing power at the expected rate the same day. 3. Inverter module 4 was offline on 02/20/25. The technician re-enabled module 4 and brought it back online at 12:45 the same day. | 1. SR096254 2. SR096363 3. SR097551 | SR096363 | SR097551

## Mar
AB CarVal |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 4645780.9648 | 6645113.407 | -1999332.4422 | -30.09% | 7624160.3 | -2978379.3352 | -39.07%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 323586 | 314641.5225 | 8944.4775 | 2.843% | 318415.1 | 5170.9 | 1.624% | 1.Site tripped offline at 14:40 on 03/13 and back online at 12:15PM on 03/14 after technician reset SEL Relay. | 1.SR098555
Bakersfield - 100 Basic School Rd | CA | 1058174.4362 | 1108865 | -50690.5638 | -4.571% | 1183365 | -125190.5638 | -10.58% | 1.Inverter 1.2 was RMA'D from 02/21 and on 03/21 technician replaced RMA'D inverter with new chint inverter. 2.Inverters 1.1, 2.4, 2.5, 2.6 have consistent late starts on multiple days of the month due to Isolation or ground fault. 3.Tracker Controller 2 Motor 2 is stuck at 8:15AM on 03/03 and back in track at 7:45AM on 03/05. | 1.SR096082 2.SR098340 3.SR097932 | SR098340 | SR097932
Fresno - 2685 Cornelia Ave | CA | 596979 | 1938533 | -1341554 | -69.2% | 2504713 | -1907734 | -76.17% | 1. Inverter 1 has been underproducing by 500 kW compared to Inverter 2 since 03/25/25. On 03/28/25, the technician performed inverter testing and noticed a white sedan with two individuals working on wire maintenance in the array. This may have impacted combiner production, and the underperformance decreased to 200 kW, it requiresadditional troubleshooting. 2. Tracker 3 motor 4 is stuck at 51.83 degrees; setpoint is -52 degrees from 02/02 due to Critical torque tube failure and encoder needs to be replaced. 3. Inverter 3 is offline at 14:30 from 02/24, through out the month due to ground fault and parts being replaced. 4. The site experienced frequent curtailments throughout the month from PG&E. 5. Tracker controller 1 tracker position motor 1 is stuck at -39.20 degrees at 07:45 on 03/31 | 1. SR098969 2. SR096704 3. SR097867, SR097738 4. SR095240, SR098618 5. SR099296 | SR096704 | SR097867 | SR097738 | SR095240 | SR098618 | SR099296
San Juaquin - S. Placer & W. Adams | CA | 807571 | 868882.7 | -61311.7 | -7.056% | 891875.1 | -84304.1 | -9.452% | 1. Inverter 6 was offline from 06:00 AM to 07:00 AM on 03/04 and later self-resolved. 2. Inverters 1 to 5 and 8 to 13 tripped offline from 12:15 PM to 15:45 PM on 03/05 due to a technician being on site. | 1. SR095174 2. SR095174 | SR095174
Charlemont - 0 Tea St | MA | 63339 | 379513.5847 | -316174.5847 | -83.31% | 409585.1 | -346246.1 | -84.54% | 1.Inverter 1 tripped offline at 03:25PM on 02/20 due to AC Separating Point fault and back online at 10:40AM on 03/03 after both ameresco and SMA technicians repaired. Inverter again tripped offline at 12PM on 03/04 due to AC Separating Point fault and back online at 10AM on 03/25 after technician repiared a loose control wire on AC breaker was causing intermittent issues. Inverter was offline from 12:20 to 14:40 due to pilot deployment on 03/27. Again tripped offline at 10AM on 03/31 to finish pending pilot deployment. | 1.SR096224, SR098038 & SR099232 | SR098038 | SR099232
Amherst - 740 Belchertown Rd | MA | 389637 | 393920.5046 | -4283.5046 | -1.087% | 448362 | -58725 | -13.1% | 1.Site tripped offline from 9:25 to 13:55 on 03/13. Due to technician on site | 1.PM10676
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 872010.5286 | 854213.7357 | 17796.7929 | 2.083% | 994476 | -122465.4714 | -12.31% | 1.Site was offline from 12:25 to 14:20 on 03/20 due to Utility Outage. | 1.SR098832
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 534484 | 786543.3596 | -252059.3596 | -32.05% | 873369 | -338885 | -38.8% | 1.The site was offline from 08:45 AM to 03:35 PM on 03/03 due to a planned utility outage. 2.Site has low production on 03/05, 03/06 , 03/16, 03/17, 03/24,03/30 due to bad weather. | 1. SR097990

## Apr
AB CarVal |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 5564676.4714 | 8050779.1141 | -2486102.6426 | -30.88% | 8880847.1 | -3316170.6286 | -37.34%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 349562 | 335399.0214 | 14162.9786 | 4.223% | 357592.3 | -8030.3 | -2.246% | 1. Site tripped offline at 17:45 on 04/15 and later technician closed the SEL recloser, and the site came back online at 11:15 AM on 04/16 | 1. SR099863
Bakersfield - 100 Basic School Rd | CA | 1209796 | 1250774 | -40978 | -3.276% | 1397262 | -187466 | -13.42% | 1. Site was offline from 12:45pm to 03:00pm PDT on 04/02. 2. Inverter 1.2 was derated by 80kW from 04/01 to 04/28 after replacing comms board by CPS on 04/28 the inverter started to derate by 20kW. 3.Inverter 1.1, 2.4 and 2.6 started late on 04/01 at 07:45am and again started late on 04/04 at 07:00am | 1. SR099330 2. SR099275, SR099909 3. SR098340 | SR099275 | SR099909 | SR098340
Fresno - 2685 Cornelia Ave | CA | 567887 | 2735287 | -2167400 | -79.24% | 2979124 | -2411237 | -80.94% | 1. The site experienced frequent curtailments throughout the month from PG&E. 2.Inverter 3 tripped offline on 02/24. On 04/10, a technician re-energized the inverter, and it was back online at 12:00 PM. However, the inverter tripped offline again on 04/11 at 07:00 AM due to a DC overvoltage. On 04/14, a technician was on site and found a blown GFDI fuse, which allowed fault current to pass through the line, damaging the R3 resistor. The technician also discovered three broken modules and one faulty home run on Inverter 3. The inverter remained offline. On 04/21, the technician troubleshot the Inverter 3 combiner boxes and replaced the necessary parts. The inverter was re-energized and brought back online at 6:00 PM. On 04/24, the technician returned to the site and successfully restored the combiner boxes associated with Inverter 3. A total of 10 combiner boxes (CBs) were brought back online and further troubleshoot unit 2 side to get the inverter 3 back up to full capacity. 3. Inverter 1 was underproduced by 500 kW compared to Inverter 2 due to tracker 1 motor 1 stuck -39degrees, motor stuck at -18degree for alternative days starting from 03/25. On 04/09, Inverter 1 tripped offline. A technician reset the breaker, and the inverter was back online on 04/10 at 5:30 PM. On 04/22, Inverter 1 was derated by 2,800 kW due to an AC switch fault. At 9:30 AM the same day, it tripped offline again due to an AC Switch Breaking Fault and Overload Protection Fault affecting both Unit 1 and Unit 2. A technician was on site on 04/24 and successfully brought the inverter back online. However, Module 1 remains offline. 4. On 04/10 at 17:40, Inverter 2 was operating at only 50% capacity because Module 1 was offline due to a "Backup Power Supply Abnormal" fault. A technician was able to reset Unit 1 on 04/14, and Inverter 2 resumed normal production. 5. Tracker 2 motor 2 and 4, tracker 3 motor 2 being stuck for alternative days and encoder being replaced. | 1. SR095240, SR098618 2. SR099707, SR099905, SR100397 3. SR098969, SR100138, SR099905, SR099296 4. SR099719, SR099707 5. SR099296 | SR098618 | SR099707 | SR099905 | SR100397 | SR098969 | SR100138 | SR099905 | SR099296 | SR099719 | SR099707 | SR099296
San Juaquin - S. Placer & W. Adams | CA | 996777 | 1019173 | -22396 | -2.197% | 1093936 | -97159 | -8.882% | 1. Summit energy was on site on 04/23 to work on CT of meter and took site offline from 10:15 to 13:15. | 1. SR092199, SR099408 | SR099408
Charlemont - 0 Tea St | MA | 258439 | 429887.8824 | -171448.8824 | -39.88% | 444628.8 | -186189.8 | -41.88% | 1.Inverter 1 was tripped offline at 10AM on 03/31 and back online at 14:05 on 04/09. SMA technician completed the pilot deployments. | 1.SR096136
Amherst - 740 Belchertown Rd | MA | 450159 | 429678.9791 | 20480.0209 | 4.766% | 514837 | -64678 | -12.56% | 1. The site production was dropped from 2470kW to 27kW on 04/01 as technician was onsite performing PM event. 2. The site is experiencing data quality issues—ambient temp gaps, faulty low-temp readings (~6550), incorrect module temperatures, and one missing pyranometer. These impact performance analysis and PVsyst modeling. Ticket created on 04/30/25; Ameresco ROC is investigating. 3. Site production was low on 04/03, 04/05, 04/07, 04/10 and 04/11 due to rain. | 1. PM13562 2. SR100719
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 1031730.4714 | 939764.6634 | 91965.808 | 9.786% | 1105608 | -73877.5286 | -6.682%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 700326 | 910814.5677 | -210488.5677 | -23.11% | 987859 | -287533 | -29.11% | 1.Meter is capturing only inverter 1 data and inverter 1 was derating on multiple days of the month. | 1.SR099273

## May
AB CarVal |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 7200052 | 9205968.7669 | -2005916.7669 | -21.79% | 10199555.07 | -2999503.07 | -29.41%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 376615 | 367019.0165 | 9595.9835 | 2.615% | 390136.9 | -13521.9 | -3.466% | 1. Site was taken offline at 08:15 to 10:05 on 05/27 due technition was on site to take DGA samples. 1. Site tripped offline at 11:40 on 05/28 and later technician closed the SEL recloser, and the site came back online at 08:35 on 05/29. | 1. PM9804 2. SR102048
Bakersfield - 100 Basic School Rd | CA | 1543190 | 1562688.88 | -19498.88 | -1.248% | 1663413.73 | -120223.73 | -7.228% | 1. Inverter 1.2 was derated by 20 kW since 04/28. Chint remotely re-energized the inverter on 04/29 but still inverter is derating. from 05/02 inverter producing expected possibly due to all DC Switchs are in operation. | 1. SR099275, SR099909,SR096082 | SR099909 | SR096082
Fresno - 2685 Cornelia Ave | CA | 1529058 | 3539921.72 | -2010863.72 | -56.81% | 3468101.2 | -1939043.2 | -55.91% | 1. The site experienced frequent curtailments throughout the month from PG&E. 2. Inverter 3 was producing at half of its capacity for the entire month because circuit breakers CB 3.1 to CB 3.10 were isolated by a technician. This was done because the inverter would fault when operating at its rated capacity. On 05/13 inverter was taken offline from 12:15 to 15:30 to troubleshoot and it required further troubleshooting. 3. CB 2.6 and CB 2.21 are offline for whole month. 4. Inverter 1 was offline from 05/01 to 05/21 due to bad AC breakers on 05/20 Inverter 1 AC breaker has been replaced and re-energized by PPS and Ameresco technician. | 1. SR095240 2. SR100397, SR101962 3. SR102333 4. SR100138 | SR100397 | SR101962 | SR102333 | SR100138
San Juaquin - S. Placer & W. Adams | CA | 1205619 | 1254897.27 | -49278.27 | -3.927% | 1273551.34 | -67932.34 | -5.334%
Charlemont - 0 Tea St | MA | 372549 | 373087.8292 | -538.8292 | -0.1444% | 466328.9 | -93779.9 | -20.11%
Amherst - 740 Belchertown Rd | MA | 438172 | 414418.9424 | 23753.0576 | 5.732% | 558634 | -120462 | -21.56% | 1. The site is experiencing data quality issues, including ambient temperature gaps, faulty low-temperature readings (~6550), incorrect module temperatures, and one missing pyranometer. These issues are impacting performance analysis and PVsyst modeling. A ticket was created on 04/30/25. After Aaron’s inspection, it was found that the module temperature sensors are off by a factor of 25°C. Additionally, Pyranometer 6 is the GHI sensor attached to the albedometer; however, we do not see a pyranometer associated with the IRR down of the albedometer. This reading should be coming from the same sensor as Pyranometer 6. | 1. SR100719
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 943484 | 871480.654 | 72003.346 | 8.262% | 1273112 | -329628 | -25.89% | 1. Values for IRR sensor for the GHI, Albedometer up or albedometer down, Ambient temperature sensor are not available in PF Drive. Waiting for response from PF drive. | 1. SR102053
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 791365 | 822454.4547 | -31089.4547 | -3.78% | 1106277 | -314912 | -28.47% | 1. Inverter 1 was underproducing by 800 kW on 05/01. On 05/02, the technician found the combiner handle in the OFF position. The system was fully tested, passed all checks, and was brought back online. Power levels returned to normal on 05/02. 2. Inverter 1 again started underproducing by 1300kW from 05/30 to end of month due to the fan that is not communicating that is forcing a derate to the 675 kW Limit. | 1. SR100841 2. SR102282 | SR102282

## Jun
AB CarVal |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 8563572 | 10056656.8162 | -1493084.8162 | -14.85% | 10404353.14 | -1840781.14 | -17.69%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 243273 | 385041.4491 | -141768.4491 | -36.82% | 405949.1 | -162676.1 | -40.07% | 1. Inverters 1,3 & 5 are derating by approximately 40kW each from 09:20 on 06/05 and reporting "PF200 - Production Degraded".Additionally Inverter 6 is derating by approximately 40KW and reporting "PF200 - Production Degraded" since on 06/06. later on 06/09 technician checked into the site and he check all cb's and modules and found that all modules have a high degree of pollen. all inverters resolved and returned to normal operation on 06/09. 2. The site was taken offline at 10:10 on 06/13 due to a planned outage. A technician was on site to disconnect the UPS and relay batteries. Later, the technician reconnected all the batteries and re-energized the site. The site was back online at 13:00 on 06/24. 3. Inverter 11 is underperforming by 10KW at 14:55 on 06/24. 4. Inverter 4 is derating approximately by 55kW from 09:00 on 06/29 and reporting "PF200 - Production Degraded". | 1. SR102542, SR102680 2. SR102548 3. SR103448,SR102548 4. SR103714 | SR102680 | SR102548 | SR103448 | SR102548 | SR103714
Bakersfield - 100 Basic School Rd | CA | 1609662 | 1624110.43 | -14448.43 | -0.8896% | 1711634.44 | -101972.44 | -5.958%
Fresno - 2685 Cornelia Ave | CA | 2388390 | 3627202.4 | -1238812.4 | -34.15% | 3529152.2 | -1140762.2 | -32.32% | 1. The site experienced frequent curtailments throughout the month from PG&E. 2. Inverters 1, 2, and 3 tripped offline at 09:53 on 06/10, reporting 'Islanding Protection.' After a remote reclose, the inverters were back online at 10:50 on 06/10. Additionally, the site tripped offline again at 14:25 on 06/10. A remote reset was performed, and the site came back online at 05:15 on 06/11. The inverters 1, 2, and 3 has tripped offline again at 16:30 on 06/15. After another remote reset, the site was back online at 04:45 on 06/16 3. CB 2.6 and CB 2.21 went offline on 06/02. A technician was on site on 06/05 and worked on the inverter fuses and circuit breakers. Further troubleshooting is required, and both the CBs and inverter fuses need to be checked. 4. DC zones 3.5, 3.7, 3.20 are offline and DC zones 3.19, 3.22, 3.24, 3.3, 1.22, 1.24 are underperforming since 06/18. 5. Inverter 2 tripped offline at 15:15 on 06/26. A technician was on site on 06/30 and found that the inverter had experienced a high oil temperature. The temperature has since returned to normal, and the inverter was brought back online at 10:15 on 06/30. 6. Inverter 3 was producing at half of its capacity for the entire month because circuit breakers CB 3.1 to CB 3.10 were isolated by a technician. This was done because the inverter would fault when operating at its rated capacity. On 05/13 inverter was taken offline from 12:15 to 15:30 to troubleshoot and it required further troubleshooting. later on 06/09 technician repaired homerun cable and bring the inverter to the normal operation on 06/09. again started Inverter 3 was producing at half of its capacity for the entire month since 06/12 and it required further troubleshooting. | 1. SR095240 2. SR102767 3. SR102333 4. SR102731 5. SR103640, SR103633 6. SR100397, SR101962,SR103633 | SR102767 | SR102333 | SR102731 | SR103640 | SR103633 | SR100397 | SR101962 | SR103633
San Juaquin - S. Placer & W. Adams | CA | 1242936 | 1280895.39 | -37959.39 | -2.964% | 1320586 | -77650 | -5.88%
Charlemont - 0 Tea St | MA | 394484 | 483762.4802 | -89278.4802 | -18.46% | 479792.4 | -85308.4 | -17.78% | 1. The inverter and batteries went offline at 09:50 on 06/25, as a technician and electrician were on site to perform a planned shutdown. Later, on 06/26, the technician returned and re-energized the inverter, inverter communications, auxiliary power, BESS, and DPS units. The system was fully back online at 16:20 on 06/26. | 1. SR103455
Amherst - 740 Belchertown Rd | MA | 505357 | 486693.5145 | 18663.4855 | 3.835% | 561092 | -55735 | -9.933%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 1173460 | 1107864.7908 | 65595.2092 | 5.921% | 1269140 | -95680 | -7.539%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 1006010 | 1061086.3616 | -55076.3616 | -5.191% | 1127007 | -120997 | -10.74% | 1. Inverter 1 was underproducing by approximately 1300 kW from 05/30 due to a non-communicating fan, which forced the inverter to derate to the 675 kW limit. On 06/03, PE inspected the unit, replaced the fan, and the inverter returned online and has been producing as expected since 06/03. 2. Inverters 1 and 2 went offline at 14:50 on 06/07. On 06/08, a technician checked in and reset the inverters. Both inverters were back online by 11:15 on 06/08 | 1. SR102282 2. SR102650 | SR102650

## Jul
AB CarVal |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 8153754 | 10328735.0957 | -2174981.0957 | -21.06% | 10844829.8 | -2691075.8 | -24.81%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 410498 | 413780.5264 | -3282.5264 | -0.7933% | 435349.3 | -24851.3 | -5.708% | 1. The site tripped offline at 13:50 on 07/07 due to a utility outage. On 07/08, a technician closed the recloser, and the site came back online at 11:25. 2. Inverter 11 is underperforming by 10KW at 14:55 on 06/24. Required mowing | 1. SR104118 2. SR103448 | SR103448
Bakersfield - 100 Basic School Rd | CA | 1559636 | 1659526.31 | -99890.31 | -6.019% | 1669196.89 | -109560.89 | -6.564% | 1. Inverter 1.5 is derating daily due to an 'External fan fault.' On 07/17, a technician inspected the external fans and found that two out of five were not working. The technician contacted Chint and initiated the RMA process for new external fans. 2. All inverters are intermittently derating in the afternoon hours during high irradiance. PMA is the failure, need to be investigate. | 1. SR104525 2. SR103837 | SR103837
Fresno - 2685 Cornelia Ave | CA | 2587774 | 3673909.7 | -1086135.7 | -29.56% | 3619661.9 | -1031887.9 | -28.51% | 1. The site experienced frequent curtailments throughout the month from PG&E. 2. The site tripped offline at 14:15 on 07/28 due to "Islanding Protection" and later came back online at 09:30 on 07/29 after remote reset. 3. Inverter 2 tripped offline at 14:45 on 07/20. On 07/21 technician found inverter was faulted with Oil Temp high alert. After troubleshooting inverter was back online at 16:15. 4. DC zones 3.5, 3.7, 3.20 are offline and DC zones 3.19, 3.22, 3.24, 3.3, 1.22, 1.24 are underperforming since 06/18. Required further troubleshooting. | 1. SR095240 2. SR105269 3. SR104667 4. SR102731 | SR105269 | SR104667 | SR102731
San Juaquin - S. Placer & W. Adams | CA | 740140 | 1277273 | -537133 | -42.05% | 1312466.01 | -572326.01 | -43.61% | 1. Inverter 3 tripped offline at 11:44 on 07/14 due to "Fault Loss of Main - GridV.OutLim" while a technician was on site and later came back online at 12:28 on the same day. 2. All inverters are intermittently derating in the peak hours during high irradiance. Working with CPS to resolve the issue. 3. Inverter 12 tripped offline at 15:10 on 07/01 due to 'Fault Bus Imbalance - Protect0070.' On 07/02, a technician found that all six fuses were blown. On 07/11, the technician replaced the old inverter with a new one, but found that the inverter was producing but not communicating. On 07/14, the technician stated that a new communications board needs to be RMA'd. | 1. SR104424 2. SR103838 3. SR103862 | SR103838 | SR103862
Charlemont - 0 Tea St | MA | 460390 | 524371.3742 | -63981.3742 | -12.2% | 518049.7 | -57659.7 | -11.13% | 1. The inverter was offline for PV production in the afternoon on 07/22 and remained offline for PV production on 07/23.Waiting for the response from IHI. 2. The inverter tripped offline at 16:25 on 07/17 due to the AC breaker switch was in 'Open' state and later came back online at 17:00 after a remote reset. 3. The inverter went offline overnight on 07/18 and later came back online at 08:10 on the same day after a remote reset. 4. The inverter went offline overnight on 07/30 and later came back online at 09:40 on the same day after a remote reset. | 1. SR103391 2. SR104578 3. SR104598 4. SR105332 | SR104578 | SR104598 | SR105332
Amherst - 740 Belchertown Rd | MA | 552903 | 480535.1211 | 72367.8789 | 15.06% | 619548 | -66645 | -10.76% | 1. Zone 4 was disabled on 07/02 as it was obstructing the system's operation. On 07/09, Zone 4 was reset via the ShortBus tool and became operational again. However, later that same day, it went offline again due to Alarm Code (6) – "Mod Softcharge Timeout." After a subsequent reset, all zones were back in operation on 07/09. | 1. SR103937, SR104116 | SR104116
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 726125 | 1135976.42 | -409851.42 | -36.08% | 1428393 | -702268 | -49.16% | 1. Huxley 1 DC2 was offline on 07/14 and was brought back online the same day by a remote reset. 2. Huxley 2 Zone 3 was offline on 07/14 and was brought back online the same day by a remote reset. However, it went offline again on 07/15 and will remain offline until further notice. 3. Zone 2 was went offline on 07/14 and 07/15 and back operational by a remote reset. | 1. SR104384 2. SR104385 3. SR104411 | SR104385 | SR104411
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 1116288 | 1163362.644 | -47074.644 | -4.046% | 1242165 | -125877 | -10.13% | 1. The site went offline at 23:00 on 07/29 and came back online at 12:20 on 07/30 after the recloser was remotely closed. 2. Beacon 2 DC1 was offline on 07/09. On 07/10, the technician found no issues with DC1 but discovered that DC3 was disabled. To resolve the issue, the technician briefly took the site offline, reset the network gear, and restored DC3. All four DCs were back online as of 07/10. | 1. SR104659 2. SR104193 | SR104193

## Aug
AB CarVal |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 9282557.818 | 9843754.7855 | -561196.9675 | -5.701% | 9849421.94 | -566864.122 | -5.755%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 447547 | 440217.3483 | 7329.6517 | 1.665% | 401728.6 | 45818.4 | 11.41% | 1.Inverter 11 has been performing as expected since 08/26. On 08/26, the technician replaced the fans, and since then, Inverter 11 has been producing as expected. | 1.SR103448
Bakersfield - 100 Basic School Rd | CA | 1345437.511 | 1492316.35 | -146878.839 | -9.842% | 1548927.35 | -203489.839 | -13.14% | 1. Inverter 1.9 is being RMA'd from 07/10. 2.Inverter 1.4 tripped offline due to and reporting Fault Inverter Hardware Over Current - Protect0140 at 7:59 to 14:30 on 08/20. Again tripped offline due to and reporting Fault Inverter Hardware Over Current - Protect0140 at 13:45 from 08/21 | 1.SR104291 2.SR106840 | SR106840
Fresno - 2685 Cornelia Ave | CA | 2947204 | 3380580.95 | -433376.95 | -12.82% | 3274476.71 | -327272.71 | -9.995% | 1.Tracker Controller 2 Tracker position motors has stuck, setpoint is at -52 from 08/03/25 and later tracking from 08/08. 2.Combiner Box 3.7 is offline and CBs 3.19, 3.24, 1.22, 1.24 are underperforming 08/08/2025 3. Tracker controller 2 position motor 1 stuck on 08/15 and later self resolved on 08/18 but having issues 4. Inverter 3 is derating and reporting AC Switch fault. Likely 1 of 2 units are offline on 08/28.Inverter 3 CB 3.22 offline on 08/30. 5.The site experienced frequent curtailments throughout the month from PG&E. 6.Site was curtailed to 100% (to 0 MW) by the CAISO. But the site didn't follow the commands. Inverter 1 didn’t follow the curtailment command and continued produced from 08/27 | 1.SR105726 2.SR105880 3.SR106361 4.SR107086 5.SR095240 6.SR107235 | SR105880 | SR106361 | SR107086 | SR095240 | SR107235
San Juaquin - S. Placer & W. Adams | CA | 1099899 | 1122941.11 | -23042.11 | -2.052% | 1193145.88 | -93246.88 | -7.815%
Charlemont - 0 Tea St | MA | 439866 | 508374.513 | -68508.513 | -13.48% | 480907.4 | -41041.4 | -8.534% | 1. Inverter was tripped offline at 17:05 on 08/01 and later back online at 08:30 on 08/02 2.Inverter was tripped offline at 13:20 on 08/11 and later back online at 16:00 on 08/12. 3. Site was offline from 08:30 to 10:30 on 08/28 due to NG planned outage 4.Inverter started for production at 08:55 on 08/25 Inverter started late for the production at 13:00 on 08/31. | 1.SR105523 2.SR106036 3. SR107069 4.SR107172 | SR106036 | SR107069 | SR107172
Amherst - 740 Belchertown Rd | MA | 561050 | 550179.5232 | 10870.4768 | 1.976% | 577264 | -16214 | -2.809% | 1. Site was offline from 13:45 to 16:00 on 08/11 | 1.SR106018
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 1307316.307 | 1212685.578 | 94630.729 | 7.803% | 1281513 | 25803.307 | 2.014% | 1.Huxley 2 inverter module 6 is offline on 08/06 and back online at 16:00 on 08/06 | 1.SR105736
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 1134238 | 1136459.413 | -2221.413 | -0.1955% | 1091459 | 42779 | 3.919%

## Sep
AB CarVal |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 6723854.4886 | 7758200.8387 | -1034346.3501 | -13.33% | 8334417.7 | -1610563.2114 | -19.32%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 341483 | 332266.8951 | 9216.1049 | 2.774% | 340974.3 | 508.7 | 0.1492%
Bakersfield - 100 Basic School Rd | CA | 1039170.4886 | 1207869 | -168698.5114 | -13.97% | 1336687 | -297516.5114 | -22.26% | 1. Inverter 1.9 was offline for whole month and being RMA'd. 2.Inverter 1.4 tripped again tripped offline due to and reporting Fault Inverter Hardware Over Current - Protect0140 at 13:45 from 08/21 and remained offline throughout the month. 3. Inverter 2.6 tripped offline at 11:45 on 09/21 and left offline for whole month | 1. SR104291 2. SR106840 3. SR108325 | SR106840 | SR108325
Fresno - 2685 Cornelia Ave | CA | 1667188 | 2699378 | -1032190 | -38.24% | 2812419 | -1145231 | -40.72% | 1. Combiner Box 3.22 went offline on 09/04, and DC Zones 3.19, 3.21, 3.24, and 3.26 have been underperforming. and on 09/24, CB 3.22, 3.7 offline, CB 3.19, 3.21, 3.24, 3.26, 2.19 are underperforming. 2. Tracker controller 2 motor 1 is stuck from 9/6/25. Reporting "TrackerPos1 position (51.690) is outside acceptable range of Set Point (-52.000). Error limit is: 4.000". and also tracker controller 3 motor 4 is intermittently getting stuck from 9/21/25. 3. Inverter 3 CB 3.22 offline since 08/30. 4. The site experienced frequent curtailments throughout the month from PG&E. 5. Site was curtailed to 100% (to 0 MW) by the CAISO. But the site didn't follow the commands. Inverter 1 didn’t follow the curtailment command and continued produced from 09/05. 6. The site tripped offline from 11:00 to 11:45 on 09/04, and again tripped offline at 02:42 on 09/04 and back online at 19:00 on 09/04. 7. Inverter 3 has been derating by approximately 1500 kW since 09/25 and reported an "AC Switch Fault" on 09/26. A technician power cycled the inverter both units, after which the inverter came back online and resumed normal production along with its peers. | 1. SR105880, SR107769, SR107393 2. SR106361, SR107812 3. SR107086, SR107393 4. SR095240 5. SR107235 6. SR108482 7. SR108565 | SR107769 | SR107393 | SR106361 | SR107812 | SR107086 | SR107393 | SR095240 | SR107235 | SR108482 | SR108565
San Juaquin - S. Placer & W. Adams | CA | 937702 | 936026.7 | 1675.3 | 0.179% | 1009669 | -71967 | -7.128%
Charlemont - 0 Tea St | MA | 439378 | 436339.9189 | 3038.0811 | 0.6963% | 415518.4 | 23859.6 | 5.742%
Amherst - 740 Belchertown Rd | MA | 460566 | 460992.1664 | -426.1664 | -0.09245% | 495914 | -35348 | -7.128%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 1038900 | 997456.2244 | 41443.7756 | 4.155% | 1048902 | -10002 | -0.9536%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 799467 | 687871.9339 | 111595.0661 | 16.22% | 874334 | -74867 | -8.563% | 1. The site was offline at 08:20 to 13:15 on 09/04 due to utility planned outage. and again site was offline at 09:00 on 09/05 and after remotely reset site is back online at 14:45 on 09/05. 2. Zone 3 and DC - DC converter 3 is in shutdown at 08:30 to 10:45 on 09/09 and reporting on "Modbus communication" fault and after resetting the pilot zone is back online. 3. The site went offline at 08:15 on 09/10 due to a recloser trip. After remotely closing the recloser, the site was back online at 11:20 on 09/10. 4. The inverter tripped offline at 09:45 on 09/12, reporting fault code 108:HBMX (3). Inverter module 3 also faulted with code F108: Idc Overcurrent. The inverter came back online at 03:55 on 09/12. 5. Inverter 2 tripped offline at 15:20 to 16:40 due to technician was on site to replace the fuses for the inverter 2. | 1. SR107419 2. SR107724 3. SR107768 4. SR107897 5. SR106821 | SR107724 | SR107768 | SR107897 | SR106821

## Oct
AB CarVal |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 5807071 | 6128127.1819 | -321056.1819 | -5.239% | 6349981.8 | -542910.8 | -8.55%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Fairhaven - 279 Mill Rd | MA | 82516 | 293095 | -210579 | -71.85% | 282090 | -199574 | -70.75% | 1. The site went offline at 09:15 on 10/07 and remained offline for the rest of the month because the DAS and SEL batteries were under replacement. | 1. SR109153 | 1. Pending
Bakersfield - 100 Basic School Rd | CA | 1013678 | 1106845 | -93167 | -8.417% | 1063225 | -49547 | -4.66% | 1. Inverter 1.9 was offline for whole month and being RMA'd. 2.Inverter 1.4 tripped again tripped offline due to and reporting Fault Inverter Hardware Over Current - Protect0140 at 13:45 from 08/21 and back online at 13:45 on 10/01. 3. Inverter 2.6 tripped offline at 11:45 on 09/21 and left offline for whole month 4. Inverter 2.2 had been derating to 166 kW at 12:00 since 10/04, reporting an "Internal Fan Error – IntFanErr." After the inverter was replaced, it began producing as expected from 10/22. 5. Site went offline at 12:00 on 10/14 and back online at 09:30 on 10/15. | 1. SR104291,SR110220 2. SR106840 3. SR108325 4. SR109053 5. SR109475 | 1. Pending 2. Closed 3. Closed 4. Closed 5. Closed | SR110220 | SR106840 | SR108325 | SR109053 | SR109475
Fresno - 2685 Cornelia Ave | CA | 1670359 | 1817918 | -147559 | -8.117% | 2157891 | -487532 | -22.59% | 1. Combiner Box 3.22 went offline on 09/04, and DC Zones 3.19, 3.21, 3.24, and 3.26 have been underperforming. and on 09/24, CB 3.22, 3.7 offline, CB 3.19, 3.21, 3.24, 3.26, 2.19 are underperforming On 10/29, all CBs were back online and producing as expected. 2. Tracker controller 2 motor 1 is stuck from 9/6/25. Reporting "TrackerPos1 position (51.690) is outside acceptable range of Set Point (-52.000). Error limit is: 4.000". and also tracker controller 3 motor 4 is intermittently getting stuck from 9/21/25. on 10/10 , after technician reset the tracker then tracking as expected. 3. Inverter 3 CB 3.22 offline since 08/30. On 10/29, CBs was back online and producing as expected. 4. The site experienced frequent curtailments throughout the month from PG&E. 5. The site tripped offline at 12:45 on 10/04. Additionally, the inverters reported an "Islanding Protection" alarm. After a remote reset, the site was back online at 18:00 on 10/04. 6. Tracker controller 3, tracker position motor 4 stuck from 10/13/25. 7. Site tripped offline at 13:30 on 10/17 due to main breaker trip and back online at 14:15 | 1. SR105880, SR107769, SR107393 2. SR106361, SR107812 3. SR107086, SR107393 4. SR095240 5. SR109054 6. SR109501 7. SR109653 | 1. pending 2. Closed 3. Pending 4. Pending 5. Closed 6. pending 7. Closed | SR107769 | SR107393 | SR106361 | SR107812 | SR107086 | SR107393 | SR095240 | SR109054 | SR109501 | SR109653
San Juaquin - S. Placer & W. Adams | CA | 841734 | 833579 | 8155 | 0.9783% | 789174.4 | 52559.6 | 6.66%
Charlemont - 0 Tea St | MA | 343987 | 352716.2946 | -8729.2946 | -2.475% | 299842.4 | 44144.6 | 14.72% | 1. Inverter 1 tripped offline at 09:30 on 10/09 due to technician was on-site for replacing the AC disconnect. The inverter was back online at 04:00 on 10/09. | 1. SR106141 | 1. Closed
Amherst - 740 Belchertown Rd | MA | 393279 | 389460.457 | 3818.543 | 0.9805% | 373707 | 19572 | 5.237%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 836118 | 787065.7036 | 49052.2964 | 6.232% | 763190 | 72928 | 9.556%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 625400 | 547447.7268 | 77952.2732 | 14.24% | 620862 | 4538 | 0.7309% | 1. Site tripped offline at 14:00 on 10/06 due to utility glitch and back online at 16:15 on 10/06. | 1. SR109116 | 1. Closed

## Nov
AB CarVal |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 3171819.2451 | 3137677.7205 | 34141.5246 | 1.088% | 4187553.1 | -1015733.8549 | -24.26%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Fairhaven - 279 Mill Rd | MA | 0 | 128345.4517 | -128345.4517 | -100% | 201634.3 | -201634.3 | -100% | 1. Site was ofline for whole month due to utility outage | 1. SR109153 | 1. Pending
Bakersfield - 100 Basic School Rd | CA | 561959.2451 | 579618.7 | -17659.4549 | -3.047% | 748197.4 | -186238.1549 | -24.89% | 1. Technician found 2 broken modules and isolated the strings on inverter 1.1 and 1.5 for whole month while inspecting the CPS inverters 2. Inverter 1.9 was offline for whole month and pending for replacement of fuses. | 1. SR110163 2. SR110139 | 1. pending 2. Pending | SR110139
Fresno - 2685 Cornelia Ave | CA | 972629 | 797649.3 | 174979.7 | 21.94% | 1298315 | -325686 | -25.09% | 1. All inverters were offline from 15:30 to 18:30 on 11/25 due to "Islanding Protection" fault. 2. CB 1.2, 1.6, 1.9, 2.28, 3.46, 3.52, 3.55, 3.56, 3.57, 3.59 were underproducing for whole month and CB 2.8 was offline from 12:00 on 11/06. 3. Tracker controller 1, tracker positions motor 2, Tracker controller 3, tracker position motor 4 were stuck for whole month. 4. Site was cutailed from 08:50 to 09:00 on 11/08, and from 14:23 to 14:28 on 11/07 and again from 14:24 to 15:24 on 11/24. | 1. SR111742 2. SR111676 3. SR109501 4. SR095240 | 1. Closed 2. Completed 3. Pending 4. Closed | SR111676 | SR109501 | SR095240
San Juaquin - S. Placer & W. Adams | CA | 369806 | 401799.8 | -31993.8 | -7.963% | 538566.2 | -168760.2 | -31.34% | 1. Inverter 13 was offline from 11:00 on 11/04 to end of the month and being RMA'd 2. Inverter 9 was offline from 10:45 on 11/04 to end of the month 3. 68 modules were damaged and need tobe replaced. 4. Inverter 14 was offline from 10:45 on 11/04 to 11:15 on 11/05 and was derated to 27kW from 11:15 to 15:30 on 11/05. | 1. SR111289, SR110783 2. SR110781 3. SR110642 4. SR110377 | 1. Pending 2. Denied 3. Pending 4. Closed | SR110783 | SR110781 | SR110642 | SR110377
Charlemont - 0 Tea St | MA | 188846 | 197229.5198 | -8383.5198 | -4.251% | 210361.2 | -21515.2 | -10.23% | 1. Site was taken offline from 08:20 to 10:05 on 11/26 for MV inspection. | 1. PM10758 | 1. Work in progress
Amherst - 740 Belchertown Rd | MA | 225186 | 244822.3824 | -19636.3824 | -8.021% | 253398 | -28212 | -11.13% | 1. Site production was low on 11/09 to 11/11, 11/13.
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 507862 | 473333.6331 | 34528.3669 | 7.295% | 528527 | -20665 | -3.91%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 345531 | 314878.9335 | 30652.0665 | 9.735% | 408554 | -63023 | -15.43% | 1. Site was taken offline from 12:00 to 01:00 on 11/26 for MV inspection. | 1. PM10757 | 1. Work in progress

## Dec
AB CarVal |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 2068376.755 | 2373435.8701 | -305059.1151 | -12.85% | 3317952.55 | -1249575.795 | -37.66%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: Fairhaven - 279 Mill Rd | MA | 124077 | 194713.7807 | -70636.7807 | -36.28% | 153235.9 | -29158.9 | -19.03% | 1. The site was back online at 10:00 on 12/05 after the technician replaced the SEL battery. | 1. SR109153 | 1. Closed
Bakersfield - 100 Basic School Rd | CA | 308118.755 | 306950.636 | 1168.119 | 0.3806% | 613990.88 | -305872.125 | -49.82% | 1. Technician found 2 broken modules and isolated the strings on inverter 1.1 and 1.5 for whole month while inspecting the CPS inverters 2. Inverter 1.9 was offline for whole month and pending for replacement of fuses. | 1. SR110163 ,SR113876 2. SR110139 | 1. Closed ,Pending 2. Pending | SR110139
Fresno - 2685 Cornelia Ave | CA | 491734 | 405139.759 | 86594.241 | 21.37% | 1045219.44 | -553485.44 | -52.95% | 1. CB 1.2, 1.6, 1.9, 2.28, 3.46, 3.52, 3.55, 3.56, 3.57, and 3.59 were underproducing, and CB 2.28 was offline from 12:00 on 11/06. After the technician checked in and found some fuses were open, the fuses were closed and all CBs were back online at 19:30 on 12/02. 2. Tracker controller 1, tracker position motor 2, tracker controller 3, and tracker position motor 4 were offline from 10/13/25. After the technician installed a spare encoder, all trackers were back online at 16:45 on 12/22. 3. Site was cutailed from 11:00 to 14:15 on 12/25, and from 13:15 to 15:30 and again from 14:15 to 15:00 on 12/27 and again from 14:00 to 14:40 on 12/29 4.Inverters tripped offline from 09:30 to 10:00 on 12/11 while technician was on site to perform PM. | 1. SR111676 2. SR109501 3. SR095240 4.PM 11019 | 1. Closed 2. Closed 3. Pending 4.Completed | SR095240
San Juaquin - S. Placer & W. Adams | CA | 209424 | 213042.73 | -3618.73 | -1.699% | 398351.33 | -188927.33 | -47.43% | 1. Inverter 13 was offline from 11:00 on 11/04. After the technician replaced the inverter, it was back online at 13:15 on 12/02. 2. Inverter 9 was offline from 10:45 on 11/04. After the technician removed the LOTO, the inverter was back online at 11:00 on 12/30. 3. 68 modules were damaged and need tobe replaced. | 1. SR111289, SR110783 2. SR110781 3. SR110642 | 1. Closed 2. Closed 3. Pending | SR110781 | SR110642
Charlemont - 0 Tea St | MA | 80997 | 231774.3427 | -150777.3427 | -65.05% | 153733 | -72736 | -47.31% | 1. Site production was low on 12/02,12/03,12/07,12/13,12/14,12/19,12/23,12/27 and 12/29. 2.POA 2 -Pyranometer POA 01 has intermittent communication through out the month.
Amherst - 740 Belchertown Rd | MA | 121166 | 235435.7388 | -114269.7388 | -48.54% | 179854 | -58688 | -32.63% | 1. The inverter started late on most days during the month. 2.Site production was low on 12/02, 12/10 , 12/23 ,12/24 , 12/28 ,12.29 | 1. SR112147 | 1. Closed
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 433437 | 429829.4485 | 3607.5515 | 0.8393% | 435806 | -2369 | -0.5436%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 299423 | 356549.4344 | -57126.4344 | -16.02% | 337762 | -38339 | -11.35% | 1. Site production was low on 12/02,12/13,12/14,12/19,12/23,12/27 and 12/29.

## Sites
Portfolio: | AB CarVal
Site DAS Name | Site | State | Update | DAS
001 - Fairhaven | MA: Fairhaven - 279 Mill Rd | MA |  | PowerFactors
AFTW Solar - Wheeler | Bakersfield - 100 Basic School Rd | CA | AEF | Also Energy API
Fresno 14MW Solar - CAISO - AB Carval | Fresno - 2685 Cornelia Ave | CA | AEF | Also Energy API
JID - Crystal Farms Local Solar | San Juaquin - S. Placer & W. Adams | CA | AEF | Also Energy API
002 - Charlemont | Charlemont - 0 Tea St | MA |  | PowerFactors
003 - Town of Amherst | Amherst - 740 Belchertown Rd | MA |  | PowerFactors
004 - Huxley | Ludlow - Huxley 1 & 2 - 504 Fuller St | MA |  | PowerFactors
005 - Beacon | Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA |  | PowerFactors