## Year to Date
Cave Creek USD |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1218969.29 | 813350.69 | 405618.6 | 49.87% | 0 | 1218969.29 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Cave Creek - DWES | AZ | 468075.65 | 447479.51 | 20596.14 | 4.603% | 0 | 349605.65 | 0%
AZ: Cave Creek - HTES | AZ | 355778.39 | 365871.18 | -10092.79 | -2.759% | 0 | 305582.1 | 0%
AZ: Cave Creek - LMES | AZ | 395115.25 | 0 | 395115.25 | 0% | 0 | 294016.25 | 0%

## 1st Qtr
Cave Creek USD |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 343815 | 192646 | 151169 | 78.47% | 0 | 343815 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Cave Creek - DWES | AZ | 125662 | 97376 | 28286 | 29.05% | 0 | 92731 | 0%
AZ: Cave Creek - HTES | AZ | 126367 | 95270 | 31097 | 32.64% | 0 | 99602 | 0%
AZ: Cave Creek - LMES | AZ | 91786 | 0 | 91786 | 0% | 0 | 64038 | 0%

## 2nd Qtr
Cave Creek USD |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 346431.73 | 267076.87 | 79354.86 | 29.71% | 0 | 346431.73 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Cave Creek - DWES | AZ | 134189.65 | 138324.76 | -4135.11 | -2.989% | 0 | 134189.65 | 0%
AZ: Cave Creek - HTES | AZ | 87951.83 | 128752.11 | -40800.28 | -31.69% | 0 | 87951.83 | 0%
AZ: Cave Creek - LMES | AZ | 124290.25 | 0 | 124290.25 | 0% | 0 | 124290.25 | 0%

## 3rd Qtr
Cave Creek USD |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 346401.27 | 239478.93 | 106922.34 | 44.65% | 0 | 346401.27 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Cave Creek - DWES | AZ | 122685 | 125607.79 | -2922.79 | -2.327% | 0 | 122685 | 0%
AZ: Cave Creek - HTES | AZ | 118028.27 | 113871.14 | 4157.13 | 3.651% | 0 | 118028.27 | 0%
AZ: Cave Creek - LMES | AZ | 105688 | 0 | 105688 | 0% | 0 | 105688 | 0%

## 4th Qtr
Cave Creek USD |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 182321.29 | 114148.89 | 68172.4 | 59.72% | 0 | 182321.29 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Cave Creek - DWES | AZ | 85539 | 86170.96 | -631.96 | -0.7334% | 0 | 0
AZ: Cave Creek - HTES | AZ | 23431.29 | 27977.93 | -4546.64 | -16.25% |  | 0
AZ: Cave Creek - LMES | AZ | 73351 | 0 | 73351 |  |  | 0

## Jan
Cave Creek USD |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 87444 | 58113 | 29331 | 50.47% | 0 | 87444 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 32931 | 30249 | 2682 | 8.866% | N/A |  |  | 1. Site was offline from 12:15 to 13:30 on 01/21 for the installation of new CTs and a meter. The system's readings returned to the correct range after troubleshooting on site. 2. Inverter 1-4 experienced multiple trip events throughout the month. 3. Inverter 1-6 was offline on 01/15/25, self-resolved, and came back online at 07:30 AM on 01/20/25. Inverter again went offline on 01/27/25 andbackonline on 01/28/25 4. Inverter 3-2 tripped offline at 08:30 on 01/20/25 and later self resolved, back online on 01/21. | 1. SR094032 2. SR094314, SR094074 & SR092118 3. SR095603, SR097617 4. SR095749
AZ: Cave Creek - HTES | AZ | 26765 | 27864 | -1099 | -3.944% | N/A |  |  | 1.Inverter 1-7 is offline through the month. due to faulting on start up from Grid Frequency failures. 2. Site was offline from 10:15 to 11:00 on 01/22 for the installation of new CTs and a meter. The system's readings returned to the correct range from 01/23 3. Inverter 1-3 was offline throughout the month due to a frozen screen issue. | 1. SR075156, SR094079 2. SR087559, SR095887 3. SR091482
AZ: Cave Creek - LMES | AZ | 27748 | N/A |  | 0% | N/A

## Feb
Cave Creek USD |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 115381 | 59593 | 55788 | 93.62% | 0 | 115381 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 41596 | 30973 | 10623 | 34.3% | 0 | 41596 |  | 1.Inverter 1-4 experienced multiple trip events throughout the month. 2. Inverters 1-6 was offline multiple times throughout the month, including on 02/01, 02/09, 02/14, 02/21, and 02/26, with self-resolving on 02/02, 02/11, 02/15, and 02/27. On 02/18, a technician identified a Display error 121 (Grid Overvolt), reenergized the inverter, and brought it back online at 11:00 AM the same day. Additional troubleshooting was required. 3. Inverter 3-2 tripped offline at 13:30 on 02/03 and self resolved, back online at 07:45 on 02/04 | 1. SR094314, SR094074 ,SR092118 & SR096716 2. SR095603, SR097617 3. SR095749 | SR094074 | SR092118 | SR096716 | SR095603 | SR097617 | SR095749
AZ: Cave Creek - HTES | AZ | 45127 | 28620 | 16507 | 57.68% | 0 | 45127 |  | 1. Inverter 1.6 is underperforming by 5kW and is undergoing further troubleshooting during the PM event. 2. Inverter 1-7 is offline through the month. due to faulting on start up from Grid Frequency failures. 3. Inverter 1-3 was offline throughout the month due to a frozen screen issue. | 1. SR097459 2. SR075156, SR094079 3. SR091482 | SR075156 | SR094079 | SR091482
AZ: Cave Creek - LMES | AZ | 28658 | N/A |  |  | 0 | 28658

## Mar
Cave Creek USD |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 140990 | 74940 | 66050 | 88.14% | 0 | 140990 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 51135 | 36154 | 14981 | 41.44% | 0 | 51135 |  | 1. Inverter 1.6 was frequently offline throughout the month. 2. Inverter 1.4 was offline on multiple days the entire month including 03/12 - 03/14 and 03/26 - 03/28 | 1. SR097617 2. SR094314 | SR094314
AZ: Cave Creek - HTES | AZ | 54475 | 38786 | 15689 | 40.45% | 0 | 54475 |  | 1. Inverter 1.4 was offline on 03/26 and back online on 03/27 2. Inverter 1-3 was offline throughout the month due to a frozen screen issue. 3. Inverter 1.6 is underperforming by 5kW and is undergoing further troubleshooting during the PM event. | 1. SR099023 2. SR091482 3. SR097459 | SR091482 | SR097459
AZ: Cave Creek - LMES | AZ | 35380 | N/A |  |  | 0 | 35380

## Apr
Cave Creek USD |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 135395.82 | 85644.97 | 49750.85 | 58.09% | 0 | 135395.82 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 40824.36 | 44419.86 | -3595.5 | -8.094% | 0 | 40824.36 |  | 1.Inverter 1.4 was offline for most of the month. 2.Meter was not reporting production since 04/23. 3.Inverter 1.6 was offline on 04/06, 04/27 and inverter 1.6 produced at about half capacity on 04/18 and 04/20 | 1.SR094314 2.SR095857 3.SR097617 | SR095857 | SR097617
AZ: Cave Creek - HTES | AZ | 54418.46 | 41225.11 | 13193.35 | 32% | 0 | 54418.46 |  | 1. Meter was intermittently communicating after CTs were replaced. 2. Inverter 1-4 was offline for most of the days of the month 3. Inverter 1-3 was offline for throughout the month | 1.SR095887 2.SR100961, SR099023 3.SR091482 | SR100961 | SR099023 | SR091482
AZ: Cave Creek - LMES | AZ | 40153 | N/A |  |  | 0 | 40153

## May
Cave Creek USD |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 117359.53 | 91017.06 | 26342.47 | 28.94% | 0 | 117359.53 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 46757 | 46929.54 | -172.54 | -0.3677% | 0 | 46757 |  | 1. Meter was not reporting production since 04/23. 2. Inverter 1.4 was offline for most of the days in month 3. Inverter 1.6 was offline on 05/06, 05/08, 05/16, 05/24, 05/26, 05/27 ,05/30 | 1. SR095857 2.SR094314 3.SR097617 | SR094314 | SR097617
AZ: Cave Creek - HTES | AZ | 27588.78 | 44087.52 | -16498.74 | -37.42% | 0 | 27588.78 |  | 1. Inverter 1-3 was offline for throughout the month 2.Inverter 1-4 was offline for most of the days of the month 3.All inverters tripped offline at 09:00 from 05/17 and remained offline for rest of the month 4.Meter was intermittently communicating after CTs were replaced. | 1. SR091482 2. SR100961 3. SR101622 4. SR095887 | SR100961 | SR101622 | SR095887
AZ: Cave Creek - LMES | AZ | 43013.75 | N/A |  |  | 0 | 43013.75
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inverters Cumulative Production value.

## Jun
Cave Creek USD |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 93676.38 | 90414.84 | 3261.54 | 3.607% | 0 | 93676.38 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 46608.29 | 46975.36 | -367.07 | -0.7814% | 0 | 46608.29 |  | 1.Meter was not reporting production since 04/23. 2.Inverter 1.4 was offline for most of the days in month. 3.Inverter 1.6 was offline on 06/05, 06/06, 06/12 ,06/15, 06/16, 06/21, 06/25, 06/26 and was produced at about half capacity on 06/03, 06/08 | 1. SR095857 2.SR094314 3.SR097617 | SR094314 | SR097617
AZ: Cave Creek - HTES | AZ | 5944.59 | 43439.48 | -37494.89 | -86.32% | 0 | 5944.59 |  | 1.All inverters have been re-energized at 10:45 on 06/27 except inverters 1.2 ( fuses need to be replaced) and 1.3 (Waiting for manufacturer response) 2.Meter was intermittently communicating after CTs were replaced. | 1.SR101622 2.SR095887 | SR095887
AZ: Cave Creek - LMES | AZ | 41123.5 | N/A |  |  | 0 | 41123.5
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inverters Cumulative Production value.

## Jul
Cave Creek USD |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 130770.19 | 87480.53 | 43289.66 | 49.48% | 0 | 130770.19 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 45559 | 45632.54 | -73.54 | -0.1612% | 0 | 45559 |  | 1. Meter was not reporting production since 04/23. 2. Inverter 1.4 was offline for most of the days in month. 3. Inverter 1.6 was offline on 07/04, 07/05, 07/06, 07/09, 07/14, 07/18, 07/24, 07/25 and 07/26. | 1. SR095857 2. SR094314 3. SR097616 | SR094314 | SR097616
AZ: Cave Creek - HTES | AZ | 46688.19 | 41847.99 | 4840.2 | 11.57% | 0 | 46688.19 |  | 1. Inverter 1.4 has been offline since 07/21. 2. Inverters 1.2 and 1.3 have been offline since 09:00 on 05/17 — Inverter 1.2 requires fuse replacement, and Inverter 1.3 is awaiting a manufacturer response. 3. Inverter 2.4 has been offline since 07/16. 4. Meter was intermittently communicating after CTs were replaced. | 1. SR100961 2. SR101622, SR104488 3. SR104526 4. SR095887 | SR101622 | SR104488 | SR104526 | SR095887
AZ: Cave Creek - LMES | AZ | 38523 | N/A |  |  | 0 | 38523
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inverters Cumulative Production value.

## Aug
Cave Creek USD |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 127315.08 | 83751.4 | 43563.68 | 52.02% | 0 | 127315.08 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 42565 | 44053.25 | -1488.25 | -3.378% | 0 | 42565 |  | 1. Meter was not reporting production since 04/23. 2. Inverter 1.4 was offline for most of the days in month. 3. Inverter 1.6 was offline for most of the days in month. | 1. SR095857 2. SR094314 3. SR097617, SR106882 | SR094314 | SR097617 | SR106882
AZ: Cave Creek - HTES | AZ | 48030.08 | 39698.15 | 8331.93 | 20.99% | 0 | 48030.08 |  | 1. Inverter 1.4 has been offline since 07/21. 2. Inverters 1.2 and 1.3 have been offline since 09:00 on 05/17 — Inverter 1.2 requires fuse replacement, and Inverter 1.3 is awaiting a manufacturer response. 3. Inverter 2.4 has been offline since 07/16. 4. Meter was intermittently communicating after CTs were replaced. | 1. SR100961 2. SR101622, SR104488 3. SR104526 4. SR095887 | SR101622 | SR104488 | SR104526 | SR095887
AZ: Cave Creek - LMES | AZ | 36720 | N/A |  |  | 0 | 36720
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inverters Cumulative Production value.

## Sep
Cave Creek USD |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 88316 | 68247 | 20069 | 29.41% | 0 | 88316 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Cave Creek - DWES | AZ | 34561 | 35922 | -1361 | -3.789% | 0 | 34561 |  | 1. Meter was not reporting production since 04/23. 2. Inverter 1.4 was offline for most of the days in month. 3. Inverter 1.6 was offline for most of the days in month. | 1. SR095857 2. SR094314 3. SR097617, SR106882 | SR094314 | SR097617 | SR106882
AZ: Cave Creek - HTES | AZ | 23310 | 32325 | -9015 | -27.89% | 0 | 23310 |  | 1. Inverter 1.4 has been offline since 07/21. 2. Inverters 1.2 and 1.3 have been offline since 09:00 on 05/17 — Inverter 1.2 requires fuse replacement, and Inverter 1.3 is awaiting a manufacturer response. 3. Inverter 2.4 has been offline since 07/16. 4. Meter was intermittently communicating after CTs were replaced. 5. Site was offline from 18:45 on 09/18 to end of the month. | 1. SR100961 2. SR101622, SR104488 3. SR104526 4. SR095887 5. SR108287 | SR101622 | SR104488 | SR104526 | SR095887 | SR108287
AZ: Cave Creek - LMES | AZ | 30445 | N/A |  |  | 0 | 30445
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inverters Cumulative Production value.

## Oct
Cave Creek USD |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 87241.29 | 62722.89 | 24518.4 | 39.09% | 0 | 87241.29 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
AZ: Cave Creek - DWES | AZ | 34335 | 34744.96 | -409.96 | -1.18% | N/A |  |  | 1.Inverter 3.2 is offline on 10/02&10/03 and later back online on 10/04 2.Inverter 1.6 was offline on 10/05, 10/09,10/12,10/13 & 10/27 for whole day 3.Meter is not reporting to the DAS from 04/23 | 1.SR108911 2.SR109059 3.SR095857 | 1.Closed 2.Closed 3.Closed | SR095857
AZ: Cave Creek - HTES | AZ | 23431.29 | 27977.93 | -4546.64 | -16.25% | N/A |  |  | 1.Meter was intermittently communicating after CTs were replaced. Additionally all inverters lost communication. 2.Site lost communicating from 10/29 as additional troubleshoot with modem was required. | 1.SR095887 2.SR108287 | 1.Closed 2.Pending 3.Closed
AZ: Cave Creek - LMES | AZ | 29475 | N/A |  |  | N/A |  |  | 1.Lift requires for Pyranometer cleaning | 1.SR090187 | 1.Closed
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual value is taken from total inverters value.

## Nov
Cave Creek USD |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 47461 | 25958 | 21503 | 82.84% | 0 | 47461 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
AZ: Cave Creek - DWES | AZ | 25368 | 25958 | -590 | -2.273% | N/A |  |  | 1.Meter is not reporting to the DAS from 04/23 2.Inverter 1.6 offline on 11/05 and it came back online on 11/07 and again offline on 11/10 and it acme back online on 11/11 3.Inverter 1.6 offline on 11/28 and came back online on 11/29 | 1. SR095857 2.SR110690 3. SR111823 | 1.Closed 2.Closed 3.Closed | SR111823
AZ: Cave Creek - HTES | AZ | 0 |  |  |  | N/A |  |  | 1.Meter was intermittently communicating after CTs were replaced. Additionally all inverters lost communication. 2.Site lost communicating from 10/29 as additional troubleshoot with modem was required. | 1.SR095887 2.SR108287 | 1.Closed 2.Pending 3.Closed
AZ: Cave Creek - LMES | AZ | 22093 | 0 | 22093 |  | N/A |  |  | 1.Lift requires for Pyranometer cleaning | 1.SR090187 | 1.Closed

## Dec
Cave Creek USD |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 47619 | 25468 | 22151 | 86.98% | 0 | 47619 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
AZ: Cave Creek - DWES | AZ | 25836 | 25468 | 368 | 1.445% | N/A |  |  | 1. Meter was not communicated for whole month. | 1. SR095857 | 1. Closed
AZ: Cave Creek - HTES | AZ | 0 |  |  |  | N/A |  |  | 1. Site was not communicated for whole month due to bad modem. | 1. SR108287 | 1. Pending
AZ: Cave Creek - LMES | AZ | 21783 | 0 | 21783 |  | N/A |  |  | 1.Lift requires for Pyranometer cleaning | 1.SR090187 | 1.Closed

## Sites
Portfolio: | Cave Creek USD
Site DAS Name | Site | State | Update | DAS
AZ: Cave Creek - DWES | AZ: Cave Creek - DWES | AZ
AZ: Cave Creek - HTES | AZ: Cave Creek - HTES | AZ
AZ: Cave Creek - LMES | AZ: Cave Creek - LMES | AZ