## Year to Date
Generate Capital |  |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  |  | 454279847.4235 | 279635520.352 | 174644327.0715 | 62.45% | 434730084.0148 | 19549763.4087 | 4.497%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 225804.75 | 350601.784 | -124797.034 | -35.6% | 314456.891 | -88652.141 | -28.19%
K041 | NY | SOL-10357 | 239804.3438 | 280822.537 | -41018.1933 | -14.61% | 257372 | -17567.6562 | -6.826%
K043 | NY | SOL-10358 | 288563.3442 | 311654.068 | -23090.7238 | -7.409% | 56772.278 | 231791.0662 | 408.3%
K058 | NY | SOL-10360 | 94898.8755 | 110097.181 | -15198.3055 | -13.8% | 215922.718 | -121023.8425 | -56.05%
K115 | NY | SOL-10361 | 73114.2889 | 130258.309 | -57144.0201 | -43.87% | 145405.693 | -72291.4041 | -49.72%
K152 | NY | SOL-10362 | 87875.438 | 94402.486 | -6527.048 | -6.914% | 92383 | -4507.562 | -4.879%
K166 | NY | SOL-10363 | 310025.125 | 357544.061 | -47518.936 | -13.29% | 334066.947 | -24041.822 | -7.197%
K206 | NY | SOL-10927 | 191433.3396 | 190220.257 | 1213.0826 | 0.6377% | 187779 | 3654.3396 | 1.946%
K251 | NY | SOL-10365 | 191459.375 | 0 | 191459.375 |  | 215815.006 | -24355.631 | -11.29%
K269 | NY | SOL-10366 | 191448.438 | 233166.754 | -41718.316 | -17.89% | 202482.724 | -11034.286 | -5.449%
K273 | NY | SOL-10367 | 173177.0625 | 0 | 173177.0625 |  | 233475 | -72388.9375 | -31.01%
K287 | NY | SOL-10919 | 167902.938 | 152493.257 | 15409.681 | 10.11% | 177628 | -9725.062 | -5.475%
K298 | NY | SOL-10368 | 176177.7192 | 200968.626 | -24790.9067 | -12.34% | 193842 | -17664.2808 | -9.113%
K335 | NY | SOL-10370 | 187157.1875 | 219649.852 | -32492.6645 | -14.79% | 196276.097 | -9118.9095 | -4.646%
K345 | NY | SOL-10920 | 220580.0312 | 140835.016 | 79745.0152 | 56.62% | 225609.5 | -5029.4687 | -2.229%
K445 | NY | SOL-10373 | 177922.1096 | 211621.099 | -33698.9894 | -15.92% | 187052.982 | -9130.8724 | -4.881%
K495 | NY | SOL-10374 | 577544.375 | 781001.72 | -203457.345 | -26.05% | 860700.846 | -283156.471 | -32.9%
M020 | NY | SOL-10380 | 196805.2498 | 214636.374 | -17831.1242 | -8.308% | 221847.5 | -25042.2503 | -11.29%
M092 | NY | SOL-10383 | 195386.9375 | 217420.661 | -22033.7235 | -10.13% | 208707.552 | -13320.6145 | -6.382%
M143 | NY | SOL-10384 | 216613.0317 | 259239.349 | -42626.3173 | -16.44% | 229535.611 | -12922.5793 | -5.63%
M144 | NY | SOL-10385 | 324495.75 | 260426.335 | 64069.415 | 24.6% | 396165.461 | -71669.711 | -18.09%
M167 | NY | SOL-10386 | 235739.7349 | 189072.862 | 46666.8729 | 24.68% | 271403.893 | -35664.1581 | -13.14%
M188 | NY | SOL-10387 | 166529.0761 | 129193.758 | 37335.3181 | 28.9% | 203880.119 | -37351.0429 | -18.32%
EMHC | NY | SOL-10351 | 68151.4843 | 55537.78 | 12613.7043 | 22.71% | 84631.084 | -16479.5997 | -19.47%
Q008 | NY | SOL-10397 | 105904.1869 | 127799.309 | -21895.1221 | -17.13% | 253588 | -147683.8131 | -58.24%
Q018 | NY | SOL-10398 | 179234.8125 | 192442.389 | -13207.5765 | -6.863% | 164710.714 | 14524.0985 | 8.818%
Q021 | NY | SOL-10399 | 142556.0005 | 151852.379 | -9296.3785 | -6.122% | 140210.386 | 2345.6145 | 1.673%
Q025 | NY | SOL-10400 | 243987.3125 | 251081.356 | -7094.0435 | -2.825% | 139451.5 | 104535.8125 | 74.96%
Q074 | NY | SOL-10402 | 131595.75 | 133044.248 | -1448.498 | -1.089% | 147501.701 | -15905.951 | -10.78%
Q115 | NY | SOL-10872 | 202579.938 | 228156.472 | -25576.534 | -11.21% | 211250.944 | -8671.006 | -4.105%
Q139 | NY | SOL-10403 | 123133.1875 | 135429.859 | -12296.6715 | -9.08% | 134214 | -11080.8125 | -8.256%
Q157 | NY | SOL-10404 | 211648.813 | 256140.646 | -44491.833 | -17.37% | 234164.787 | -22515.974 | -9.615%
Q192 | NY | SOL-10406 | 329764 | 384035.002 | -54271.002 | -14.13% | 271529.2138 | 58234.7862 | 21.45%
Q210 | NY | SOL-10407 | 273586.75 | 285640.009 | -12053.259 | -4.22% | 290968 | -17381.25 | -5.974%
Q229 | NY | SOL-10408 | 117685.7812 | 140954.342 | -23268.5608 | -16.51% | 108247.444 | 9438.3373 | 8.719%
Q231 | NY | SOL-10870 | 444365.375 | 512458.911 | -68093.536 | -13.29% | 466972.5 | -22607.125 | -4.841%
Q405 | NY | SOL-10409 | 511231.5 | 583204.295 | -71972.795 | -12.34% | 519431.522 | -8200.022 | -1.579%
Q435 | NY | SOL-10923 | 599487.75 | 535036.907 | 64450.843 | 12.05% | 669709.5 | -70221.75 | -10.49%
Q485 | NY | SOL-10869 | 595420.3125 | 506339.236 | 89081.0765 | 17.59% | 632488.409 | -37068.0965 | -5.861%
Q490 | NY | SOL-10411 | 431056.4328 | 0 | 431056.4328 |  | 446612.305 | -15555.8722 | -3.483%
Q620 | NY | SOL-10867 | 661733.3748 | 686216.183 | -24482.8082 | -3.568% | 675259.263 | -13525.8882 | -2.003%
QMOA | NY | SOL-10415 | 57462 | 0 | 57462 |  | 62186.916 | -4724.916 | -7.598%
X024 | NY | SOL-10419 | 247348.4372 | 267622.994 | -20274.5568 | -7.576% | 237023 | 10325.4372 | 4.356%
X026 | NY | SOL-10420 | 215615.5 | 217740.953 | -2125.453 | -0.9761% | 314658.971 | -99043.471 | -31.48%
X090 | NY | SOL-10925 | 177279.8752 | 162376.861 | 14903.0143 | 9.178% | 194263.742 | -16983.8668 | -8.743%
X117 | NY | SOL-10422 | 156132.7 | 184558.132 | -28425.432 | -15.4% | 171901.725 | -15769.025 | -9.173%
X125 | NY | SOL-10423 | 295957.75 | 318788.672 | -22830.922 | -7.162% | 300122.733 | -4164.983 | -1.388%
X134 | NY | SOL-10424 | 278680.0325 | 148952.17 | 129727.8625 | 87.09% | 293977.354 | -15297.3215 | -5.204%
X135 | NY | SOL-10425 | 228155.5002 | 273419.75 | -45264.2498 | -16.55% | 241976.517 | -13821.0168 | -5.712%
X139 JHS 222 | NY | SOL-10426 | 345729.3076 | 384085.847 | -38356.5394 | -9.986% | 363579.614 | -17850.3064 | -4.91%
X140 | NY | SOL-10926 | 202489.1567 | 174510.608 | 27978.5487 | 16.03% | 203784 | -1294.8433 | -0.6354%
X166 | NY | SOL-10427 | 209103.9 | 224692.147 | -15588.247 | -6.938% | 218148.807 | -9044.907 | -4.146%
Murphy | MN | SOL-10094 | 8270680 | 9710361.134 | -1439681.134 | -14.83% | 9193456.3 | -922776.3 | -10.04%
Terning | MN | SOL-10093 | 8670166.73 | 9962186.567 | -1292019.837 | -12.97% | 8976953.95 | -306787.22 | -3.417%
Boas Road 04 | NY | SOL-10908 | 508152 | 2284521.903 | -1776369.903 | -77.76% | 3382162.288 | -2492688.288 | -73.7%
Kelly Bridge Farm | NY | SOL-10911 | 1379650 | 2407087.328 | -1027437.328 | -42.68% | 3398741.533 | -2019091.533 | -59.41%
Pool Brook Road | NY | SOL-10909 | 2470717 | 2787698.874 | -316981.874 | -11.37% | 3247874.205 | -777157.205 | -23.93%
Sackett Lake | NY | SOL-10910 | 2731452 | 1906520.406 | 824931.594 | 43.27% | 3442913.829 | -711461.829 | -20.66%
Burritt Road | NY | SOL-10913 | 3043900 | 1780451.91 | 1263448.09 | 70.96% | 3285596.373 | -241696.373 | -7.356%
Villa Roma 1 | NY | SOL-10914 | 2742863 | 385288.604 | 2357574.396 | 611.9% | 2953328.707 | -210465.707 | -7.126%
Villa Roma 2 | NY | SOL-10915 | 2657528 | 2561573.378 | 95954.622 | 3.746% | 2865654.886 | -208126.886 | -7.263%
Washington 1 | NY | SOL-10912 | 3106500 | 2994485.279 | 112014.721 | 3.741% | 3234673.063 | -128173.063 | -3.962%
Washington 3 | NY | SOL-10828 | 2909076 | 3942280.193 | -1033204.193 | -26.21% | 3958090.835 | -1049014.835 | -26.5%
Washington 4 | NY | SOL-10829 | 3522780.5 | 3328718.568 | 194061.932 | 5.83% | 3964164.018 | -441383.518 | -11.13%
Big Tree | NY | SOL-10966 | 3102594 | 1665750 | 1436844 | 86.26% | 3306767.25 | -204173.25 | -6.174%
Canoga | NY | SOL-10965 | 5089060 | 0 | 5089060 |  | 1932497.02 | 2127662.98 | 110.1%
County Route 84 | NY | SOL-10967 | 8352570 | 4040450 | 4312120 | 106.7% | 8859524.468 | -506954.468 | -5.722%
Donati | NY | SOL-10968 | 3407204 | 456170 | 2951034 | 646.9% | 4138762.815 | -731558.815 | -17.68%
Henrietta | NY | SOL-10972 | 7268830 | 3934600 | 3334230 | 84.74% | 8411554.11 | -1142724.11 | -13.59%
NY 70 | NY | SOL-10970 | 8388920 | 4226750 | 4162170 | 98.47% | 9711590.646 | -1322670.646 | -13.62%
Reid | NY | SOL-10991 | 6172786.0799 | 6526936.224 | -354150.1441 | -5.426% | 6792091.5 | -619305.4201 | -9.118%
Sangolqui | NY | SOL-10975 | 3265632 | 1337250 | 1928382 | 144.2% | 4036659.289 | -771027.289 | -19.1%
State Highway 17B | NY | SOL-10988 | 7001830 | 2640170 | 4361660 | 165.2% | 4305062.75 | -507622.75 | -11.79%
State Route 14A | NY | SOL-10997 | 1706902 | 0 | 1706902 |  | 8719783.198 | -6045233.198 | -69.33%
West Creek | NY | SOL-10995 | 8029180 | 3842750 | 4186430 | 108.9% | 8558879.932 | -529699.932 | -6.189%
Wildflower | NY | SOL-10982 | 7129473.9 | 3245123 | 3884350.9 | 119.7% | 8766663.66 | -1637189.76 | -18.68%
Glen Mary 1 | NY | SOL-10993 | 7857080 | 3890180 | 3966900 | 102% | 8964684.374 | -1107604.374 | -12.36%
Glen Mary 2 | NY | SOL-10994 | 3301940 | 473050 | 2828890 | 598% | 3787406.145 | -485466.145 | -12.82%
Telegraph 1 | NY | SOL-11003 | 5861186 | 0 | 5861186 |  | 6250586.391 | -389400.391 | -6.23%
Telegraph 2 | NY | SOL-11004 | 3104707 | 0 | 3104707 |  | 3247643.937 | -142936.937 | -4.401%
Cafferty Hill | NY | SOL-10996 | 8250380 | 4460255.87 | 3790124.13 | 84.98% | 8313988.691 | -63608.691 | -0.7651%
Dunkleman | NY | SOL-11008 | 9109800 | 4081520 | 5028280 | 123.2% | 10090410.637 | -980610.637 | -9.718%
Route 19 1 | NY | SOL-11001 | 3378726.7 | 1521248.77 | 1857477.93 | 122.1% | 4047212.51 | -668485.81 | -16.52%
Route 19 2 | NY | SOL-11002 | 9296820 | 4741100 | 4555720 | 96.09% | 10128822.992 | -832002.992 | -8.214%
Yellow Mills 1 | NY | SOL-11006 | 2631963 | 1477199 | 1154764 | 78.17% | 3417687.298 | -785724.298 | -22.99%
Yellow Mills 2 | NY | SOL-11005 | 2954881 | 0 | 2954881 |  | 3532979.389 | -578098.389 | -16.36%
Yellow Mills 3 | NY | SOL-11007 | 2872264 | 1375184 | 1497080 | 108.9% | 3338708.213 | -466444.213 | -13.97%
Catskill | NY | SOL-11021 | 5029643 | 358236 | 4671407 | 1304% | 6440896.807 | -1411253.807 | -21.91%
Eddy Ridge | NY | SOL-11054 | 4302681.5 | 2092093 | 2210588.5 | 105.7% | 4828123.075 | -525441.575 | -10.88%
Ridgeway #1 | NY | SOL-11018 | 9977319 | 5216568 | 4760751 | 91.26% | 10515427.62 | -538108.62 | -5.117%
Rivard 1 | NY | SOL-11011 | 7610877.4274 | 5633677.08 | 1977200.3474 | 35.1% | 6954415.06 | 656462.3674 | 9.44%
Rivard 2 | NY | SOL-11012 | 7782490.4673 | 7687155.04 | 95335.4273 | 1.24% | 7776256.21 | 6234.2573 | 0.08017%
Ridgeway #2 | NY | SOL-11027 | 4146861 | 1905333 | 2241528 | 117.6% | 4597241.77 | -450380.77 | -9.797%
Spencer | NY | SOL-11017 | 9299363.38 | 4701797.69 | 4597565.69 | 97.78% | 10072930.6 | -773567.22 | -7.68%
Reisender | NY | SOL-10886 | 3068650 | 3228167.661 | -159517.661 | -4.941% | 3441137.504 | -372487.504 | -10.82%
Finney | NY | SOL-10999 | 8033150 | 3466210 | 4566940 | 131.8% | 10227836.843 | -2194686.843 | -21.46%
Davis Solar | NY | SOL-10958 | 3214345 | 3846494.53 | -632149.53 | -16.43% | 4030320 | -815975 | -20.25%
Genesee | NY | SOL-10951 | 5013266.4 | 2773605.02 | 2239661.38 | 80.75% | 7422679.789 | -2409413.389 | -32.46%
Landau I | NY | SOL-10891 | 3390250 | 0 | 3390250 |  | 3822895.809 | -432645.809 | -11.32%
Landau II | NY | SOL-10895 | 4517130 | 0 | 4517130 |  | 3354739.53 | -1514349.53 | -45.14%
New Beginnings | NY | SOL-10890 | 2838630 | 3441729.66 | -603099.66 | -17.52% | 3753940.679 | -915310.679 | -24.38%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 7662663 | 8382750.722 | -720087.722 | -8.59% | 9016376.8 | -1353713.8 | -15.01%
Brodhead Solar, LLC | NY | SOL-10899 | 4488075 | 4828356.188 | -340281.188 | -7.048% | 4974137.52 | -486062.52 | -9.772%
Svenski | NY | SOL-10894 | 3283688 | 0 | 3283688 |  | 3811037.812 | -527349.812 | -13.84%
Bantam | NY | SOL-10986 | 1636370 | 2416730 | -780360 | -32.29% | 9416846.85 | -7887066.85 | -83.75%
Bogart | NY | SOL-10887 | 2897310 | 3351969.198 | -454659.198 | -13.56% | 3625012.277 | -727702.277 | -20.07%
Dubois | NY | SOL-10892 | 1752601.7 | 516309.01 | 1236292.69 | 239.4% | 0 | 480
Salt Point | NY | SOL-10888 | 3402100 | 1634110 | 1767990 | 108.2% | 3974106.867 | -572006.867 | -14.39%
Wheatland 2A | NY | SOL-10971 | 7560910 | 3932820 | 3628090 | 92.25% | 8455033.938 | -894123.938 | -10.58%
Wheatland 2B | NY | SOL-10961 | 8020550 | 3760110 | 4260440 | 113.3% | 8374383.079 | -353833.079 | -4.225%
Brickchurch | NY | SOL-10889 | 1697680 | 2286691.93 | -589011.93 | -25.76% | 3694903.879 | -1997223.879 | -54.05%
McCarthy Solar | NY | SOL-10992 | 2552480 | 0 | 2552480 |  | 3818774.13 | -1266294.13 | -33.16%
Costanza | NY | SOL-10907 | 3333250 | 1696252.08 | 1636997.92 | 96.51% | 3736212.029 | -402962.029 | -10.79%
Lockenhurst Pond | NY | SOL-11000 | 3866679 | 4214798.178 | -348119.178 | -8.259% | 4106139 | -239460 | -5.832%
Drinkwater | NY | SOL-10896 | 3546530 | 1874660 | 1671870 | 89.18% | 3742114.317 | -195584.317 | -5.227%
Altamont | NY | SOL-11085 | 6925852 | 7588015.573 | -662163.573 | -8.726% | 6490675.73 | 435176.27 | 6.705%
Krumkill North | NY | SOL-11086 | 6367819 | 7643126.24 | -1275307.24 | -16.69% | 7698164.24 | -1330345.24 | -17.28%
Krumkill South | NY | SOL-11087 | 5456982 | 6249468.361 | -792486.361 | -12.68% | 6035118.95 | -578136.95 | -9.58%
X092 | NY | SOL-11189 | 155305 | 158403.713 | -3098.713 | -1.956% | 168738.5 | -13433.5 | -7.961%
X093 | NY | SOL-10932 | 88090.3651 | 87987.845 | 102.5201 | 0.1165% | 117450 | -29359.6349 | -25%
X095 | NY | SOL-10929 | 164589.0789 | 90367.927 | 74221.1519 | 82.13% | 160039 | 4550.0789 | 2.843%
X181 | NY | SOL-10428 | 299811.465 | 143469.93 | 156341.535 | 109% | 292186 | 7625.465 | 2.61%
X415 | NY | SOL-10429 | 193817.4555 | 86862.767 | 106954.6885 | 123.1% | 168221.5 | 25595.9555 | 15.22%
K198 | NY | SOL-10930 | 147347.1972 | 104691.944 | 42655.2532 | 40.74% | 135129.5 | 12217.6972 | 9.041%
K203 | NY | SOL-11190 | 166443 | 139017.025 | 27425.975 | 19.73% | 166652.5 | -209.5 | -0.1257%
K213 | NY | SOL-11191 | 185777.2 | 205878.671 | -20101.471 | -9.764% | 193576.5 | -7799.3 | -4.029%
K217 | NY | SOL-10933 | 109202.3679 | 56113.779 | 53088.5889 | 94.61% | 101909.5 | 7292.8679 | 7.156%
K307 | NY | SOL-10876 | 233291.941 | 138520.942 | 94770.999 | 68.42% | 211619 | 21672.941 | 10.24%
K610 | NY | SOL-11158 | 221249.4 | 247972.292 | -26722.892 | -10.78% | 256940 | -35690.6 | -13.89%
M025 | NY | SOL-10392 | 157588.4885 | 186080.153 | -28491.6645 | -15.31% | 224528.5 | -66940.0115 | -29.81%
M028 | NY | SOL-10381 | 182956.0527 | 132099.138 | 50856.9147 | 38.5% | 169609.5 | 13346.5527 | 7.869%
Q030 | NY | SOL-10878 | 226124.018 | 111694.033 | 114429.985 | 102.4% | 206264 | 19860.018 | 9.628%
Q130 | NY | SOL-10877 | 125876.2743 | 63486.698 | 62389.5763 | 98.27% | 115738.202 | 10138.0723 | 8.759%
Q196 | NY | SOL-10879 | 162722.5254 | 87327.556 | 75394.9694 | 86.34% | 150638 | 8848.5654 | 5.874%
Q220 | NY | SOL-10873 | 191899.8355 | 115977.37 | 75922.4655 | 65.46% | 171088 | 14342.6345 | 8.383%
Q205 | NY | SOL-10922 | 209544.1052 | 256489.713 | -46945.6078 | -18.3% | 209643 | -98.8948 | -0.04717%
Q400 | NY | SOL-10871 | 249541.8331 | 0 | 249541.8331 |  | 334397 | -84855.1669 | -25.38%
R003 | NY | SOL-10416 | 319306.5469 | 203282.687 | 116023.8599 | 57.08% | 313538 | -14888.0859 | -4.748%
R007 | NY | SOL-10417 | 366942.9354 | 268008.226 | 98934.7094 | 36.91% | 358797.557 | 8145.3784 | 2.27%
BK16 | NY | SOL-11093 | 368989.2018 | 187303.342 | 181685.8598 | 97% | 333838 | 35151.2018 | 10.53%
Trenton - Trenton East | IL | SOL-11060 | 3435170.4998 | 3596146.792 | -160976.2922 | -4.476% | 4283466 | -818810.5002 | -19.12%
Trenton - Trenton West | IL | SOL-11061 | 2345346.0524 | 2830165.178 | -484819.1256 | -17.13% | 4307039.504 | -1961693.4516 | -45.55%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 4496434 | 4773198.328 | -276764.328 | -5.798% | 1799535 | 2292440 | 127.4%
X018 | NY | SOL-10418 | 154259.6855 | 142775.431 | 11484.2545 | 8.044% | 172924.5 | -18664.8145 | -10.79%
Janiak Solar | NY | SOL-10898 | 3517968.644 | 3866737.221 | -348768.577 | -9.02% | 3881732.069 | -363763.425 | -9.371%
County Route 11B | NY | SOL-10983 | 8209060.26 | 5187801.27 | 3021258.99 | 58.24% | 0 | 1581049
Barone | NY | SOL-11034 | 5149109 | 2808677 | 2340432 | 83.33% | 5450743.2 | -301634.2 | -5.534%
Cedarville | IL | SOL-11069 | 3811366 | 3863020.839 | -51654.839 | -1.337% | 4407139.64 | -595773.64 | -13.52%
O'Brien Hill #1 | NY | SOL-11098 | 838303 | 0 | 838303 |  | 0 | 770286
O'Brien Hill #2 | NY | SOL-11099 | 6598770.06 | 4259176 | 2339594.06 | 54.93% | 288848 | 656879 | 227.4%
Trinity - Freeport | IL | SOL-11057 | 3749896 | 3678317.828 | 71578.172 | 1.946% | 3210551.5 | 147402.5 | 4.591%
Ransom | NY | SOL-11157 | 6327600.5 | 4066944 | 2260656.5 | 55.59% | 326042 | 404070.7 | 123.9%
Horseheads - Wedge | NY | SOL-11160 | 4260669 | 2698731 | 1561938 | 57.88% | 344639 | 171594 | 49.79%
Otisville - Shoddy Hollow | NY | SOL-11185 | 7293597.8 | 4645686 | 2647911.8 | 57% | 363236 | 580678.7 | 159.9%
Wellsville - Chenunda Creek | NY | SOL-11187 | 3542668.7 | 2158196 | 1384472.7 | 64.15% | 381833 | 167439.8 | 43.85%
DC: Washington - Essex Condominium | DC | SOL-10036 | 36282.958 | 46050.902 | -9767.944 | -21.21% | 46149.917 | -10275.917 | -22.27%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 100599.029 | 128796.988 | -28197.959 | -21.89% | 140960.39 | -40361.361 | -28.63%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 147891 | 117543.45 | 30347.55 | 25.82% | 140891.21 | 6999.79 | 4.968%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 1273953 | 1562552.419 | -288599.419 | -18.47% | 1763065.26 | -489112.26 | -27.74%
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 3662492.7765 | 3899251.93 | -236759.1535 | -6.072% | 4245917.7 | -583424.9235 | -13.74%
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 1656496 | 846354.673 | 810141.327 | 95.72% | 1738422.58 | -81926.58 | -4.713%
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 1704508.8292 | 2285371.48 | -580862.6508 | -25.42% | 2326721.5 | -643001.4008 | -27.64%
NY: Whitesville - Independence North | NY | SOL-11186 | 1753873 | 0 | 1753873 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 712474 | 757794.9 | -45320.9 | -5.981% | 753184 | -40710 | -5.405%
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 734767 | 955373.9 | -220606.9 | -23.09% | 706289 | 28478 | 4.032%
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 636487 | 1171509.3 | -535022.3 | -45.67% | 604106 | 32381 | 5.36%
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 714603 | 824791.6 | -110188.6 | -13.36% | 629174.5 | 85428.5 | 13.58%
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 36872512.6 | 0 | 36872512.6 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 999568 | 0 | 999568 |  | 1085696.5 | -86128.5 | -7.933%
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 94776.515 | 121981.2 | -27204.685 | -22.3% | 178632.9 | -83856.385 | -46.94%

## 1st Qtr
Generate Capital |  |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  |  | 73187517.3696 | 31614296.346 | 41573221.0236 | 131.5% | 79163514.454 | -5975997.0844 | -7.549%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 59541.5 | 72002.03 | -12460.53 | -17.31% | 50886.23 | 8655.27 | 17.01%
K041 | NY | SOL-10357 | 45035.9688 | 56199.33 | -11163.3613 | -19.86% | 46068 | -1032.0312 | -2.24%
K043 | NY | SOL-10358 | 53077.0938 | 62413.61 | -9336.5163 | -14.96% | 10325 | 42752.0938 | 414.1%
K058 | NY | SOL-10360 | 12634.75 | 22177.693 | -9542.943 | -43.03% | 39956.249 | -27321.499 | -68.38%
K115 | NY | SOL-10361 | 11799.1172 | 26169.976 | -14370.8588 | -54.91% | 25362.094 | -13562.9768 | -53.48%
K152 | NY | SOL-10362 | 16402.1875 | 18944.047 | -2541.8595 | -13.42% | 15415 | 987.1875 | 6.404%
K166 | NY | SOL-10363 | 58816.625 | 71150.65 | -12334.025 | -17.34% | 54476.13 | 4340.495 | 7.968%
K206 | NY | SOL-10927 | 35230.824 | 42404.21 | -7173.386 | -16.92% | 32033 | 3197.824 | 9.983%
K251 | NY | SOL-10365 | 39545.375 | 0 | 39545.375 |  | 36320.712 | 3224.663 | 8.878%
K269 | NY | SOL-10366 | 35207.875 | 46926.1 | -11718.225 | -24.97% | 35757.562 | -549.687 | -1.537%
K273 | NY | SOL-10367 | 37234.6875 | 0 | 37234.6875 |  | 42215 | -4980.3125 | -11.8%
K287 | NY | SOL-10919 | 31794.0938 | 31809.195 | -15.1012 | -0.04747% | 31948 | -153.9062 | -0.4817%
K298 | NY | SOL-10368 | 30988.3125 | 41019.48 | -10031.1675 | -24.45% | 32201 | -1212.6875 | -3.766%
K335 | NY | SOL-10370 | 34573.9375 | 44090.73 | -9516.7925 | -21.58% | 35771 | -1197.0625 | -3.346%
K345 | NY | SOL-10920 | 40739.3438 | 30184.546 | 10554.7978 | 34.97% | 38421 | 2318.3438 | 6.034%
K445 | NY | SOL-10373 | 34367.8594 | 43977.83 | -9609.9706 | -21.85% | 32201.837 | 2166.0224 | 6.726%
K495 | NY | SOL-10374 | 576 | 133849.47 | -133273.47 | -99.57% | 145580 | -145004 | -99.6%
M020 | NY | SOL-10380 | 36141.6875 | 43127.54 | -6985.8525 | -16.2% | 39795 | -3653.3125 | -9.18%
M092 | NY | SOL-10383 | 35420.75 | 43593.08 | -8172.33 | -18.75% | 36415.06 | -994.31 | -2.73%
M143 | NY | SOL-10384 | 40552.0312 | 48973.74 | -8421.7087 | -17.2% | 40133.094 | 418.9372 | 1.044%
M144 | NY | SOL-10385 | 60786.125 | 0 | 60786.125 |  | 61123 | -336.875 | -0.5511%
M167 | NY | SOL-10386 | 41523.2656 | 37503.086 | 4020.1796 | 10.72% | 45030.831 | -3507.5654 | -7.789%
M188 | NY | SOL-10387 | 31767.3438 | 0 | 31767.3438 |  | 31939 | -171.6562 | -0.5375%
EMHC | NY | SOL-10351 | 11616.3203 | 10045.342 | 1570.9783 | 15.64% | 12208.593 | -592.2727 | -4.851%
Q008 | NY | SOL-10397 | 39978.6875 | 49531.6 | -9552.9125 | -19.29% | 50157 | -10178.3125 | -20.29%
Q018 | NY | SOL-10398 | 34397.125 | 36028.132 | -1631.007 | -4.527% | 28526.106 | 5871.019 | 20.58%
Q021 | NY | SOL-10399 | 27566.9062 | 33378.944 | -5812.0378 | -17.41% | 23127.077 | 4439.8292 | 19.2%
Q025 | NY | SOL-10400 | 46126.375 | 52071.73 | -5945.355 | -11.42% | 30045 | 16081.375 | 53.52%
Q074 | NY | SOL-10402 | 29699.875 | 31804.751 | -2104.876 | -6.618% | 26494.826 | 3205.049 | 12.1%
Q115 | NY | SOL-10872 | 39141.875 | 47215.26 | -8073.385 | -17.1% | 35263.257 | 3878.618 | 11%
Q139 | NY | SOL-10403 | 23405.0938 | 26141.15 | -2736.0563 | -10.47% | 22305 | 1100.0938 | 4.932%
Q157 | NY | SOL-10404 | 39595.875 | 50882.78 | -11286.905 | -22.18% | 40055.241 | -459.366 | -1.147%
Q192 | NY | SOL-10406 | 64536.5 | 77228.18 | -12691.68 | -16.43% | 59130.01 | 5406.49 | 9.143%
Q210 | NY | SOL-10407 | 53490.375 | 56846.85 | -3356.475 | -5.904% | 49341 | 4149.375 | 8.41%
Q229 | NY | SOL-10408 | 21814.7188 | 28808.939 | -6994.2202 | -24.28% | 9902.809 | 11911.9098 | 120.3%
Q231 | NY | SOL-10870 | 85514.375 | 108830.63 | -23316.255 | -21.42% | 80616 | 4898.375 | 6.076%
Q405 | NY | SOL-10409 | 99440.5 | 115189.99 | -15749.49 | -13.67% | 87640.71 | 11799.79 | 13.46%
Q435 | NY | SOL-10923 | 127573 | 110358.02 | 17214.98 | 15.6% | 117825 | 9748 | 8.273%
Q485 | NY | SOL-10869 | 110495.75 | 105103.41 | 5392.34 | 5.131% | 110570.03 | -74.28 | -0.06718%
Q490 | NY | SOL-10411 | 83374.8078 | 0 | 83374.8078 |  | 74562.65 | 8812.1578 | 11.82%
Q620 | NY | SOL-10867 | 125105.625 | 137409.16 | -12303.535 | -8.954% | 120760.39 | 4345.235 | 3.598%
QMOA | NY | SOL-10415 | 11408.7 | 0 | 11408.7 |  | 11777.986 | -369.286 | -3.135%
X024 | NY | SOL-10419 | 45004.375 | 57750.19 | -12745.815 | -22.07% | 38352 | 6652.375 | 17.35%
X026 | NY | SOL-10420 | 37650 | 45220.32 | -7570.32 | -16.74% | 50959.61 | -13309.61 | -26.12%
X090 | NY | SOL-10925 | 36597.2188 | 29963.485 | 6633.7337 | 22.14% | 34352 | 2245.2188 | 6.536%
X117 | NY | SOL-10422 | 28496.8 | 38005.027 | -9508.227 | -25.02% | 28558.339 | -61.539 | -0.2155%
X125 | NY | SOL-10423 | 55729.0625 | 65241.37 | -9512.3075 | -14.58% | 52855.43 | 2873.6325 | 5.437%
X134 | NY | SOL-10424 | 52172.7188 | 0 | 52172.7188 |  | 51414 | 758.7188 | 1.476%
X135 | NY | SOL-10425 | 42983.0938 | 53320.36 | -10337.2663 | -19.39% | 43904 | -920.9062 | -2.098%
X139 JHS 222 | NY | SOL-10426 | 65304.3636 | 74458.5 | -9154.1364 | -12.29% | 60317 | 4987.3636 | 8.269%
X140 | NY | SOL-10926 | 36989.3594 | 35154.074 | 1835.2854 | 5.221% | 36763 | 226.3594 | 0.6157%
X166 | NY | SOL-10427 | 39872.2 | 48413.64 | -8541.44 | -17.64% | 37390 | 2482.2 | 6.639%
Murphy | MN | SOL-10094 | 1866950 | 2333706.1 | -466756.1 | -20% | 1991521.7 | -124571.7 | -6.255%
Terning | MN | SOL-10093 | 1723767.795 | 2329333.8 | -605566.005 | -26% | 1889625.5 | -165857.705 | -8.777%
Boas Road 04 | NY | SOL-10908 | 409196 | 732048.483 | -322852.483 | -44.1% | 677797.76 | -268601.76 | -39.63%
Kelly Bridge Farm | NY | SOL-10911 | 393266 | 739185.218 | -345919.218 | -46.8% | 660243.3 | -266977.3 | -40.44%
Pool Brook Road | NY | SOL-10909 | 443783 | 625318.024 | -181535.024 | -29.03% | 599925.68 | -156142.68 | -26.03%
Sackett Lake | NY | SOL-10910 | 580372 | 766915.036 | -186543.036 | -24.32% | 700396.02 | -120024.02 | -17.14%
Burritt Road | NY | SOL-10913 | 386530 | 0 | 386530 |  | 550528.54 | -163998.54 | -29.79%
Villa Roma 1 | NY | SOL-10914 | 476023 | 378718.374 | 97304.626 | 25.69% | 504370.94 | -28347.94 | -5.62%
Villa Roma 2 | NY | SOL-10915 | 493282 | 651162.878 | -157880.878 | -24.25% | 489594.4 | 3687.6 | 0.7532%
Washington 1 | NY | SOL-10912 | 482600 | 637922.499 | -155322.499 | -24.35% | 539834.58 | -57234.58 | -10.6%
Washington 3 | NY | SOL-10828 | 582985 | 96875.183 | 486109.817 | 501.8% | 663362.07 | -80377.07 | -12.12%
Washington 4 | NY | SOL-10829 | 507100 | 569391.538 | -62291.538 | -10.94% | 662129.7 | -155029.7 | -23.41%
Big Tree | NY | SOL-10966 | 370242 | 0 | 370242 |  | 579179.2 | -208937.2 | -36.07%
Canoga | NY | SOL-10965 | 1282330 | 0 | 1282330 |  | 1264221.12 | -296881.12 | -23.48%
County Route 84 | NY | SOL-10967 | 1679480 | 0 | 1679480 |  | 1839235.33 | -159755.33 | -8.686%
Donati | NY | SOL-10968 | 399588 | 0 | 399588 |  | 739969.58 | -340381.58 | -46%
Henrietta | NY | SOL-10972 | 1142260 | 0 | 1142260 |  | 1375164.38 | -232904.38 | -16.94%
NY 70 | NY | SOL-10970 | 1358830 | 0 | 1358830 |  | 1775637.56 | -416807.56 | -23.47%
Reid | NY | SOL-10991 | 865560.9719 | 1332958.5 | -467397.5281 | -35.06% | 1353538 | -487977.0281 | -36.05%
Sangolqui | NY | SOL-10975 | 582872 | 0 | 582872 |  | 719241.46 | -136369.46 | -18.96%
State Highway 17B | NY | SOL-10988 | 1323280 | 0 | 1323280 |  | 1495286.03 | -172006.03 | -11.5%
State Route 14A | NY | SOL-10997 | 1472594 | 0 | 1472594 |  | 1690430.99 | -217836.99 | -12.89%
West Creek | NY | SOL-10995 | 1608240 | 0 | 1608240 |  | 1647805.14 | -39565.14 | -2.401%
Wildflower | NY | SOL-10982 | 1311316.9 | 0 | 1311316.9 |  | 1786008.62 | -474691.72 | -26.58%
Glen Mary 1 | NY | SOL-10993 | 1658570 | 0 | 1658570 |  | 1770554.53 | -111984.53 | -6.325%
Glen Mary 2 | NY | SOL-10994 | 427230 | 0 | 427230 |  | 738205.96 | -310975.96 | -42.13%
Telegraph 1 | NY | SOL-11003 | 908160 | 0 | 908160 |  | 1200362.37 | -292202.37 | -24.34%
Telegraph 2 | NY | SOL-11004 | 503671 | 0 | 503671 |  | 620509.76 | -116838.76 | -18.83%
Cafferty Hill | NY | SOL-10996 | 1545620 | 0 | 1545620 |  | 1548566 | -2946 | -0.1902%
Dunkleman | NY | SOL-11008 | 1239050 | 0 | 1239050 |  | 1827365.4 | -588315.4 | -32.19%
Route 19 1 | NY | SOL-11001 | 599580 | 0 | 599580 |  | 734699.06 | -135119.06 | -18.39%
Route 19 2 | NY | SOL-11002 | 1508780 | 0 | 1508780 |  | 1875001.22 | -366221.22 | -19.53%
Yellow Mills 1 | NY | SOL-11006 | 217178 | 0 | 217178 |  | 590012.82 | -372834.82 | -63.19%
Yellow Mills 2 | NY | SOL-11005 | 536407 | 0 | 536407 |  | 608233.1 | -71826.1 | -11.81%
Yellow Mills 3 | NY | SOL-11007 | 463994 | 0 | 463994 |  | 558855.09 | -94861.09 | -16.97%
Catskill | NY | SOL-11021 | 1047060 | 0 | 1047060 |  | 1210172.43 | -163112.43 | -13.48%
Eddy Ridge | NY | SOL-11054 | 681679.5 | 0 | 681679.5 |  | 848735 | -167055.5 | -19.68%
Ridgeway #1 | NY | SOL-11018 | 1455922 | 0 | 1455922 |  | 1887846.5 | -431924.5 | -22.88%
Rivard 1 | NY | SOL-11011 | 1110890 | 1333490.2 | -222600.2 | -16.69% | 1306920.6 | -196030.6 | -15%
Rivard 2 | NY | SOL-11012 | 1124733.3778 | 1139128 | -14394.6222 | -1.264% | 1253494.9 | -128761.5222 | -10.27%
Ridgeway #2 | NY | SOL-11027 | 634923 | 0 | 634923 |  | 970007.31 | -335084.31 | -34.54%
Spencer | NY | SOL-11017 | 1726882 | 0 | 1726882 |  | 1768660.6 | -41778.6 | -2.362%
Reisender | NY | SOL-10886 | 574990 | 712210.541 | -137220.541 | -19.27% | 659096.66 | -84106.66 | -12.76%
Finney | NY | SOL-10999 | 1669700 | 0 | 1669700 |  | 1961662.18 | -291962.18 | -14.88%
Davis Solar | NY | SOL-10958 | 624204 | 824082.2 | -199878.2 | -24.25% | 800901 | -176697 | -22.06%
Genesee | NY | SOL-10951 | 828013.5 | 0 | 828013.5 |  | 1225115.14 | -397101.64 | -32.41%
Landau I | NY | SOL-10891 | 649830 | 0 | 649830 |  | 786342.21 | -136512.21 | -17.36%
Landau II | NY | SOL-10895 | 1104430 | 0 | 1104430 |  | 1639446.05 | -535016.05 | -32.63%
New Beginnings | NY | SOL-10890 | 653410 | 837518.23 | -184108.23 | -21.98% | 765286.75 | -111876.75 | -14.62%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 1198693 | 1581948.604 | -383255.604 | -24.23% | 1772768.28 | -574075.28 | -32.38%
Brodhead Solar, LLC | NY | SOL-10899 | 823637 | 894614.644 | -70977.644 | -7.934% | 879972.47 | -56335.47 | -6.402%
Svenski | NY | SOL-10894 | 612069 | 0 | 612069 |  | 734878.49 | -122809.49 | -16.71%
Bantam | NY | SOL-10986 | 888990 | 0 | 888990 |  | 1462159.3 | -679759.3 | -46.49%
Bogart | NY | SOL-10887 | 691310 | 774249.438 | -82939.438 | -10.71% | 728934.5 | -37624.5 | -5.162%
Dubois | NY | SOL-10892 | 629651.7 | 0 | 629651.7 |  | 0 | 0
Salt Point | NY | SOL-10888 | 705260 | 0 | 705260 |  | 696169.77 | 9090.23 | 1.306%
Wheatland 2A | NY | SOL-10971 | 1291910 | 0 | 1291910 |  | 1409117.96 | -117207.96 | -8.318%
Wheatland 2B | NY | SOL-10961 | 1250010 | 0 | 1250010 |  | 1393371.52 | -143361.52 | -10.29%
Brickchurch | NY | SOL-10889 | 434840 | 527867.09 | -93027.09 | -17.62% | 483295.74 | -48455.74 | -10.03%
McCarthy Solar | NY | SOL-10992 | 698670 | 0 | 698670 |  | 774863.7 | -76193.7 | -9.833%
Costanza | NY | SOL-10907 | 616320 | 0 | 616320 |  | 753359.09 | -137039.09 | -18.19%
Lockenhurst Pond | NY | SOL-11000 | 773533 | 851153.1 | -77620.1 | -9.119% | 728645 | 44888 | 6.16%
Drinkwater | NY | SOL-10896 | 589830 | 0 | 589830 |  | 738279.76 | -148449.76 | -20.11%
Altamont | NY | SOL-11085 | 1326645 | 1687662.5 | -361017.5 | -21.39% | 1394156.6 | -67511.6 | -4.842%
Krumkill North | NY | SOL-11086 | 1136190 | 1538793.4 | -402603.4 | -26.16% | 1729374.9 | -593184.9 | -34.3%
Krumkill South | NY | SOL-11087 | 1041009 | 1307044.5 | -266035.5 | -20.35% | 1355778.1 | -314769.1 | -23.22%
X092 | NY | SOL-11189 | 15832.4 | 15885.47 | -53.07 | -0.3341% | 16758 | -925.6 | -5.523%
X093 | NY | SOL-10932 | 13436.6987 | 0 | 13436.6987 |  | 11061 | 2375.6987 | 21.48%
X095 | NY | SOL-10929 | 26232.7034 | 0 | 26232.7034 |  | 15084 | 11148.7034 | 73.91%
X181 | NY | SOL-10428 | 46052.2812 | 0 | 46052.2812 |  | 27420 | 18632.2812 | 67.95%
X415 | NY | SOL-10429 | 31229.7522 | 0 | 31229.7522 |  | 15528 | 15701.7522 | 101.1%
K198 | NY | SOL-10930 | 28011.8028 | 0 | 28011.8028 |  | 12752 | 15259.8028 | 119.7%
K203 | NY | SOL-11190 | 13616 | 0 | 13616 |  | 0 | 13616
K213 | NY | SOL-11191 | 19107.2 | 20224.73 | -1117.53 | -5.526% | 18782 | 325.2 | 1.731%
K217 | NY | SOL-10933 | 19930.4768 | 0 | 19930.4768 |  | 9298 | 10632.4768 | 114.4%
K307 | NY | SOL-10876 | 41741.9641 | 0 | 41741.9641 |  | 19546 | 22195.9641 | 113.6%
K610 | NY | SOL-11158 | 25056.5 | 24720.24 | 336.26 | 1.36% | 24582 | 474.5 | 1.93%
M025 | NY | SOL-10392 | 26784.1823 | 0 | 26784.1823 |  | 21500 | 5284.1823 | 24.58%
M028 | NY | SOL-10381 | 28412.4201 | 0 | 28412.4201 |  | 15744 | 12668.4201 | 80.47%
Q030 | NY | SOL-10878 | 43631.7525 | 0 | 43631.7525 |  | 19517 | 24114.7525 | 123.6%
Q130 | NY | SOL-10877 | 22567.2786 | 0 | 22567.2786 |  | 10779.37 | 11787.9086 | 109.4%
Q196 | NY | SOL-10879 | 27263.4877 | 0 | 27263.4877 |  | 14155 | 9872.5277 | 69.75%
Q220 | NY | SOL-10873 | 35224.9061 | 0 | 35224.9061 |  | 15807 | 12948.7051 | 81.92%
Q205 | NY | SOL-10922 | 22716.957 | 25173.09 | -2456.133 | -9.757% | 19352 | 3364.957 | 17.39%
Q400 | NY | SOL-10871 | 40289 | 0 | 40289 |  | 30789 | 9500 | 30.86%
R003 | NY | SOL-10416 | 54609.5082 | 0 | 54609.5082 |  | 29898 | 4054.8754 | 13.56%
R007 | NY | SOL-10417 | 70915.4742 | 0 | 70915.4742 |  | 29854 | 41061.4742 | 137.5%
BK16 | NY | SOL-11093 | 68301.6474 | 0 | 68301.6474 |  | 31346 | 36955.6474 | 117.9%
Trenton - Trenton East | IL | SOL-11060 | 488927 | 498262.4 | -9335.4 | -1.874% | 613135 | -124208 | -20.26%
Trenton - Trenton West | IL | SOL-11061 | 511811 | 479983.1 | 31827.9 | 6.631% | 616255.004 | -104444.004 | -16.95%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 910089 | 821340.269 | 88748.731 | 10.81% | 0 | 910089
X018 | NY | SOL-10418 | 26638.644 | 36216.344 | -9577.7 | -26.45% | 15457 | 11181.644 | 72.34%
Janiak Solar | NY | SOL-10898 | 722149.0001 | 877484.898 | -155335.8979 | -17.7% | 812707.069 | -90558.0689 | -11.14%
County Route 11B | NY | SOL-10983 | 1581049 | 0 | 1581049 |  | 0 | 1581049
Barone | NY | SOL-11034 | 1074960 | 0 | 1074960 |  | 1044522.5 | 30437.5 | 2.914%
Cedarville | IL | SOL-11069 | 776639 | 842466.8 | -65827.8 | -7.814% | 807480.9 | -30841.9 | -3.82%
O'Brien Hill #1 | NY | SOL-11098 | 770286 | 0 | 770286 |  | 0 | 770286
O'Brien Hill #2 | NY | SOL-11099 | 805058 | 0 | 805058 |  | 0 | 805058
Trinity - Freeport | IL | SOL-11057 | 380764 | 262931.7 | 117832.3 | 44.81% | 0 | 380764
Ransom | NY | SOL-11157 | 573181.7 | 0 | 573181.7 |  | 0 | 573181.7
Horseheads - Wedge | NY | SOL-11160 | 351172 | 0 | 351172 |  | 0 | 351172
Otisville - Shoddy Hollow | NY | SOL-11185 | 770722.7 | 0 | 770722.7 |  | 0 | 770722.7
Wellsville - Chenunda Creek | NY | SOL-11187 | 367949.8 | 0 | 367949.8 |  | 0 | 367949.8
DC: Washington - Essex Condominium | DC | SOL-10036 | 6661.958 | 7882.524 | -1220.566 | -15.48% | 8796.319 | -2543.319 | -28.91%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 28914 | 29374.276 | -460.276 | -1.567% | 32426.188 | -3512.188 | -10.83%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 34818 | 28134.248 | 6683.752 | 23.76% | 32408.821 | 2409.179 | 7.434%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 0 | 0 | 0 |  | 0 | 0
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 0 | 0 | 0 |  | 0 | 0
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 0 | 0 | 0 |  | 0 | 0
NY: Whitesville - Independence North | NY | SOL-11186 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 0 | 0 | 0 |  | 0 | 0
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 0 | 0 | 0 |  | 0 | 0
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 0 | 0 | 0 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 0 | 0 | 0 |  | 0 | 0
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Generate Capital |  |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  |  | 121005964.9921 | 46675281.727 | 74330683.2651 | 159.3% | 141633279.185 | -20627314.1929 | -14.56%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 68306.5 | 106688.99 | -38382.49 | -35.98% | 111665.88 | -43359.38 | -38.83%
K041 | NY | SOL-10357 | 75953.4062 | 86786.34 | -10832.9337 | -12.48% | 88785 | -12831.5938 | -14.45%
K043 | NY | SOL-10358 | 92752.2505 | 95284.617 | -2532.3665 | -2.658% | 19497.39 | 73254.8605 | 375.7%
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 59563 | -59563 | -100%
K115 | NY | SOL-10361 | 17549.2031 | 33770.05 | -16220.8469 | -48.03% | 50850.15 | -33300.9469 | -65.49%
K152 | NY | SOL-10362 | 27928.25 | 29089.714 | -1161.464 | -3.993% | 32067 | -4138.75 | -12.91%
K166 | NY | SOL-10363 | 102875.5 | 110758.07 | -7882.57 | -7.117% | 117571.05 | -14695.55 | -12.5%
K206 | NY | SOL-10927 | 60686.7812 | 58984.7 | 1702.0813 | 2.886% | 65939 | -5252.2188 | -7.965%
K251 | NY | SOL-10365 | 55076 | 0 | 55076 |  | 74161.86 | -19085.86 | -25.74%
K269 | NY | SOL-10366 | 60935.25 | 70904.83 | -9969.58 | -14.06% | 69988.55 | -9053.3 | -12.94%
K273 | NY | SOL-10367 | 62937.1875 | 0 | 62937.1875 |  | 89807 | -26869.8125 | -29.92%
K287 | NY | SOL-10919 | 52962.8125 | 46110.94 | 6851.8725 | 14.86% | 61335 | -8372.1875 | -13.65%
K298 | NY | SOL-10368 | 57863.9062 | 60971.71 | -3107.8038 | -5.097% | 70465 | -12601.0938 | -17.88%
K335 | NY | SOL-10370 | 60065.625 | 67653.73 | -7588.105 | -11.22% | 74490 | -14424.375 | -19.36%
K345 | NY | SOL-10920 | 70369.9062 | 41715.08 | 28654.8262 | 68.69% | 81770 | -11400.0938 | -13.94%
K445 | NY | SOL-10373 | 58022.0938 | 63169.63 | -5147.5362 | -8.149% | 65662.47 | -7640.3763 | -11.64%
K495 | NY | SOL-10374 | 199709.375 | 242052.38 | -42343.005 | -17.49% | 283857.73 | -84148.355 | -29.64%
M020 | NY | SOL-10380 | 59768.0625 | 66545.84 | -6777.7775 | -10.19% | 76609 | -16840.9375 | -21.98%
M092 | NY | SOL-10383 | 62289.5 | 66272.36 | -3982.86 | -6.01% | 73474.2 | -11184.7 | -15.22%
M143 | NY | SOL-10384 | 69756.125 | 82860.54 | -13104.415 | -15.82% | 81619.65 | -11863.525 | -14.54%
M144 | NY | SOL-10385 | 102563.6875 | 76120.71 | 26442.9775 | 34.74% | 130868.28 | -28304.5925 | -21.63%
M167 | NY | SOL-10386 | 78928.6562 | 58444.63 | 20484.0262 | 35.05% | 98966.46 | -20037.8037 | -20.25%
M188 | NY | SOL-10387 | 50565.6875 | 38334.36 | 12231.3275 | 31.91% | 66835.29 | -16269.6025 | -24.34%
EMHC | NY | SOL-10351 | 22106.2344 | 18603.372 | 3502.8624 | 18.83% | 32533.419 | -10427.1846 | -32.05%
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 69512 | -69512 | -100%
Q018 | NY | SOL-10398 | 56453.3125 | 58714.73 | -2261.4175 | -3.852% | 58393.53 | -1940.2175 | -3.323%
Q021 | NY | SOL-10399 | 45110.9688 | 43698.71 | 1412.2588 | 3.232% | 48862.52 | -3751.5513 | -7.678%
Q025 | NY | SOL-10400 | 77637.8125 | 76800.78 | 837.0325 | 1.09% | 43488 | 34149.8125 | 78.53%
Q074 | NY | SOL-10402 | 50738.4375 | 50606.16 | 132.2775 | 0.2614% | 55523.36 | -4784.9225 | -8.618%
Q115 | NY | SOL-10872 | 64576.1875 | 68703.72 | -4127.5325 | -6.008% | 72812.27 | -8236.0825 | -11.31%
Q139 | NY | SOL-10403 | 39318.25 | 43483.78 | -4165.53 | -9.58% | 46846 | -7527.75 | -16.07%
Q157 | NY | SOL-10404 | 69630.9375 | 74537.96 | -4907.0225 | -6.583% | 81748.46 | -12117.5225 | -14.82%
Q192 | NY | SOL-10406 | 107539.625 | 117429.03 | -9889.405 | -8.422% | 83222.4 | 24317.225 | 29.22%
Q210 | NY | SOL-10407 | 86597.125 | 88930.45 | -2333.325 | -2.624% | 100170 | -13572.875 | -13.55%
Q229 | NY | SOL-10408 | 38305.3125 | 43180.66 | -4875.3475 | -11.29% | 43122.22 | -4816.9075 | -11.17%
Q231 | NY | SOL-10870 | 142266 | 149273.89 | -7007.89 | -4.695% | 164396 | -22130 | -13.46%
Q405 | NY | SOL-10409 | 157165.25 | 179366.95 | -22201.7 | -12.38% | 179263.26 | -22098.01 | -12.33%
Q435 | NY | SOL-10923 | 194191.125 | 168797.9 | 25393.225 | 15.04% | 234476 | -40284.875 | -17.18%
Q485 | NY | SOL-10869 | 190327.125 | 151661.1 | 38666.025 | 25.5% | 221354.92 | -31027.795 | -14.02%
Q490 | NY | SOL-10411 | 138378.9863 | 0 | 138378.9863 |  | 155428.01 | -17049.0237 | -10.97%
Q620 | NY | SOL-10867 | 209633.25 | 211811.97 | -2178.72 | -1.029% | 232489.78 | -22856.53 | -9.831%
QMOA | NY | SOL-10415 | 17694.4 | 0 | 17694.4 |  | 20735.358 | -3040.958 | -14.67%
X024 | NY | SOL-10419 | 78479 | 81024.99 | -2545.99 | -3.142% | 83775 | -5296 | -6.322%
X026 | NY | SOL-10420 | 71029.3 | 65342.1 | 5687.2 | 8.704% | 110781.077 | -39751.777 | -35.88%
X090 | NY | SOL-10925 | 58577.9375 | 53198.494 | 5379.4435 | 10.11% | 67723.742 | -9145.8045 | -13.5%
X117 | NY | SOL-10422 | 50060.5 | 55935.623 | -5875.123 | -10.5% | 59437.063 | -9376.563 | -15.78%
X125 | NY | SOL-10423 | 93232.5 | 96324.144 | -3091.644 | -3.21% | 104531.344 | -11298.844 | -10.81%
X134 | NY | SOL-10424 | 90271.1252 | 63524.796 | 26746.3292 | 42.1% | 104673.354 | -14402.2287 | -13.76%
X135 | NY | SOL-10425 | 72376.156 | 76175.456 | -3799.3 | -4.988% | 83456.517 | -11080.361 | -13.28%
X139 JHS 222 | NY | SOL-10426 | 112599.0086 | 121367.306 | -8768.2974 | -7.225% | 130387.114 | -17788.1054 | -13.64%
X140 | NY | SOL-10926 | 64471.3906 | 53511.73 | 10959.6606 | 20.48% | 70176 | -5704.6094 | -8.129%
X166 | NY | SOL-10427 | 66122.7 | 64563.846 | 1558.854 | 2.414% | 77757.807 | -11635.107 | -14.96%
Murphy | MN | SOL-10094 | 2562470 | 2787532 | -225062 | -8.074% | 2767309.7 | -204839.7 | -7.402%
Terning | MN | SOL-10093 | 2794458 | 2901092 | -106634 | -3.676% | 2789624.4 | 4833.6 | 0.1733%
Boas Road 04 | NY | SOL-10908 | 0 | 1034656.96 | -1034656.96 | -100% | 1093253.59 | -711931.59 | -65.12%
Kelly Bridge Farm | NY | SOL-10911 | 66233 | 980629.51 | -914396.51 | -93.25% | 1094228.83 | -1027995.83 | -93.95%
Pool Brook Road | NY | SOL-10909 | 768176 | 816663.44 | -48487.44 | -5.937% | 1053072.03 | -284896.03 | -27.05%
Sackett Lake | NY | SOL-10910 | 584699 | 957255.11 | -372556.11 | -38.92% | 1074743.93 | -490044.93 | -45.6%
Burritt Road | NY | SOL-10913 | 1000340 | 889574.24 | 110765.76 | 12.45% | 1130199.97 | -129859.97 | -11.49%
Villa Roma 1 | NY | SOL-10914 | 860376 | 2453.08 | 857922.92 | 34973% | 1007756.83 | -147380.83 | -14.62%
Villa Roma 2 | NY | SOL-10915 | 847564 | 879081.29 | -31517.29 | -3.585% | 978203.94 | -130639.94 | -13.36%
Washington 1 | NY | SOL-10912 | 1055700 | 1099413.62 | -43713.62 | -3.976% | 1118087.82 | -62387.82 | -5.58%
Washington 3 | NY | SOL-10828 | 1190650 | 730330.59 | 460319.41 | 63.03% | 1367659.88 | -177009.88 | -12.94%
Washington 4 | NY | SOL-10829 | 1121567.5 | 1314711.4 | -193143.9 | -14.69% | 1370606.37 | -249038.87 | -18.17%
Big Tree | NY | SOL-10966 | 1060842 | 0 | 1060842 |  | 1149448.35 | -88606.35 | -7.709%
Canoga | NY | SOL-10965 | 0 | 0 | 0 |  | 0 | 0
County Route 84 | NY | SOL-10967 | 2509160 | 0 | 2509160 |  | 2783810.47 | -274650.47 | -9.866%
Donati | NY | SOL-10968 | 1170726 | 0 | 1170726 |  | 1456005.45 | -285279.45 | -19.59%
Henrietta | NY | SOL-10972 | 2129630 | 0 | 2129630 |  | 3085254.41 | -955624.41 | -30.97%
NY 70 | NY | SOL-10970 | 2785990 | 0 | 2785990 |  | 3424830.79 | -638840.79 | -18.65%
Reid | NY | SOL-10991 | 1878330.1785 | 1851091.6 | 27238.5785 | 1.471% | 2654719 | -776388.8215 | -29.25%
Sangolqui | NY | SOL-10975 | 1143520 | 0 | 1143520 |  | 1424648.06 | -281128.06 | -19.73%
State Highway 17B | NY | SOL-10988 | 2093120 | 0 | 2093120 |  | 1506419.65 | -132629.65 | -8.804%
State Route 14A | NY | SOL-10997 | 234308 | 0 | 234308 |  | 2783106.86 | -1581150.86 | -56.81%
West Creek | NY | SOL-10995 | 2178780 | 0 | 2178780 |  | 2774419.17 | -595639.17 | -21.47%
Wildflower | NY | SOL-10982 | 2174278 | 0 | 2174278 |  | 2806017.95 | -631739.95 | -22.51%
Glen Mary 1 | NY | SOL-10993 | 2254140 | 0 | 2254140 |  | 2879976.84 | -625836.84 | -21.73%
Glen Mary 2 | NY | SOL-10994 | 997420 | 0 | 997420 |  | 1228364.37 | -230944.37 | -18.8%
Telegraph 1 | NY | SOL-11003 | 1943527 | 0 | 1943527 |  | 2080730.64 | -137203.64 | -6.594%
Telegraph 2 | NY | SOL-11004 | 1028696 | 0 | 1028696 |  | 1084004.85 | -55308.85 | -5.102%
Cafferty Hill | NY | SOL-10996 | 2354210 | 0 | 2354210 |  | 2678023.65 | -323813.65 | -12.09%
Dunkleman | NY | SOL-11008 | 2988490 | 0 | 2988490 |  | 3534522.39 | -546032.39 | -15.45%
Route 19 1 | NY | SOL-11001 | 1247000 | 0 | 1247000 |  | 1438654.94 | -191654.94 | -13.32%
Route 19 2 | NY | SOL-11002 | 3022000 | 0 | 3022000 |  | 3557550.39 | -535550.39 | -15.05%
Yellow Mills 1 | NY | SOL-11006 | 925214 | 0 | 925214 |  | 1174204.58 | -248990.58 | -21.21%
Yellow Mills 2 | NY | SOL-11005 | 1033612 | 0 | 1033612 |  | 1211761.03 | -178149.03 | -14.7%
Yellow Mills 3 | NY | SOL-11007 | 1006313 | 0 | 1006313 |  | 1158289.18 | -151976.18 | -13.12%
Catskill | NY | SOL-11021 | 1851707 | 0 | 1851707 |  | 2063982.36 | -212275.36 | -10.28%
Eddy Ridge | NY | SOL-11054 | 1516274 | 0 | 1516274 |  | 1690505 | -174231 | -10.31%
Ridgeway #1 | NY | SOL-11018 | 3266522 | 0 | 3266522 |  | 3549511.65 | -282989.65 | -7.973%
Rivard 1 | NY | SOL-11011 | 2562808.2982 | 103072.2 | 2459736.0982 | 2386% | 1874854.45 | 687953.8482 | 36.69%
Rivard 2 | NY | SOL-11012 | 2622973.0896 | 2586631.8 | 36341.2896 | 1.405% | 2905297.4 | -282324.3104 | -9.718%
Ridgeway #2 | NY | SOL-11027 | 1592692 | 0 | 1592692 |  | 1804344.26 | -211652.26 | -11.73%
Spencer | NY | SOL-11017 | 2826576 | 0 | 2826576 |  | 3451655 | -625079 | -18.11%
Reisender | NY | SOL-10886 | 945850 | 960944.12 | -15094.12 | -1.571% | 1116329.75 | -170479.75 | -15.27%
Finney | NY | SOL-10999 | 2875000 | 0 | 2875000 |  | 3412414.59 | -537414.59 | -15.75%
Davis Solar | NY | SOL-10958 | 878311 | 1055845.3 | -177534.3 | -16.81% | 1305424 | -427113 | -32.72%
Genesee | NY | SOL-10951 | 1060616 | 0 | 1060616 |  | 2666907.12 | -1606291.12 | -60.23%
Landau I | NY | SOL-10891 | 1053070 | 0 | 1053070 |  | 1193405.57 | -140335.57 | -11.76%
Landau II | NY | SOL-10895 | 758420 | 0 | 758420 |  | 1715293.48 | -979333.48 | -57.09%
New Beginnings | NY | SOL-10890 | 651810 | 1055750.54 | -403940.54 | -38.26% | 1163083.22 | -511273.22 | -43.96%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 2684223 | 2695710.707 | -11487.707 | -0.4261% | 3286795.4 | -602572.4 | -18.33%
Brodhead Solar, LLC | NY | SOL-10899 | 1140529 | 1249481.019 | -108952.019 | -8.72% | 1489472.9 | -348943.9 | -23.43%
Svenski | NY | SOL-10894 | 972265 | 0 | 972265 |  | 1270425.09 | -298160.09 | -23.47%
Bantam | NY | SOL-10986 | 250520 | 0 | 250520 |  | 3314779.1 | -3064259.1 | -92.44%
Bogart | NY | SOL-10887 | 984420 | 1035523.6 | -51103.6 | -4.935% | 1146534.17 | -162114.17 | -14.14%
Dubois | NY | SOL-10892 | 606490 | 0 | 606490 |  | 0 | 0
Salt Point | NY | SOL-10888 | 1054770 | 0 | 1054770 |  | 1384848.74 | -330078.74 | -23.84%
Wheatland 2A | NY | SOL-10971 | 2324430 | 0 | 2324430 |  | 2988271.6 | -663841.6 | -22.21%
Wheatland 2B | NY | SOL-10961 | 2624810 | 0 | 2624810 |  | 2967972.63 | -343162.63 | -11.56%
Brickchurch | NY | SOL-10889 | 1099100 | 1072782.29 | 26317.71 | 2.453% | 1414015.08 | -314915.08 | -22.27%
McCarthy Solar | NY | SOL-10992 | 959780 | 0 | 959780 |  | 1182855.18 | -223075.18 | -18.86%
Costanza | NY | SOL-10907 | 1006080 | 0 | 1006080 |  | 1201762.63 | -195682.63 | -16.28%
Lockenhurst Pond | NY | SOL-11000 | 1129440 | 1207206.1 | -77766.1 | -6.442% | 1369272 | -239832 | -17.52%
Drinkwater | NY | SOL-10896 | 1062410 | 0 | 1062410 |  | 1199836.77 | -137426.77 | -11.45%
Altamont | NY | SOL-11085 | 2084313 | 2143289 | -58976 | -2.752% | 2071550 | 12763 | 0.6161%
Krumkill North | NY | SOL-11086 | 2025116 | 2236316.2 | -211200.2 | -9.444% | 2340825 | -315709 | -13.49%
Krumkill South | NY | SOL-11087 | 1677481 | 1771167.5 | -93686.5 | -5.29% | 1835137.2 | -157656.2 | -8.591%
X092 | NY | SOL-11189 | 54707 | 55248.52 | -541.52 | -0.9802% | 64283 | -9576 | -14.9%
X093 | NY | SOL-10932 | 15614.1094 | 25777.97 | -10163.8606 | -39.43% | 45364 | -29749.8906 | -65.58%
X095 | NY | SOL-10929 | 54487.625 | 0 | 54487.625 |  | 61390 | -6902.375 | -11.24%
X181 | NY | SOL-10428 | 96280.418 | 0 | 96280.418 |  | 113233 | -16952.582 | -14.97%
X415 | NY | SOL-10429 | 63644.3906 | 0 | 63644.3906 |  | 66105 | -2460.6094 | -3.722%
K198 | NY | SOL-10930 | 46883.6211 | 30962.55 | 15921.0711 | 51.42% | 50588 | -3704.3789 | -7.323%
K203 | NY | SOL-11190 | 59019.9 | 53425.02 | 5594.88 | 10.47% | 68891 | -9871.1 | -14.33%
K213 | NY | SOL-11191 | 61858.5 | 69739.38 | -7880.88 | -11.3% | 72319 | -10460.5 | -14.46%
K217 | NY | SOL-10933 | 35164.4297 | 0 | 35164.4297 |  | 39839 | -4674.5703 | -11.73%
K307 | NY | SOL-10876 | 74822.0859 | 0 | 74822.0859 |  | 83519 | -8696.9141 | -10.41%
K610 | NY | SOL-11158 | 84591.9 | 85211.29 | -619.39 | -0.7269% | 96940 | -12348.1 | -12.74%
M025 | NY | SOL-10392 | 36596.9473 | 52975.84 | -16378.8927 | -30.92% | 83454 | -46857.0527 | -56.15%
M028 | NY | SOL-10381 | 59667.6268 | 38868.58 | 20799.0468 | 53.51% | 65636 | -5968.3732 | -9.093%
Q030 | NY | SOL-10878 | 72570.4923 | 0 | 72570.4923 |  | 78882 | -6311.5077 | -8.001%
Q130 | NY | SOL-10877 | 41552.8086 | 0 | 41552.8086 |  | 44793.53 | -3240.7214 | -7.235%
Q196 | NY | SOL-10879 | 54201.8527 | 0 | 54201.8527 |  | 58065 | -3863.1473 | -6.653%
Q220 | NY | SOL-10873 | 63817.4453 | 0 | 63817.4453 |  | 67422 | -3604.5547 | -5.346%
Q205 | NY | SOL-10922 | 75330.9453 | 86255.98 | -10925.0347 | -12.67% | 80611 | -5280.0547 | -6.55%
Q400 | NY | SOL-10871 | 89219.3516 | 0 | 89219.3516 |  | 130238 | -41018.6484 | -31.5%
R003 | NY | SOL-10416 | 105423.648 | 31288 | 74135.648 | 236.9% | 118413 | -12989.352 | -10.97%
R007 | NY | SOL-10417 | 113058.1797 | 77141.24 | 35916.9397 | 46.56% | 127251.59 | -14193.4103 | -11.15%
BK16 | NY | SOL-11093 | 117349.5859 | 0 | 117349.5859 |  | 126541 | -9191.4141 | -7.264%
Trenton - Trenton East | IL | SOL-11060 | 906995.4998 | 991887.2 | -84891.7002 | -8.559% | 1462562 | -555566.5002 | -37.99%
Trenton - Trenton West | IL | SOL-11061 | 359754.0524 | 586747.88 | -226993.8276 | -38.69% | 1461120 | -1101365.9476 | -75.38%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 1442059 | 1730745.9 | -288686.9 | -16.68% | 0 | 1037600
X018 | NY | SOL-10418 | 39969.9269 | 34623.62 | 5346.3069 | 15.44% | 64694 | -24724.0731 | -38.22%
Janiak Solar | NY | SOL-10898 | 1002214 | 1056635.7 | -54421.7 | -5.15% | 1201725 | -199511 | -16.6%
County Route 11B | NY | SOL-10983 | 1411312 | 0 | 1411312 |  | 0 | 0
Barone | NY | SOL-11034 | 1246549 | 0 | 1246549 |  | 1467985.7 | -221436.7 | -15.08%
Cedarville | IL | SOL-11069 | 1244661 | 1224082.1 | 20578.9 | 1.681% | 1487656.8 | -242995.8 | -16.33%
O'Brien Hill #1 | NY | SOL-11098 | 68017 | 0 | 68017 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 1533876.06 | 0 | 1533876.06 |  | 288848 | -148179 | -51.3%
Trinity - Freeport | IL | SOL-11057 | 1352828 | 1162840.7 | 189987.3 | 16.34% | 1066336 | -105450 | -9.889%
Ransom | NY | SOL-11157 | 1662379.8 | 0 | 1662379.8 |  | 326042 | -169111 | -51.87%
Horseheads - Wedge | NY | SOL-11160 | 1193377 | 0 | 1193377 |  | 344639 | -179578 | -52.11%
Otisville - Shoddy Hollow | NY | SOL-11185 | 1814688.1 | 0 | 1814688.1 |  | 363236 | -190044 | -52.32%
Wellsville - Chenunda Creek | NY | SOL-11187 | 1001224.9 | 0 | 1001224.9 |  | 381833 | -200510 | -52.51%
DC: Washington - Essex Condominium | DC | SOL-10036 | 12238 | 15626.204 | -3388.204 | -21.68% | 15173.213 | -2935.213 | -19.34%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 24365 | 35826.98 | -11461.98 | -31.99% | 38937.007 | -14572.007 | -37.42%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 40492 | 32076.989 | 8415.011 | 26.23% | 38916.21 | 1575.79 | 4.049%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 0 | 0 |  | 0 | 0
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 0 | 0 | 0 |  | 0 | 0
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 0 | 0 | 0 |  | 0 | 0
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 0 | 0 | 0 |  | 0 | 0
NY: Whitesville - Independence North | NY | SOL-11186 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 0 | 0 | 0 |  | 0 | 0
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 0 | 0 | 0 |  | 0 | 0
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 0 | 0 | 0 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 0 | 0 | 0 |  | 0 | 0
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
Generate Capital |  |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  |  | 154440947.7485 | 142263992.335 | 12176955.4135 | 8.559% | 141919842.8948 | 12521104.8537 | 8.823%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 67502.625 | 116340.784 | -48838.159 | -41.98% | 105071.805 | -37569.18 | -35.76%
K041 | NY | SOL-10357 | 83369.3125 | 94700.345 | -11331.0325 | -11.97% | 84647 | -1277.6875 | -1.509%
K043 | NY | SOL-10358 | 100275.625 | 105766.011 | -5490.386 | -5.191% | 18422.888 | 81852.737 | 444.3%
K058 | NY | SOL-10360 | 47810.7505 | 49255.904 | -1445.1535 | -2.934% | 79064.713 | -31253.9625 | -39.53%
K115 | NY | SOL-10361 | 23853.328 | 45857.462 | -22004.134 | -47.98% | 48263.555 | -24410.227 | -50.58%
K152 | NY | SOL-10362 | 30753.563 | 31815.94 | -1062.377 | -3.339% | 30294 | 459.563 | 1.517%
K166 | NY | SOL-10363 | 108447.875 | 121781.591 | -13333.716 | -10.95% | 111255.987 | -2808.112 | -2.524%
K206 | NY | SOL-10927 | 68533.9844 | 63397.64 | 5136.3444 | 8.102% | 63283 | 5250.9844 | 8.298%
K251 | NY | SOL-10365 | 65859.8125 | 0 | 65859.8125 |  | 70866.957 | -5007.1445 | -7.066%
K269 | NY | SOL-10366 | 67163.0005 | 78829.963 | -11666.9625 | -14.8% | 67148.255 | 14.7455 | 0.02196%
K273 | NY | SOL-10367 | 47901.5625 | 0 | 47901.5625 |  | 61742 | -25931.4375 | -42%
K287 | NY | SOL-10919 | 57940.5318 | 50076.436 | 7864.0958 | 15.7% | 57858 | 82.5318 | 0.1426%
K298 | NY | SOL-10368 | 63226.188 | 67072.088 | -3845.9 | -5.734% | 66523 | -3296.812 | -4.956%
K335 | NY | SOL-10370 | 65936.625 | 74000.684 | -8064.059 | -10.9% | 52227.097 | 13709.528 | 26.25%
K345 | NY | SOL-10920 | 77640.75 | 45360.697 | 32280.053 | 71.16% | 76681.5 | 959.25 | 1.251%
K445 | NY | SOL-10373 | 63606.094 | 70248.956 | -6642.862 | -9.456% | 63005.58 | 600.514 | 0.9531%
K495 | NY | SOL-10374 | 265274 | 273026.19 | -7752.19 | -2.839% | 276632.596 | -11358.596 | -4.106%
M020 | NY | SOL-10380 | 71058.0935 | 72481.083 | -1422.9895 | -1.963% | 72379.5 | -1321.4065 | -1.826%
M092 | NY | SOL-10383 | 69569 | 73855.492 | -4286.492 | -5.804% | 69176.449 | 392.551 | 0.5675%
M143 | NY | SOL-10384 | 74840.1255 | 90753.038 | -15912.9125 | -17.53% | 75396.105 | -555.9795 | -0.7374%
M144 | NY | SOL-10385 | 114122.375 | 124493.745 | -10371.37 | -8.331% | 129978.841 | -15856.466 | -12.2%
M167 | NY | SOL-10386 | 84940.5317 | 64544.728 | 20395.8037 | 31.6% | 92900.014 | -7959.4823 | -8.568%
M188 | NY | SOL-10387 | 59380.5938 | 61299.343 | -1918.7492 | -3.13% | 66314.489 | -6933.8952 | -10.46%
EMHC | NY | SOL-10351 | 25153.6483 | 19554.665 | 5598.9833 | 28.63% | 30192.233 | -5038.5847 | -16.69%
Q008 | NY | SOL-10397 | 26542.0306 | 31294.699 | -4752.6684 | -15.19% | 92935 | -66392.9694 | -71.44%
Q018 | NY | SOL-10398 | 61128.5625 | 66556.276 | -5427.7135 | -8.155% | 50883.92 | 10244.6425 | 20.13%
Q021 | NY | SOL-10399 | 49071.563 | 48793.346 | 278.217 | 0.5702% | 46463.824 | 2607.739 | 5.612%
Q025 | NY | SOL-10400 | 83921.75 | 82790.903 | 1130.847 | 1.366% | 42188.5 | 41733.25 | 98.92%
Q074 | NY | SOL-10402 | 51157.4375 | 50633.337 | 524.1005 | 1.035% | 52420.515 | -1263.0775 | -2.41%
Q115 | NY | SOL-10872 | 70737.188 | 75838.468 | -5101.28 | -6.727% | 69710.339 | 1026.849 | 1.473%
Q139 | NY | SOL-10403 | 42470.7188 | 45742.152 | -3271.4333 | -7.152% | 44081 | -1610.2812 | -3.653%
Q157 | NY | SOL-10404 | 70272.563 | 86302.056 | -16029.493 | -18.57% | 75192.888 | -4920.325 | -6.544%
Q192 | NY | SOL-10406 | 116700.125 | 128995.252 | -12295.127 | -9.531% | 73423.0738 | 43277.0512 | 58.94%
Q210 | NY | SOL-10407 | 91265 | 96334.689 | -5069.689 | -5.263% | 94829 | -3564 | -3.758%
Q229 | NY | SOL-10408 | 41357.5625 | 47038.144 | -5680.5815 | -12.08% | 39172.507 | 2185.0555 | 5.578%
Q231 | NY | SOL-10870 | 149443 | 165122.901 | -15679.901 | -9.496% | 158130.5 | -8687.5 | -5.494%
Q405 | NY | SOL-10409 | 175885.5 | 195128.265 | -19242.765 | -9.862% | 169322.102 | 6563.398 | 3.876%
Q435 | NY | SOL-10923 | 174837.25 | 179471.697 | -4634.447 | -2.582% | 220244.5 | -45407.25 | -20.62%
Q485 | NY | SOL-10869 | 209581.4375 | 168001.176 | 41580.2615 | 24.75% | 208686.769 | 894.6685 | 0.4287%
Q490 | NY | SOL-10411 | 146882.1387 | 0 | 146882.1387 |  | 146984.135 | -101.9963 | -0.06939%
Q620 | NY | SOL-10867 | 228427.7498 | 232227.803 | -3800.0532 | -1.636% | 220518.303 | 7909.4468 | 3.587%
QMOA | NY | SOL-10415 | 19343.5 | 0 | 19343.5 |  | 19960.398 | -616.898 | -3.091%
X024 | NY | SOL-10419 | 88103.6872 | 88458.057 | -354.3698 | -0.4006% | 78887 | 9216.6872 | 11.68%
X026 | NY | SOL-10420 | 77426.5 | 72581.792 | 4844.708 | 6.675% | 106017.776 | -28591.276 | -26.97%
X090 | NY | SOL-10925 | 62442.4065 | 57426.805 | 5015.6015 | 8.734% | 64862 | -2419.5935 | -3.73%
X117 | NY | SOL-10422 | 56000.8 | 61264.91 | -5264.11 | -8.592% | 57083.04 | -1082.24 | -1.896%
X125 | NY | SOL-10423 | 103474.8125 | 106407.308 | -2932.4955 | -2.756% | 98306.009 | 5168.8035 | 5.258%
X134 | NY | SOL-10424 | 99947.751 | 41349.814 | 58597.937 | 141.7% | 98297 | 1650.751 | 1.679%
X135 | NY | SOL-10425 | 77905.2505 | 95760.584 | -17855.3335 | -18.65% | 78460 | -554.7495 | -0.707%
X139 JHS 222 | NY | SOL-10426 | 116507.1215 | 133106.131 | -16599.0095 | -12.47% | 124378.5 | -7871.3785 | -6.329%
X140 | NY | SOL-10926 | 69917.0317 | 58796.188 | 11120.8438 | 18.91% | 66691 | 3226.0317 | 4.837%
X166 | NY | SOL-10427 | 72747.5 | 72761.211 | -13.711 | -0.01884% | 73891 | -1143.5 | -1.548%
Murphy | MN | SOL-10094 | 2759660 | 3005254.034 | -245594.034 | -8.172% | 2882979.8 | -123319.8 | -4.278%
Terning | MN | SOL-10093 | 2923784 | 3119352.667 | -195568.667 | -6.27% | 2845764.85 | 78019.15 | 2.742%
Boas Road 04 | NY | SOL-10908 | 0 | 418860.46 | -418860.46 | -100% | 1106907.333 | -1106907.333 | -100%
Kelly Bridge Farm | NY | SOL-10911 | 636925 | 687272.6 | -50347.6 | -7.326% | 1099105.349 | -462180.349 | -42.05%
Pool Brook Road | NY | SOL-10909 | 888544 | 975500.41 | -86956.41 | -8.914% | 1061937.529 | -173393.529 | -16.33%
Sackett Lake | NY | SOL-10910 | 1087983 | 182350.26 | 905632.74 | 496.6% | 1088535.226 | -552.226 | -0.05073%
Burritt Road | NY | SOL-10913 | 1198010 | 890877.67 | 307132.33 | 34.48% | 1121561.463 | 76448.537 | 6.816%
Villa Roma 1 | NY | SOL-10914 | 979565 | 4117.15 | 975447.85 | 23692% | 972293.455 | 7271.545 | 0.7479%
Villa Roma 2 | NY | SOL-10915 | 931050 | 1031329.21 | -100279.21 | -9.723% | 942740.46 | -11690.46 | -1.24%
Washington 1 | NY | SOL-10912 | 1113540 | 1257149.16 | -143609.16 | -11.42% | 1107252.122 | 6287.878 | 0.5679%
Washington 3 | NY | SOL-10828 | 1133007 | 3115074.42 | -1982067.42 | -63.63% | 1352995.109 | -219988.109 | -16.26%
Washington 4 | NY | SOL-10829 | 1339173 | 1444615.63 | -105442.63 | -7.299% | 1356039.065 | -16866.065 | -1.244%
Big Tree | NY | SOL-10966 | 1209050 | 1206230 | 2820 | 0.2338% | 1103905.75 | 105144.25 | 9.525%
Canoga | NY | SOL-10965 | 2558980 | 0 | 2558980 |  | 0 | 2558980
County Route 84 | NY | SOL-10967 | 2886740 | 2782690 | 104050 | 3.739% | 2824365.998 | 62374.002 | 2.208%
Donati | NY | SOL-10968 | 1356620 | 0 | 1356620 |  | 1425547.787 | -68927.787 | -4.835%
Henrietta | NY | SOL-10972 | 3055530 | 3010270 | 45260 | 1.504% | 2951284.322 | 104245.678 | 3.532%
NY 70 | NY | SOL-10970 | 3307430 | 3299630 | 7800 | 0.2364% | 3181543.876 | 125886.124 | 3.957%
Reid | NY | SOL-10991 | 2475451.8452 | 2211093.424 | 264358.4212 | 11.96% | 1675506.5 | 799945.3452 | 47.74%
Sangolqui | NY | SOL-10975 | 1139710 | 1068400 | 71310 | 6.674% | 1392778.811 | -253068.811 | -18.17%
State Highway 17B | NY | SOL-10988 | 2485060 | 1556820 | 928240 | 59.62% | 0 | 0
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 2839019.421 | -2839019.421 | -100%
West Creek | NY | SOL-10995 | 2901170 | 2543560 | 357610 | 14.06% | 2835607.795 | 65562.205 | 2.312%
Wildflower | NY | SOL-10982 | 2517103 | 2510655 | 6448 | 0.2568% | 2711596.06 | -194493.06 | -7.173%
Glen Mary 1 | NY | SOL-10993 | 2885780 | 2874200 | 11580 | 0.4029% | 2793945.606 | 91834.394 | 3.287%
Glen Mary 2 | NY | SOL-10994 | 1264540 | 473050 | 791490 | 167.3% | 1188326.806 | 76213.194 | 6.413%
Telegraph 1 | NY | SOL-11003 | 2147619 | 0 | 2147619 |  | 1995786.274 | 151832.726 | 7.608%
Telegraph 2 | NY | SOL-11004 | 1111130 | 0 | 1111130 |  | 1039062.123 | 72067.877 | 6.936%
Cafferty Hill | NY | SOL-10996 | 2982310 | 3076673.95 | -94363.95 | -3.067% | 2742218.603 | 240091.397 | 8.755%
Dunkleman | NY | SOL-11008 | 3618040 | 3609080 | 8960 | 0.2483% | 3338553.303 | 279486.697 | 8.371%
Route 19 1 | NY | SOL-11001 | 1230240 | 1225300 | 4940 | 0.4032% | 1356278.644 | -126038.644 | -9.293%
Route 19 2 | NY | SOL-11002 | 3520420 | 3509420 | 11000 | 0.3134% | 3352274.038 | 168145.962 | 5.016%
Yellow Mills 1 | NY | SOL-11006 | 1010411 | 1005252 | 5159 | 0.5132% | 1162592.176 | -152181.176 | -13.09%
Yellow Mills 2 | NY | SOL-11005 | 998560 | 0 | 998560 |  | 1206340.466 | -207780.466 | -17.22%
Yellow Mills 3 | NY | SOL-11007 | 950025 | 930142 | 19883 | 2.138% | 1148258.991 | -198233.991 | -17.26%
Catskill | NY | SOL-11021 | 1275409 | 358236 | 917173 | 256% | 2134906.812 | -859497.812 | -40.26%
Eddy Ridge | NY | SOL-11054 | 1621025 | 1615367 | 5658 | 0.3503% | 1665630 | -44605 | -2.678%
Ridgeway #1 | NY | SOL-11018 | 3897796 | 3884735 | 13061 | 0.3362% | 3692237.64 | 205558.36 | 5.567%
Rivard 1 | NY | SOL-11011 | 2948952.1043 | 3133096.68 | -184144.5757 | -5.877% | 2775918.31 | 173033.7943 | 6.233%
Rivard 2 | NY | SOL-11012 | 3083382 | 3020007.84 | 63374.16 | 2.098% | 2669049.41 | 414332.59 | 15.52%
Ridgeway #2 | NY | SOL-11027 | 1241274 | 1237054 | 4220 | 0.3411% | 1107137.51 | 134136.49 | 12.12%
Spencer | NY | SOL-11017 | 3371243.05 | 3361661.15 | 9581.9 | 0.285% | 3433745 | -62501.95 | -1.82%
Reisender | NY | SOL-10886 | 1122430 | 1130183 | -7753 | -0.686% | 1116783.077 | 5646.923 | 0.5056%
Finney | NY | SOL-10999 | 2276510 | 2261080 | 15430 | 0.6824% | 3489900.231 | -1213390.231 | -34.77%
Davis Solar | NY | SOL-10958 | 1158562 | 1260227.83 | -101665.83 | -8.067% | 1282123 | -123561 | -9.637%
Genesee | NY | SOL-10951 | 2560299.3 | 2224787.89 | 335511.41 | 15.08% | 2663980.348 | -103681.048 | -3.892%
Landau I | NY | SOL-10891 | 1207510 | 0 | 1207510 |  | 1208529.09 | -1019.09 | -0.08432%
Landau II | NY | SOL-10895 | 1645320 | 0 | 1645320 |  | 0 | 0
New Beginnings | NY | SOL-10890 | 1193220 | 1208310.89 | -15090.89 | -1.249% | 1169690.215 | 23529.785 | 2.012%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 2698101 | 2805159.111 | -107058.111 | -3.816% | 2782056.12 | -83955.12 | -3.018%
Brodhead Solar, LLC | NY | SOL-10899 | 1878949 | 1958582.325 | -79633.325 | -4.066% | 1905468.15 | -26519.15 | -1.392%
Svenski | NY | SOL-10894 | 1194178 | 0 | 1194178 |  | 1219673.606 | -25495.606 | -2.09%
Bantam | NY | SOL-10986 | 200870 | 1574600 | -1373730 | -87.24% | 3392222.883 | -3191352.883 | -94.08%
Bogart | NY | SOL-10887 | 678890 | 1074976.16 | -396086.16 | -36.85% | 1149750.349 | -470860.349 | -40.95%
Dubois | NY | SOL-10892 | 515980 | 515924.51 | 55.49 | 0.01076% | 0 | 0
Salt Point | NY | SOL-10888 | 1113070 | 1113070 | 0 | 0% | 1341684.951 | -228614.951 | -17.04%
Wheatland 2A | NY | SOL-10971 | 2920400 | 2914370 | 6030 | 0.2069% | 3022697.842 | -102297.842 | -3.384%
Wheatland 2B | NY | SOL-10961 | 3079390 | 3073160 | 6230 | 0.2027% | 2991938.269 | 87451.731 | 2.923%
Brickchurch | NY | SOL-10889 | 0 | 519962.55 | -519962.55 | -100% | 1381198.446 | -1381198.446 | -100%
McCarthy Solar | NY | SOL-10992 | 628760 | 0 | 628760 |  | 1210292.02 | -581532.02 | -48.05%
Costanza | NY | SOL-10907 | 1184650 | 1169904.63 | 14745.37 | 1.26% | 1203943.061 | -19293.061 | -1.602%
Lockenhurst Pond | NY | SOL-11000 | 1340895 | 1463999.678 | -123104.678 | -8.409% | 1405318 | -64423 | -4.584%
Drinkwater | NY | SOL-10896 | 1340940 | 1326560 | 14380 | 1.084% | 1238976.337 | 101963.663 | 8.23%
Altamont | NY | SOL-11085 | 2551005 | 2642654.473 | -91649.473 | -3.468% | 1995490.53 | 555514.47 | 27.84%
Krumkill North | NY | SOL-11086 | 2295506 | 2676349.74 | -380843.74 | -14.23% | 2293853.94 | 1652.06 | 0.07202%
Krumkill South | NY | SOL-11087 | 1945802 | 2121566.961 | -175764.961 | -8.285% | 1798301.75 | 147500.25 | 8.202%
X092 | NY | SOL-11189 | 60146.2 | 60576.128 | -429.928 | -0.7097% | 60080.5 | 65.7 | 0.1094%
X093 | NY | SOL-10932 | 40591.6976 | 42694.315 | -2102.6174 | -4.925% | 42464 | -1872.3024 | -4.409%
X095 | NY | SOL-10929 | 59575.8755 | 57040.893 | 2534.9825 | 4.444% | 57702 | 1873.8755 | 3.248%
X181 | NY | SOL-10428 | 111198.1877 | 95831.21 | 15366.9778 | 16.04% | 106859 | 4339.1878 | 4.061%
X415 | NY | SOL-10429 | 70480.5939 | 60472.819 | 10007.7749 | 16.55% | 62182.5 | 8298.0939 | 13.34%
K198 | NY | SOL-10930 | 50674.7578 | 49440.792 | 1233.9658 | 2.496% | 49230.5 | 1444.2578 | 2.934%
K203 | NY | SOL-11190 | 66025.5 | 59001.54 | 7023.96 | 11.9% | 66093.5 | -68 | -0.1029%
K213 | NY | SOL-11191 | 74538 | 79135.172 | -4597.172 | -5.809% | 69685.5 | 4852.5 | 6.963%
K217 | NY | SOL-10933 | 39628.4145 | 37568.988 | 2059.4265 | 5.482% | 37715.5 | 1912.9145 | 5.072%
K307 | NY | SOL-10876 | 81938.4223 | 84461.912 | -2523.4898 | -2.988% | 78543 | 3395.4222 | 4.323%
K610 | NY | SOL-11158 | 70866.1 | 94164.542 | -23298.442 | -24.74% | 92738 | -21871.9 | -23.58%
M025 | NY | SOL-10392 | 63842.0231 | 87869.323 | -24027.2999 | -27.34% | 81637.5 | -17795.4769 | -21.8%
M028 | NY | SOL-10381 | 67025.0214 | 64202.36 | 2822.6614 | 4.397% | 62213.5 | 4811.5214 | 7.734%
Q030 | NY | SOL-10878 | 78967.1951 | 78003.445 | 963.7501 | 1.236% | 74861 | 4106.1951 | 5.485%
Q130 | NY | SOL-10877 | 44386.8825 | 41472.133 | 2914.7495 | 7.028% | 42914.892 | 1471.9905 | 3.43%
Q196 | NY | SOL-10879 | 58232.2006 | 59693.25 | -1461.0494 | -2.448% | 55529 | 2703.2006 | 4.868%
Q220 | NY | SOL-10873 | 69023.2966 | 79109.393 | -10086.0964 | -12.75% | 63784 | 5239.2966 | 8.214%
Q205 | NY | SOL-10922 | 75602.7185 | 97699.793 | -22097.0745 | -22.62% | 76269 | -666.2815 | -0.8736%
Q400 | NY | SOL-10871 | 81220.7652 | 0 | 81220.7652 |  | 123657 | -42436.2348 | -34.32%
R003 | NY | SOL-10416 | 105505.9651 | 117887.207 | -12381.2419 | -10.5% | 114638 | -9132.0349 | -7.966%
R007 | NY | SOL-10417 | 126316.844 | 127802.526 | -1485.682 | -1.162% | 128528.887 | -2212.043 | -1.721%
BK16 | NY | SOL-11093 | 128771.3123 | 127834.132 | 937.1802 | 0.7331% | 122483 | 6288.3123 | 5.134%
Trenton - Trenton East | IL | SOL-11060 | 1231604 | 1309024.292 | -77420.292 | -5.914% | 1476898 | -215809 | -14.61%
Trenton - Trenton West | IL | SOL-11061 | 757332 | 1112799.898 | -355467.898 | -31.94% | 1483031.5 | -725699.5 | -48.93%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 1450176 | 1521136.759 | -70960.759 | -4.665% | 1122135 | 328041 | 29.23%
X018 | NY | SOL-10418 | 61231.3021 | 43932.8 | 17298.5021 | 39.37% | 63163.5 | -1932.1979 | -3.059%
Janiak Solar | NY | SOL-10898 | 1173266 | 1246179.623 | -72913.623 | -5.851% | 1219570 | -46304 | -3.797%
County Route 11B | NY | SOL-10983 | 3974507.01 | 3962885.09 | 11621.92 | 0.2933% | 0 | 0
Barone | NY | SOL-11034 | 1923823 | 1915815 | 8008 | 0.418% | 1986020 | -62197 | -3.132%
Cedarville | IL | SOL-11069 | 1231957 | 1207022.139 | 24934.861 | 2.066% | 1468286.94 | -236329.94 | -16.1%
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 3136487 | 3136145 | 342 | 0.01091% | 0 | 0
Trinity - Freeport | IL | SOL-11057 | 1359928 | 1546158.528 | -186230.528 | -12.04% | 1497943.5 | -138015.5 | -9.214%
Ransom | NY | SOL-11157 | 2884283 | 2873176 | 11107 | 0.3866% | 0 | 0
Horseheads - Wedge | NY | SOL-11160 | 1975316 | 1969790 | 5526 | 0.2805% | 0 | 0
Otisville - Shoddy Hollow | NY | SOL-11185 | 3246989 | 3233839 | 13150 | 0.4066% | 0 | 0
Wellsville - Chenunda Creek | NY | SOL-11187 | 1557617 | 1553497 | 4120 | 0.2652% | 0 | 0
DC: Washington - Essex Condominium | DC | SOL-10036 | 11672 | 14990.373 | -3318.373 | -22.14% | 14303.385 | -2631.385 | -18.4%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 30106 | 36357.664 | -6251.664 | -17.19% | 38737.241 | -8631.241 | -22.28%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 41700 | 32614.072 | 9085.928 | 27.86% | 38722.739 | 2977.261 | 7.689%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 884463 | 994557.329 | -110094.329 | -11.07% | 1028639.56 | -144176.56 | -14.02%
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 2107273 | 2269947.43 | -162674.43 | -7.166% | 2460717.7 | -353444.7 | -14.36%
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 940486 | 846354.673 | 94131.327 | 11.12% | 1026101.38 | -85615.38 | -8.344%
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 859803.23 | 883303.58 | -23500.35 | -2.661% | 839014.5 | 0 | 0%
NY: Whitesville - Independence North | NY | SOL-11186 | 765233 | 0 | 765233 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 0 | 0 | 0 |  | 0 | 0
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 0 | 0 | 0 |  | 0 | 0
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 0 | 0 | 0 |  | 0 | 0
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 0 | 0 | 0 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 0 | 0 | 0 |  | 0 | 0
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Generate Capital |  |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  |  | 105645417.3132 | 59081949.944 | 46563467.3692 | 78.81% | 72013447.481 | 33631969.8322 | 46.7%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
K026 | NY | SOL-10356 | 30454.125 | 55569.98 | -25115.855 | -45.2% | 46832.976 | -16378.851 | -34.97%
K041 | NY | SOL-10357 | 35445.6562 | 43136.522 | -7690.8657 | -17.83% | 37872 | -2426.3438 | -6.407%
K043 | NY | SOL-10358 | 42458.375 | 48189.83 | -5731.455 | -11.89% | 8527 | 33931.375 | 397.9%
K058 | NY | SOL-10360 | 34453.375 | 38663.584 | -4210.209 | -10.89% | 37338.756 | -2885.381 | -7.728%
K115 | NY | SOL-10361 | 19912.6406 | 24460.821 | -4548.1804 | -18.59% | 20929.894 | -1017.2534 | -4.86%
K152 | NY | SOL-10362 | 12791.4375 | 14552.785 | -1761.3475 | -12.1% | 14607 | -1815.5625 | -12.43%
K166 | NY | SOL-10363 | 39885.125 | 53853.75 | -13968.625 | -25.94% | 50763.78 | -10878.655 | -21.43%
K206 | NY | SOL-10927 | 26981.75 | 25433.707 | 1548.043 | 6.087% | 26524 | 457.75 | 1.726%
K251 | NY | SOL-10365 | 30978.1875 | 0 | 30978.1875 |  | 34465.477 | -3487.2895 | -10.12%
K269 | NY | SOL-10366 | 28142.3125 | 36505.861 | -8363.5485 | -22.91% | 29588.357 | -1446.0445 | -4.887%
K273 | NY | SOL-10367 | 25103.625 | 0 | 25103.625 |  | 39711 | -14607.375 | -36.78%
K287 | NY | SOL-10919 | 25205.5 | 24496.686 | 708.814 | 2.894% | 26487 | -1281.5 | -4.838%
K298 | NY | SOL-10368 | 24099.3125 | 31905.348 | -7806.0355 | -24.47% | 24653 | -553.6875 | -2.246%
K335 | NY | SOL-10370 | 26581 | 33904.708 | -7323.708 | -21.6% | 33788 | -7207 | -21.33%
K345 | NY | SOL-10920 | 31830.0312 | 23574.693 | 8255.3383 | 35.02% | 28737 | 3093.0312 | 10.76%
K445 | NY | SOL-10373 | 21926.0625 | 34224.683 | -12298.6205 | -35.93% | 26183.095 | -4257.0325 | -16.26%
K495 | NY | SOL-10374 | 111985 | 132073.68 | -20088.68 | -15.21% | 154630.52 | -42645.52 | -27.58%
M020 | NY | SOL-10380 | 29837.4062 | 32481.911 | -2644.5048 | -8.141% | 33064 | -3226.5938 | -9.759%
M092 | NY | SOL-10383 | 28107.6875 | 33699.729 | -5592.0415 | -16.59% | 29641.843 | -1534.1555 | -5.176%
M143 | NY | SOL-10384 | 31464.75 | 36652.031 | -5187.281 | -14.15% | 32386.762 | -922.012 | -2.847%
M144 | NY | SOL-10385 | 47023.5625 | 59811.88 | -12788.3175 | -21.38% | 74195.34 | -27171.7775 | -36.62%
M167 | NY | SOL-10386 | 30347.2812 | 28580.418 | 1766.8633 | 6.182% | 34506.588 | -4159.3067 | -12.05%
M188 | NY | SOL-10387 | 24815.4511 | 29560.055 | -4744.6039 | -16.05% | 38791.34 | -13975.8889 | -36.03%
EMHC | NY | SOL-10351 | 9275.2812 | 7334.401 | 1940.8803 | 26.46% | 9696.839 | -421.5577 | -4.347%
Q008 | NY | SOL-10397 | 39383.4688 | 46973.01 | -7589.5412 | -16.16% | 40984 | -1600.5312 | -3.905%
Q018 | NY | SOL-10398 | 27255.8125 | 31143.251 | -3887.4385 | -12.48% | 26907.158 | 348.6545 | 1.296%
Q021 | NY | SOL-10399 | 20806.5625 | 25981.379 | -5174.8165 | -19.92% | 21756.965 | -950.4025 | -4.368%
Q025 | NY | SOL-10400 | 36301.375 | 39417.943 | -3116.568 | -7.906% | 23730 | 12571.375 | 52.98%
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 13063 | -13063 | -100%
Q115 | NY | SOL-10872 | 28124.6875 | 36399.024 | -8274.3365 | -22.73% | 33465.078 | -5340.3905 | -15.96%
Q139 | NY | SOL-10403 | 17939.125 | 20062.777 | -2123.652 | -10.59% | 20982 | -3042.875 | -14.5%
Q157 | NY | SOL-10404 | 32149.4375 | 44417.85 | -12268.4125 | -27.62% | 37168.198 | -5018.7605 | -13.5%
Q192 | NY | SOL-10406 | 40987.75 | 60382.54 | -19394.79 | -32.12% | 55753.73 | -14765.98 | -26.48%
Q210 | NY | SOL-10407 | 42234.25 | 43528.02 | -1293.77 | -2.972% | 46628 | -4393.75 | -9.423%
Q229 | NY | SOL-10408 | 16208.1875 | 21926.599 | -5718.4115 | -26.08% | 16049.908 | 158.2795 | 0.9862%
Q231 | NY | SOL-10870 | 67142 | 89231.49 | -22089.49 | -24.76% | 63830 | 3312 | 5.189%
Q405 | NY | SOL-10409 | 78740.25 | 93519.09 | -14778.84 | -15.8% | 83205.45 | -4465.2 | -5.366%
Q435 | NY | SOL-10923 | 102886.375 | 76409.29 | 26477.085 | 34.65% | 97164 | 5722.375 | 5.889%
Q485 | NY | SOL-10869 | 85016 | 81573.55 | 3442.45 | 4.22% | 91876.69 | -6860.69 | -7.467%
Q490 | NY | SOL-10411 | 62420.5 | 0 | 62420.5 |  | 69637.51 | -7217.01 | -10.36%
Q620 | NY | SOL-10867 | 98566.75 | 104767.25 | -6200.5 | -5.918% | 101490.79 | -2924.04 | -2.881%
QMOA | NY | SOL-10415 | 9015.4 | 0 | 9015.4 |  | 9713.174 | -697.774 | -7.184%
X024 | NY | SOL-10419 | 35761.375 | 40389.757 | -4628.382 | -11.46% | 36009 | -247.625 | -0.6877%
X026 | NY | SOL-10420 | 29509.7 | 34596.741 | -5087.041 | -14.7% | 46900.508 | -17390.808 | -37.08%
X090 | NY | SOL-10925 | 19662.3125 | 21788.077 | -2125.7645 | -9.757% | 27326 | -7663.6875 | -28.05%
X117 | NY | SOL-10422 | 21574.6 | 29352.572 | -7777.972 | -26.5% | 26823.283 | -5248.683 | -19.57%
X125 | NY | SOL-10423 | 43521.375 | 50815.85 | -7294.475 | -14.35% | 44429.95 | -908.575 | -2.045%
X134 | NY | SOL-10424 | 36288.4375 | 44077.56 | -7789.1225 | -17.67% | 39593 | -3304.5625 | -8.346%
X135 | NY | SOL-10425 | 34891 | 48163.35 | -13272.35 | -27.56% | 36156 | -1265 | -3.499%
X139 JHS 222 | NY | SOL-10426 | 51318.8139 | 55153.91 | -3835.0961 | -6.953% | 48497 | 2821.8139 | 5.819%
X140 | NY | SOL-10926 | 31111.375 | 27048.616 | 4062.759 | 15.02% | 30154 | 957.375 | 3.175%
X166 | NY | SOL-10427 | 30361.5 | 38953.45 | -8591.95 | -22.06% | 29110 | 1251.5 | 4.299%
Murphy | MN | SOL-10094 | 1081600 | 1583869 | -502269 | -31.71% | 1551645.1 | -470045.1 | -30.29%
Terning | MN | SOL-10093 | 1228156.935 | 1612408.1 | -384251.165 | -23.83% | 1451939.2 | -223782.265 | -15.41%
Boas Road 04 | NY | SOL-10908 | 98956 | 98956 | 0 | 0% | 504203.605 | -405247.605 | -80.37%
Kelly Bridge Farm | NY | SOL-10911 | 283226 | 0 | 283226 |  | 545164.054 | -261938.054 | -48.05%
Pool Brook Road | NY | SOL-10909 | 370214 | 370217 | -3 | -0.0008103% | 532938.966 | -162724.966 | -30.53%
Sackett Lake | NY | SOL-10910 | 478398 | 0 | 478398 |  | 579238.653 | -100840.653 | -17.41%
Burritt Road | NY | SOL-10913 | 459020 | 0 | 459020 |  | 483306.4 | -24286.4 | -5.025%
Villa Roma 1 | NY | SOL-10914 | 426899 | 0 | 426899 |  | 468907.482 | -42008.482 | -8.959%
Villa Roma 2 | NY | SOL-10915 | 385632 | 0 | 385632 |  | 455116.086 | -69484.086 | -15.27%
Washington 1 | NY | SOL-10912 | 454660 | 0 | 454660 |  | 469498.541 | -14838.541 | -3.161%
Washington 3 | NY | SOL-10828 | 2434 | 0 | 2434 |  | 574073.776 | -571639.776 | -99.58%
Washington 4 | NY | SOL-10829 | 554940 | 0 | 554940 |  | 575388.883 | -20448.883 | -3.554%
Big Tree | NY | SOL-10966 | 462460 | 459520 | 2940 | 0.6398% | 474233.95 | -11773.95 | -2.483%
Canoga | NY | SOL-10965 | 1247750 | 0 | 1247750 |  | 668275.9 | -134435.9 | -20.12%
County Route 84 | NY | SOL-10967 | 1277190 | 1257760 | 19430 | 1.545% | 1412112.67 | -134922.67 | -9.555%
Donati | NY | SOL-10968 | 480270 | 456170 | 24100 | 5.283% | 517239.998 | -36969.998 | -7.148%
Henrietta | NY | SOL-10972 | 941410 | 924330 | 17080 | 1.848% | 999850.998 | -58440.998 | -5.845%
NY 70 | NY | SOL-10970 | 936670 | 927120 | 9550 | 1.03% | 1329578.42 | -392908.42 | -29.55%
Reid | NY | SOL-10991 | 953443.0842 | 1131792.7 | -178349.6158 | -15.76% | 1108328 | -154884.9158 | -13.97%
Sangolqui | NY | SOL-10975 | 399530 | 268850 | 130680 | 48.61% | 499990.958 | -100460.958 | -20.09%
State Highway 17B | NY | SOL-10988 | 1100370 | 1083350 | 17020 | 1.571% | 1303357.07 | -202987.07 | -15.57%
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 1407225.927 | -1407225.927 | -100%
West Creek | NY | SOL-10995 | 1340990 | 1299190 | 41800 | 3.217% | 1301047.827 | 39942.173 | 3.07%
Wildflower | NY | SOL-10982 | 1126776 | 734468 | 392308 | 53.41% | 1463041.03 | -336265.03 | -22.98%
Glen Mary 1 | NY | SOL-10993 | 1058590 | 1015980 | 42610 | 4.194% | 1520207.398 | -461617.398 | -30.37%
Glen Mary 2 | NY | SOL-10994 | 612750 | 0 | 612750 |  | 632509.009 | -19759.009 | -3.124%
Telegraph 1 | NY | SOL-11003 | 861880 | 0 | 861880 |  | 973707.107 | -111827.107 | -11.48%
Telegraph 2 | NY | SOL-11004 | 461210 | 0 | 461210 |  | 504067.204 | -42857.204 | -8.502%
Cafferty Hill | NY | SOL-10996 | 1368240 | 1383581.92 | -15341.92 | -1.109% | 1345180.438 | 23059.562 | 1.714%
Dunkleman | NY | SOL-11008 | 1264220 | 472440 | 791780 | 167.6% | 1389969.544 | -125749.544 | -9.047%
Route 19 1 | NY | SOL-11001 | 301906.7 | 295948.77 | 5957.93 | 2.013% | 517579.866 | -215673.166 | -41.67%
Route 19 2 | NY | SOL-11002 | 1245620 | 1231680 | 13940 | 1.132% | 1343997.344 | -98377.344 | -7.32%
Yellow Mills 1 | NY | SOL-11006 | 479160 | 471947 | 7213 | 1.528% | 490877.722 | -11717.722 | -2.387%
Yellow Mills 2 | NY | SOL-11005 | 386302 | 0 | 386302 |  | 506644.793 | -120342.793 | -23.75%
Yellow Mills 3 | NY | SOL-11007 | 451932 | 445042 | 6890 | 1.548% | 473304.952 | -21372.952 | -4.516%
Catskill | NY | SOL-11021 | 855467 | 0 | 855467 |  | 1031835.205 | -176368.205 | -17.09%
Eddy Ridge | NY | SOL-11054 | 483703 | 476726 | 6977 | 1.464% | 623253.075 | -139550.075 | -22.39%
Ridgeway #1 | NY | SOL-11018 | 1357079 | 1331833 | 25246 | 1.896% | 1385831.83 | -28752.83 | -2.075%
Rivard 1 | NY | SOL-11011 | 988227.0249 | 1064018 | -75790.9751 | -7.123% | 996721.7 | -8494.6751 | -0.8523%
Rivard 2 | NY | SOL-11012 | 951402 | 941387.4 | 10014.6 | 1.064% | 948414.5 | 2987.5 | 0.315%
Ridgeway #2 | NY | SOL-11027 | 677972 | 668279 | 9693 | 1.45% | 715752.69 | -37780.69 | -5.278%
Spencer | NY | SOL-11017 | 1374662.33 | 1340136.54 | 34525.79 | 2.576% | 1418870 | -44207.67 | -3.116%
Reisender | NY | SOL-10886 | 425380 | 424830 | 550 | 0.1295% | 548928.017 | -123548.017 | -22.51%
Finney | NY | SOL-10999 | 1211940 | 1205130 | 6810 | 0.5651% | 1363859.842 | -151919.842 | -11.14%
Davis Solar | NY | SOL-10958 | 553268 | 706339.2 | -153071.2 | -21.67% | 641872 | -88604 | -13.8%
Genesee | NY | SOL-10951 | 564337.6 | 548817.13 | 15520.47 | 2.828% | 866677.181 | -302339.581 | -34.88%
Landau I | NY | SOL-10891 | 479840 | 0 | 479840 |  | 634618.939 | -154778.939 | -24.39%
Landau II | NY | SOL-10895 | 1008960 | 0 | 1008960 |  | 0 | 0
New Beginnings | NY | SOL-10890 | 340190 | 340150 | 40 | 0.01176% | 655880.494 | -315690.494 | -48.13%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 1081646 | 1299932.3 | -218286.3 | -16.79% | 1174757 | -93111 | -7.926%
Brodhead Solar, LLC | NY | SOL-10899 | 644960 | 725678.2 | -80718.2 | -11.12% | 699224 | -54264 | -7.761%
Svenski | NY | SOL-10894 | 505176 | 0 | 505176 |  | 586060.626 | -80884.626 | -13.8%
Bantam | NY | SOL-10986 | 295990 | 842130 | -546140 | -64.85% | 1247685.567 | -951695.567 | -76.28%
Bogart | NY | SOL-10887 | 542690 | 467220 | 75470 | 16.15% | 599793.258 | -57103.258 | -9.52%
Dubois | NY | SOL-10892 | 480 | 384.5 | 95.5 | 24.84% | 0 | 480
Salt Point | NY | SOL-10888 | 529000 | 521040 | 7960 | 1.528% | 551403.406 | -22403.406 | -4.063%
Wheatland 2A | NY | SOL-10971 | 1024170 | 1018450 | 5720 | 0.5616% | 1034946.536 | -10776.536 | -1.041%
Wheatland 2B | NY | SOL-10961 | 1066340 | 686950 | 379390 | 55.23% | 1021100.66 | 45239.34 | 4.43%
Brickchurch | NY | SOL-10889 | 163740 | 166080 | -2340 | -1.409% | 416394.613 | -252654.613 | -60.68%
McCarthy Solar | NY | SOL-10992 | 265270 | 0 | 265270 |  | 650763.23 | -385493.23 | -59.24%
Costanza | NY | SOL-10907 | 526200 | 526347.45 | -147.45 | -0.02801% | 577147.248 | -50947.248 | -8.827%
Lockenhurst Pond | NY | SOL-11000 | 622811 | 692439.3 | -69628.3 | -10.06% | 602904 | 19907 | 3.302%
Drinkwater | NY | SOL-10896 | 553350 | 548100 | 5250 | 0.9579% | 565021.45 | -11671.45 | -2.066%
Altamont | NY | SOL-11085 | 963889 | 1114409.6 | -150520.6 | -13.51% | 1029478.6 | -65589.6 | -6.371%
Krumkill North | NY | SOL-11086 | 911007 | 1191666.9 | -280659.9 | -23.55% | 1334110.4 | -423103.4 | -31.71%
Krumkill South | NY | SOL-11087 | 792690 | 1049689.4 | -256999.4 | -24.48% | 1045901.9 | -253211.9 | -24.21%
X092 | NY | SOL-11189 | 24619.4 | 26693.595 | -2074.195 | -7.77% | 27617 | -2997.6 | -10.85%
X093 | NY | SOL-10932 | 18447.8594 | 19515.56 | -1067.7006 | -5.471% | 18561 | -113.1406 | -0.6096%
X095 | NY | SOL-10929 | 24292.875 | 33327.034 | -9034.159 | -27.11% | 25863 | -1570.125 | -6.071%
X181 | NY | SOL-10428 | 46280.5781 | 47638.72 | -1358.1419 | -2.851% | 44674 | 1606.5781 | 3.596%
X415 | NY | SOL-10429 | 28462.7188 | 26389.948 | 2072.7708 | 7.854% | 24406 | 4056.7188 | 16.62%
K198 | NY | SOL-10930 | 21777.0156 | 24288.602 | -2511.5864 | -10.34% | 22559 | -781.9844 | -3.466%
K203 | NY | SOL-11190 | 27781.6 | 26590.465 | 1191.135 | 4.48% | 31668 | -3886.4 | -12.27%
K213 | NY | SOL-11191 | 30273.5 | 36779.389 | -6505.889 | -17.69% | 32790 | -2516.5 | -7.675%
K217 | NY | SOL-10933 | 14479.0469 | 18544.791 | -4065.7441 | -21.92% | 15057 | -577.9531 | -3.838%
K307 | NY | SOL-10876 | 34789.4688 | 54059.03 | -19269.5612 | -35.65% | 30011 | 4778.4688 | 15.92%
K610 | NY | SOL-11158 | 40734.9 | 43876.22 | -3141.32 | -7.16% | 42680 | -1945.1 | -4.557%
M025 | NY | SOL-10392 | 30365.3359 | 45234.99 | -14869.6541 | -32.87% | 37937 | -7571.6641 | -19.96%
M028 | NY | SOL-10381 | 27850.9844 | 29028.198 | -1177.2136 | -4.055% | 26016 | 1834.9844 | 7.053%
Q030 | NY | SOL-10878 | 30954.5781 | 33690.588 | -2736.0099 | -8.121% | 33004 | -2049.4219 | -6.21%
Q130 | NY | SOL-10877 | 17369.3047 | 22014.565 | -4645.2603 | -21.1% | 17250.41 | 118.8947 | 0.6892%
Q196 | NY | SOL-10879 | 23024.9844 | 27634.306 | -4609.3216 | -16.68% | 22889 | 135.9844 | 0.5941%
Q220 | NY | SOL-10873 | 23834.1875 | 36867.977 | -13033.7895 | -35.35% | 24075 | -240.8125 | -1%
Q205 | NY | SOL-10922 | 35893.4844 | 47360.85 | -11467.3656 | -24.21% | 33411 | 2482.4844 | 7.43%
Q400 | NY | SOL-10871 | 38812.7163 | 0 | 38812.7163 |  | 49713 | -10900.2837 | -21.93%
R003 | NY | SOL-10416 | 53767.4255 | 54107.48 | -340.0545 | -0.6285% | 50589 | 3178.4255 | 6.283%
R007 | NY | SOL-10417 | 56652.4375 | 63064.46 | -6412.0225 | -10.17% | 73163.08 | -16510.6425 | -22.57%
BK16 | NY | SOL-11093 | 54566.6562 | 59469.21 | -4902.5538 | -8.244% | 53468 | 1098.6562 | 2.055%
Trenton - Trenton East | IL | SOL-11060 | 807644 | 796972.9 | 10671.1 | 1.339% | 730871 | 76773 | 10.5%
Trenton - Trenton West | IL | SOL-11061 | 716449 | 650634.3 | 65814.7 | 10.12% | 746633 | -30184 | -4.043%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 694110 | 699975.4 | -5865.4 | -0.8379% | 677400 | 16710 | 2.467%
X018 | NY | SOL-10418 | 26419.8125 | 28002.667 | -1582.8545 | -5.653% | 29610 | -3190.1875 | -10.77%
Janiak Solar | NY | SOL-10898 | 620339.6439 | 686437 | -66097.3561 | -9.629% | 647730 | -27390.3561 | -4.229%
County Route 11B | NY | SOL-10983 | 1242192.25 | 1224916.18 | 17276.07 | 1.41% | 0 | 0
Barone | NY | SOL-11034 | 903777 | 892862 | 10915 | 1.222% | 952215 | -48438 | -5.087%
Cedarville | IL | SOL-11069 | 558109 | 589449.8 | -31340.8 | -5.317% | 643715 | -85606 | -13.3%
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | 0 | 0
O'Brien Hill #2 | NY | SOL-11099 | 1123349 | 1123031 | 318 | 0.02832% | 0 | 0
Trinity - Freeport | IL | SOL-11057 | 656376 | 706386.9 | -50010.9 | -7.08% | 646272 | 10104 | 1.563%
Ransom | NY | SOL-11157 | 1207756 | 1193768 | 13988 | 1.172% | 0 | 0
Horseheads - Wedge | NY | SOL-11160 | 740804 | 728941 | 11863 | 1.627% | 0 | 0
Otisville - Shoddy Hollow | NY | SOL-11185 | 1461198 | 1411847 | 49351 | 3.495% | 0 | 0
Wellsville - Chenunda Creek | NY | SOL-11187 | 615877 | 604699 | 11178 | 1.849% | 0 | 0
DC: Washington - Essex Condominium | DC | SOL-10036 | 5711 | 7551.801 | -1840.801 | -24.38% | 7877 | -2166 | -27.5%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 17214.029 | 27238.068 | -10024.039 | -36.8% | 30859.954 | -13645.925 | -44.22%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 30881 | 24718.141 | 6162.859 | 24.93% | 30843.44 | 37.56 | 0.1218%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 389490 | 567995.09 | -178505.09 | -31.43% | 734425.7 | -344935.7 | -46.97%
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 1555219.7765 | 1629304.5 | -74084.7235 | -4.547% | 1785200 | -229980.2235 | -12.88%
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 716010 | 0 | 716010 |  | 712321.2 | 3688.8 | 0.5179%
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 844705.5992 | 1402067.9 | -557362.3008 | -39.75% | 1487707 | -643001.4008 | -43.22%
NY: Whitesville - Independence North | NY | SOL-11186 | 988640 | 0 | 988640 |  | 0 | 0
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 712474 | 757794.9 | -45320.9 | -5.981% | 753184 | -40710 | -5.405%
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 734767 | 955373.9 | -220606.9 | -23.09% | 706289 | 28478 | 4.032%
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 636487 | 1171509.3 | -535022.3 | -45.67% | 604106 | 32381 | 5.36%
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 714603 | 824791.6 | -110188.6 | -13.36% | 629174.5 | 85428.5 | 13.58%
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 36872512.6 | 0 | 36872512.6 |  | 0 | 0
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 999568 | 0 | 999568 |  | 1085696.5 | -86128.5 | -7.933%
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 94776.515 | 121981.2 | -27204.685 | -22.3% | 178632.9 | -83856.385 | -46.94%

## Jan
Generate Capital |  |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  |  | 8302287.9 | 4150358.011 | 4151929.889 | 100% | 10397497.791 | -2095209.891 | -20.15% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 11980.125 | 18586.79 | -6606.665 | -35.54% | 11111.47 | 868.655 | 7.818%
K041 | NY | SOL-10357 | 8842.5469 | 13490.72 | -4648.1731 | -34.45% | 9924 | -1081.4531 | -10.9%
K043 | NY | SOL-10358 | 10563.6875 | 15508.68 | -4944.9925 | -31.89% | 2303 | 8260.6875 | 358.7% | 1.Estimated values are low in AE we have also verified the file which was given GC
K058 | NY | SOL-10360 | 8472.1875 | 12896.51 | -4424.3225 | -34.31% | 9147.029 | -674.8415 | -7.378%
K115 | NY | SOL-10361 | 2497.5194 | 7565.845 | -5068.3256 | -66.99% | 5593.833 | -3096.3136 | -55.35% | 1. 96 optimizers are down for site construction. | 1.SR093291
K152 | NY | SOL-10362 | 3001 | 4499.147 | -1498.147 | -33.3% | 3567 | -566 | -15.87% | 1. Low generation due to weather/snow.
K166 | NY | SOL-10363 | 10743.5 | 17382.57 | -6639.07 | -38.19% | 12125.14 | -1381.64 | -11.39% | 1. Low generation due to weather/snow.
K206 | NY | SOL-10927 | 7155.1976 | 11256.59 | -4101.3924 | -36.44% | 6894 | 261.1976 | 3.789%
K251 | NY | SOL-10365 | 7964.375 | 0 | 7964.375 |  | 8525.692 | -561.317 | -6.584% | 1.Weather station is not communicating since 11/22/2024. | 1.SR093633
K269 | NY | SOL-10366 | 6631 | 11493.23 | -4862.23 | -42.31% | 7761.932 | -1130.932 | -14.57%
K273 | NY | SOL-10367 | 6884.75 | 0 | 6884.75 |  | 9546 | -2661.25 | -27.88% | 1. Weather station is not communicating since 06/30/2024. 2. 26 optimizers are down for roof repair. | 1.SR086842 2.SR093294 | SR093294
K287 | NY | SOL-10919 | 6469.9062 | 8103.888 | -1633.9817 | -20.16% | 7303 | -833.0938 | -11.41%
K298 | NY | SOL-10368 | 4878.3438 | 10470.4 | -5592.0562 | -53.41% | 6119 | -1240.6562 | -20.28% | 1. Low generation due to weather/snow.
K335 | NY | SOL-10370 | 6585.9375 | 11111.72 | -4525.7825 | -40.73% | 8179 | -1593.0625 | -19.48%
K345 | NY | SOL-10920 | 7617.6813 | 8115.26 | -497.5787 | -6.131% | 6910 | 707.6813 | 10.24%
K445 | NY | SOL-10373 | 7247.9688 | 11595.77 | -4347.8013 | -37.49% | 6816.675 | 431.2937 | 6.327%
K495 | NY | SOL-10374 | 0 | 32841.14 | -32841.14 | -100% | 33557 | -33557 | -100% | 1.Due to shunt trips of the switchgear and overcurrent faults site is offline since 11/20/2024. | 1.SR093196
M020 | NY | SOL-10380 | 7114.6562 | 10428.83 | -3314.1737 | -31.78% | 9125 | -2010.3438 | -22.03% | 1. Low generation due to weather/snow.
M092 | NY | SOL-10383 | 7110.6875 | 11229.76 | -4119.0725 | -36.68% | 8178.46 | -1067.7725 | -13.06% | 1. Low generation due to weather/snow.
M143 | NY | SOL-10384 | 7303.2812 | 10937.18 | -3633.8988 | -33.23% | 8702.744 | -1399.4628 | -16.08% | 1. Low generation due to weather/snow.
M144 | NY | SOL-10385 | 12171.125 | 0 | 12171.125 |  | 13644 | -1472.875 | -10.8% | 1. Low generation due to weather/snow.
M167 | NY | SOL-10386 | 6736.5 | 8426.056 | -1689.556 | -20.05% | 8106.211 | -1369.711 | -16.9% | 1. Low generation due to weather/snow.
M188 | NY | SOL-10387 | 6676.8125 | 0 | 6676.8125 |  | 6981 | -304.1875 | -4.357%
EMHC | NY | SOL-10351 | 1958.0469 | 2171.019 | -212.9721 | -9.81% | 2319.395 | -361.3481 | -15.58%
Q008 | NY | SOL-10397 | 11304.4688 | 16377.23 | -5072.7612 | -30.97% | 10992 | 312.4688 | 2.843% | 1. Low generation due to weather/snow.
Q018 | NY | SOL-10398 | 6700.6875 | 8361.302 | -1660.6145 | -19.86% | 6682.311 | 18.3765 | 0.275% | 1. Low generation due to weather/snow.
Q021 | NY | SOL-10399 | 5780.4062 | 9454.255 | -3673.8487 | -38.86% | 5223.647 | 556.7593 | 10.66% | 1. Low generation due to weather/snow.
Q025 | NY | SOL-10400 | 9494.875 | 13415.23 | -3920.355 | -29.22% | 7767 | 1727.875 | 22.25% | 1. Low generation due to weather/snow.
Q074 | NY | SOL-10402 | 5694.625 | 7433.287 | -1738.662 | -23.39% | 6035.102 | -340.477 | -5.642% | 1. Site was taken offline from 12/31/24 due to ConEd shut site off for tranformer work and later back online on 01/02 at 09:30 | 1. SR095201
Q115 | NY | SOL-10872 | 7869.5625 | 12376.31 | -4506.7475 | -36.41% | 8154.507 | -284.9445 | -3.494%
Q139 | NY | SOL-10403 | 5074.7187 | 6806.319 | -1731.6003 | -25.44% | 5168 | -93.2813 | -1.805%
Q157 | NY | SOL-10404 | 7985.125 | 13511.83 | -5526.705 | -40.9% | 9200.271 | -1215.146 | -13.21% | 1.Inverter 3 offline mulptiple days due to parts RMAD 2.Inverter 4 is offline due to "Isolation Fault" from 01/3 | 1. SR094206 2. SR096202 | SR096202
Q192 | NY | SOL-10406 | 13490.125 | 19580.54 | -6090.415 | -31.1% | 13910.41 | -420.285 | -3.021%
Q210 | NY | SOL-10407 | 11766.375 | 14293.21 | -2526.835 | -17.68% | 11622 | 144.375 | 1.242%
Q229 | NY | SOL-10408 | 4152.5312 | 7352.509 | -3199.9778 | -43.52% | 3687.114 | 465.4172 | 12.62%
Q231 | NY | SOL-10870 | 17624.25 | 30638.85 | -13014.6 | -42.48% | 16899 | 725.25 | 4.292%
Q405 | NY | SOL-10409 | 21223.625 | 28842.48 | -7618.855 | -26.42% | 20777.84 | 445.785 | 2.145%
Q435 | NY | SOL-10923 | 27409.75 | 28681.61 | -1271.86 | -4.434% | 25692 | 1717.75 | 6.686%
Q485 | NY | SOL-10869 | 25454.25 | 27297.56 | -1843.31 | -6.753% | 23827.9 | 1626.35 | 6.825% | 1. Inverter 1 right unit is offline due to DC disconnect switches turned to OFF positions since 01/21 at 07:00am and back online on 01/31 | 1. SR096130
Q490 | NY | SOL-10411 | 17658.5578 | 0 | 17658.5578 |  | 16846.57 | 811.9878 | 4.82% | 1. optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline | 1. SR093326
Q620 | NY | SOL-10867 | 26364.625 | 35204.15 | -8839.525 | -25.11% | 27281.47 | -916.845 | -3.361%
QMOA | NY | SOL-10415 | 2696.5 | 0 | 2696.5 |  | 2932.063 | -235.563 | -8.034%
X024 | NY | SOL-10419 | 7807.0938 | 15291.95 | -7484.8563 | -48.95% | 8671 | -863.9062 | -9.963%
X026 | NY | SOL-10420 | 6588.3 | 11626.77 | -5038.47 | -43.34% | 11127.49 | -4539.19 | -40.79% | 1. Inverter 2 left unit at 10:30 from 01/16 and has been RMA'd. | 1. SR095758
X090 | NY | SOL-10925 | 7675.0938 | 6852.322 | 822.7717 | 12.01% | 7353 | 322.0938 | 4.38%
X117 | NY | SOL-10422 | 5524.7 | 9713.037 | -4188.337 | -43.12% | 6534.025 | -1009.325 | -15.45% | 1. Low generation due to weather/snow.
X125 | NY | SOL-10423 | 12077.875 | 16953.08 | -4875.205 | -28.76% | 11985.79 | 92.085 | 0.7683% | 1. Low generation due to weather/snow.
X134 | NY | SOL-10424 | 10465.1562 | 0 | 10465.1562 |  | 10182 | 283.1562 | 2.781%
X135 | NY | SOL-10425 | 9755.1875 | 14564.38 | -4809.1925 | -33.02% | 9790 | -34.8125 | -0.3556% | 1. Low generation due to weather/snow.
X139 JHS 222 | NY | SOL-10426 | 12809.0209 | 16768.06 | -3959.0391 | -23.61% | 12346 | 463.0209 | 3.75% | 1. Low generation due to weather/snow.
X140 | NY | SOL-10926 | 8890.625 | 8929.914 | -39.289 | -0.44% | 8234 | 656.625 | 7.975%
X166 | NY | SOL-10427 | 8246.6 | 13090.03 | -4843.43 | -37% | 7246 | 1000.6 | 13.81% | 1. Low generation due to weather/snow.
Murphy | MN | SOL-10094 | 512400 | 650404.3 | -138004.3 | -21.22% | 514855.4 | -2455.4 | -0.4769% | 1. Inverter 5 is derating by 353 kW since 01/03 due to a loose electrical connections. Additionally, one combiner may be open, or the DC contactor in the DU cabinet may not be closed and resumed production on 01/29. 2. Inverter 4/Meter 4 was derating by 640 kW on 01/19 due to a possible DC breaker trip and returned to normal production on 01/20. 3. Inverter 1 was derating by 444 kW from 9:30 to 12:00 on 01/23 and back to normal production on 01/29. | 1. SR095297, SR092042, SR095706,SR095899 2. SR095707 3. SR095899 | SR092042 | SR095706 | SR095899 | SR095707 | SR095899
Terning | MN | SOL-10093 | 526233 | 640284.3 | -114051.3 | -17.81% | 466507.1 | 59725.9 | 12.8% | 1. Low generation due to weather/snow.
Boas Road 04 | NY | SOL-10908 | 139690 | 195502.947 | -55812.947 | -28.55% | 155064.5 | -15374.5 | -9.915% | 1. Low generation due to weather/snow.
Kelly Bridge Farm | NY | SOL-10911 | 105630 | 192097.428 | -86467.428 | -45.01% | 144336.8 | -38706.8 | -26.82% | 1. Inverter 23 tripped offline at 9:30 AM on 11/15 due to a blown fuse and back online at 11:05 AM on 01/16. 2. Inverter 24 tripped offline at 12:40 on 01/08 due to blown fuse and back online at 11:05 on 01/16. 3. Inverter 30 tripped offline at 11:00AM on 01/10 and offline throughout the month due to thermal event. Inverter powerhead and dc combiner box have been RMA'd. 4. Inverter 4 tripped offline due to blown fuse at 12:25 on 01/30 and offline throughout the month. | 1. SR093285, SR093470 2. SR095395 3. SR095473 4. SR096164 | SR093470 | SR095395 | SR095473 | SR096164
Pool Brook Road | NY | SOL-10909 | 55489 | 160091.752 | -104602.752 | -65.34% | 143824.5 | -88335.5 | -61.42% | 1. Low generation due to weather/snow.
Sackett Lake | NY | SOL-10910 | 132347 | 200740.754 | -68393.754 | -34.07% | 168308.5 | -35961.5 | -21.37% | 1.Inverter 1 tripped offline from 06:50AM to 12:30 on 01/09 and again tripped offline from 8:40AM to 11:55 AM on 01/11 due to a "failing breaker". | 1. SR095433
Burritt Road | NY | SOL-10913 | 72290 | 0 | 72290 |  | 111972.4 | -39682.4 | -35.44% | 1.POA Pyranometer is not communicating from 07:00AM on 11/09 and throughout the month due to a malfunctioning NPort, where the POA and GHI are connected. | 1. SR093972
Villa Roma 1 | NY | SOL-10914 | 75089 | 234497.346 | -159408.346 | -67.98% | 119197 | -44108 | -37% | 1. Inverter 2 is offline since 01/23 due to a damaged "tbusd" board, which is being RMA'd and inverter 1 was offline on 01/23 from 08:15am to 01:25pm due to DC Contactor fault and the technician powercycled the inverter 2.Inverter 1 tripped offline on 01/25 at 13:15 due to an 'IAC overcurrent' fault and was back online on 01/26. According to the technician, both the fuses and the capacitor bank were in working order and within range. Inverter 1 tripped offline again on 01/29 at 14:40, came back online on 01/30 at 07:00, and tripped offline once more on 01/30 at 09:00. The technician swapped the CCU board between Inverters 1 and 2, and Inverter 1 was back online at 14:40 on 01/30. 3. CB 4 string 4 is offline from 01/01 due to blown fuse a technician replaced fuse on 01/21 on both string 4and string 11. | 1. SR095885, SR095919 2. SR095976, SR096119 3. SR095645 | SR095919 | SR095976 | SR096119 | SR095645
Villa Roma 2 | NY | SOL-10915 | 94660 | 158029.455 | -63369.455 | -40.1% | 116241.7 | -21581.7 | -18.57% | 1. Technician swapped the fiber optic cable, restoring Inverter 2 online at 12:15 on 1/7. | 1. SR095176
Washington 1 | NY | SOL-10912 | 106440 | 159121.526 | -52681.526 | -33.11% | 107375.8 | -935.8 | -0.8715% | 1. Inverter 1 was offline on 1/10 due to a Fault DC Contactor. Ingecon remotely restarted it, restoring operation at 4:00 PM on 1/10. | 1. SR095483
Washington 3 | NY | SOL-10828 | 126003 | 96875.183 | 29127.817 | 30.07% | 132253.8 | -6250.8 | -4.726% | 1. POA sensor continues to read inaccurately. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. 2. Inverter 2 had delayed startup on 01/09, 01/19, and was offline all day on 01/21 due to an AC Contactor fault. Technician followed Ingeteam's instructions, removed grounding and bonding fuse, switched to a floating system, and swapped the K2 relay with Inverter 1. Inverter back online on 01/23. | 1. SR093024 2. SR095445 | SR095445
Washington 4 | NY | SOL-10829 | 91589 | 0 | 91589 |  | 132064.4 | -40475.4 | -30.65% | 1. Low generation due to weather/snow.
Big Tree | NY | SOL-10966 | 23918 | 0 | 23918 |  | 116825.9 | -92907.9 | -79.53% | 1. Low generation due to weather/snow.
Canoga | NY | SOL-10965 | 314990 | 0 | 314990 |  |  |  |  | 1. Weather station has reported 0 since 8/21. New UP POA and Down POA need replacement. Gen Cap advised holding off dispatch. 2. Combiner box 19 had minimal production since 10/29. Technician found it locked/tagged, removed the lock, tested voltage, fuses, and ground faults—all tested good. Combiner box 19 back in production on 01/29. 3. Inverter 3 tripped offline at 12:10 on 01/26 due to IAC out of range. Technician found thermal damage and blown fuses. Parts have been RMA'd. 4. Inverter 4 tripped offline at 12:00 on 01/27 due to IAC out of range. Technician replaced a blown fuse on the middle phase, cap bank tested good. Inverter back online at 1:20 on 01/29. 5. Combiner boxe 3 offline due to thermal damage and fuse blown and combiner boxes 21-37,26,30 and 33 required new CT's from 01/29. | 1. SR094278 2. SR095604 3. SR095991 4. SR096045 5. SR095991 | SR095604 | SR095991 | SR096045 | SR095991
County Route 84 | NY | SOL-10967 | 423990 | 0 | 423990 |  | 472285.7 | -48295.7 |  | 1. Site tripped offline at 16:00 on 01/29 due to utility outage and back online at 20:55 on 01/29. | 1. SR096126
Donati | NY | SOL-10968 | 127357 | 0 | 127357 |  | 156570.4 | -29213.4 | -18.66% | 1. Weather station Reporting 0 value from 05/31. POA sensors need to be replaced. Quote provided to Gen Cap for approval. 2. Trackers A01, A05, A06, A07, A10, B17, D20, F19, F21, F22, F32, F33, and G14 are stuck since different dates, totaling 13. Gen Cap advised holding off dispatch. | 1. SR092964 2. SR095253 | SR095253
Henrietta | NY | SOL-10972 | 200110 | 0 | 200110 |  | 268925.4 | -68815.4 | -25.59% | 1.Low generation due to weather/snow.
NY 70 | NY | SOL-10970 | 284620 | 0 | 284620 |  | 386450 | -101830 | -26.35% | 1.Inverters 2,3,4 are offline at 11:30 on 01/06 while technician on site to troubleshoot combiner boxes. In addition Combiner Boxes 35-46 are offline from 01/02 and back online on 01/14. | 1.SR095252
Reid | NY | SOL-10991 | 165884.9893 | 348144.2 | -182259.2107 | -52.35% | 265223 | -99338.0107 | -37.45% | 1. Inverter 23 was offline since 11/29 reporting Grid Phase Voltage Out of Range. Gen Cap advised holding off dispatch. | 1. SR093436
Sangolqui | NY | SOL-10975 | 129267 | 0 | 129267 |  | 151974.9 | -22707.9 | -14.94% | 1. Inverter 1 started late for the production due to Isolation resistance value of limits and later self resolved at 11:25 on 01/29. | 1. SR096100
State Highway 17B | NY | SOL-10988 | 242020 | 0 | 242020 |  | 384984 | -142964 | -37.14% | 1. Site tripped offline at 13:50PM on 01/07/25 and came back online after a brief outage at 20:00 on same day. 2. Inverter 4 has been offline since 11/13/24 and reporting Fault elect. supply. On 01/29/25, the technician installed stacks, partially checked ground faults, and found the connecting plates were missing. Re-energizing occurred, as thermal events were observed during this step and inverter still offline. | 1. SR095376 2. SR093375 | SR093375
State Route 14A | NY | SOL-10997 | 331004 | 0 | 331004 |  | 427147.4 | -96143.4 | -22.51% | 1.Inverter 2 tripped offline at 9:40 AM on 01/14/25 due to an SE INTERNAL TEMP UNBALANCED (253) fault and came back online at 2:50 PM the same day. On 01/15/25, the technician performed a fan test. After restarting, Inverter 2 showed a Phase S blower message. Fans S & R were swapped, but the fault followed the fan. Ingeteam issued an RMA to ship a new fan. On 01/20/25, the inverter again tripped offline at 12:05 PM and remained offline. On 01/27/25, the technician replaced the RMA fan "S," and it was brought back online at 12:45 PM. | 1. SR095549
West Creek | NY | SOL-10995 | 376140 | 0 | 376140 |  | 397925.5 | -21785.5 | -5.475%
Wildflower | NY | SOL-10982 | 324291.4 | 0 | 324291.4 |  | 433603.2 | -109311.8 | -25.21% | 1. Inverters 1 and 2 tripped offline at 13:40 on 01/07/25 and came back online on 01/08. Inverter 1 tripped again at 12:20 on 01/11 due to an Iac out-of-range fault. Inverter 2 experienced multiple trips due to an isolation resistance value out-of-limits fault. On 01/12/25, the technician brought both inverters back online at 13:40 after replacing the connection with a new wire (same labeling) and a new fuse from stock. 2. Inverter 3 tripped offline at 10:40 AM on 01/22/25 due to an AC Protection fault. Inverter 4 experienced multiple trips due to a hardware error. On 01/23/25, the technician brought Inverter 3 back online at 15:05 after closing the Q4 breaker, finding the D134 LED illuminated but no other errors. Further instructions from Ingeteam are needed for part replacement. On 01/24/25, the technician tested the capacitor banks of Inverters 3 and 4 as per Ingeteam's instructions. Inverter 3's capacitor bank was RMA'd. 3. Inverter 2 tripped offline at 12:05 and back online at 13:00 on 01/28/25 due to an Insulation fault. | 1. SR095496 2. SR095852 3. SR096056 | SR095852 | SR096056
Glen Mary 1 | NY | SOL-10993 | 396140 | 0 | 396140 |  | 420494.8 | -24354.8 | -5.792%
Glen Mary 2 | NY | SOL-10994 | 63710 | 0 | 63710 |  | 171573.9 | -107863.9 | -62.87% | 1.Inverter 1 tripped offline at 14:15 on 01/16/25 due to a ground fault. On 01/17/25, the technician identified the fault on CB 13, turned it off, and restarted the inverter. On 01/18/25, condensation was found on CB 19 and voltage issues on string 9, so CB 19 was left offline. The GFDI fault returned after restarting. On 01/21/25, the technician found a hard positive ground fault on the negative busbar, but could not replicate the fault after checking all CBs. Inverter 1 has been RMA'd. | 1. SR095635
Telegraph 1 | NY | SOL-11003 | 136202 | 0 | 136202 |  | 286022.2 | -149820.2 | -52.38% | 1. Site was tripped offline on 01/07/25 at 13:15 due to utility outage and power was restored at 14:25 on same day. 2. Site was tripped offline on 01/22/25 at 11:30AM due to utility outage and power was restored at 17:25 on same day. 3. Site was tripped offline on 01/29/25 at 11:45AM due to utility outage and power was restored at 13:00 on same day. | 1. SR095374 2. SR095374 3. SR096112 | SR095374 | SR096112
Telegraph 2 | NY | SOL-11004 | 87233 | 0 | 87233 |  | 146627.1 | -59394.1 | -40.51% | 1. Site was tripped offline on 01/07/25 at 13:15 due to utility outage and power was restored at 14:25 on same day. 2. Site was tripped offline on 01/22/25 at 12:20 AM. On 01/23/25, the technician found the cradlepoint was not working and the SIM card was RMA'd. On 01/27/25 the technician pushed new firmware, power-cycled the cradlepoint site back online at 05:00 on 01/27 3. Site was tripped offline on 01/29/25 at 11:50AM due to utility outage and power was restored at 13:00 on same day. | 1. SR095375 2. SR095375 3. SR096113 | SR095375 | SR096113
Cafferty Hill | NY | SOL-10996 | 349660 | 0 | 349660 |  | 373143.4 | -23483.4 | -6.293% | 1. Inverter module 2.2 has been underproducing by 1000 kW since 01/22/25 compared to its peers due to a faulty PG board. On 01/24/25, the technician replaced the board and inverter resumed back to normal production. 2. Inverter 1 unit 2 is producing as expected after the technician replaced the PG board on 01/07/25. | 1. SR095917 2. SR094891 | SR094891
Dunkleman | NY | SOL-11008 | 142060 | 0 | 142060 |  | 369715.7 | -227655.7 | -61.58% | 1.Site tripped offline at 11:45 on 01/21 due to main breaker tripped open and back online at 10:15 on 01/22 after technician re-energised the site. 2. From 01/05, Inverter 1 trackers and multiple trackers(2.021, 2.027, 2.052, 2.059, 2.066, 2.114, 2.120, & 2.124) on Inverter 2 were stuck. Inverter 2 Trackers 2.011, 2.020, 2.027, 2.030, 2.032, 2.036, 2.039, 2.043, 2.050, 2.051, 2.052, 2.054, 2.056, 2.059, 2.060, 2.061, 2.064, 2.066, 2.068, 2.088, 2.095, 2.114, 2.119, 2.120, & 2.124 were stuck on 01/10. Technician restored Inverter 1 trackers on 01/13 and initiated the RMA process for 9 tracker control units. Modules are covered in ice/snow, and a low battery charging panel was dismounted and it will be reinstalled in better weather. | 1.SR095812 2.SR095109 | SR095109
Route 19 1 | NY | SOL-11001 | 100050 | 0 | 100050 |  | 154567.8 | -54517.8 | -35.27% | 1. Site tripped offline from 13:15PM to 14:45PM on 01/07 due to brief utility outage, again site tripped offline from 10:35 to 17:15 on 01/22 due to utility outage. | 1.SR095371
Route 19 2 | NY | SOL-11002 | 273860 | 0 | 273860 |  | 409574.6 | -135714.6 | -33.14% | 1.Site tripped offline from 13:15PM to 14:45PM on 01/07 due to brief utility outage, again site tripped offline from 10:35 to 17:15 on 01/22 due to utility outage. 2.Inverter 1 was offline on 01/31 and technician was unable to access the site due to heavy snowbank at the access road. | 1.SR095373 2.SR096177 | SR096177
Yellow Mills 1 | NY | SOL-11006 | 43612 | 0 | 43612 |  | 123508.6 | -79896.6 | -64.69% | 1. Inverter is barely producing since 01/15 and from 01/20 the inverter is offline due to bad PA1 board(PA1 board is being RMA'd) 2. Site was tripped offline on 01/12 at 18:00 due to utility outage and later power was restored at 19:55 on 01/12 | 1. SR096106, SR095599 2. SR095506 | SR095599 | SR095506
Yellow Mills 2 | NY | SOL-11005 | 133771 | 0 | 133771 |  | 126216.1 | 7554.9 | 5.986% | 1. Site was tripped offline on 01/12 at 17:50 due to utility outage and power was restored at 20:00 on 01/12 | 1. SR095508
Yellow Mills 3 | NY | SOL-11007 | 125120 | 0 | 125120 |  | 111400.8 | 13719.2 | 12.32% | 1. Site was tripped offline on 01/12 at 18:00 due to utility outage and later power was restored at 19:55 on 01/12 | 1. SR095507
Catskill | NY | SOL-11021 | 203760 | 0 | 203760 |  | 295119.3 | -91359.3 | -30.96% | 1. Site was tripped offline on 01/01 at 11:00am due to utility outage and later power was restored at 17:45 on 01/01 2.Site was tripped offline at 17:30 on 01/22 due to relay open and back online on 01/23 at 09:00am after technician closed in the relay. | 1. SR095211 2. SR095865 | SR095865
Eddy Ridge | NY | SOL-11054 | 142318.1 | 0 | 142318.1 |  | 176115 | -33796.9 | -19.19% | 1. Combiner box 1.05 is offline on 01/30 and later self resolved on 01/31. | 1. SR096147
Ridgeway #1 | NY | SOL-11018 | 278224 | 0 | 278224 |  | 426059 | -147835 | -34.7% | 1. Low generation due to weather/snow.
Rivard 1 | NY | SOL-11011 | 179839.5789 | 270917.4 | -91077.8211 | -33.62% | 258355.8 | -78516.2211 | -30.39% | 1. Low generation due to weather/snow.
Rivard 2 | NY | SOL-11012 | 181084.286 | 212124.1 | -31039.814 | -14.63% | 246477.3 | -65393.014 | -26.53% | 1. Tracker control 33 - 90, 129 - 136, 148 are not communicating & tracker 156 is stuck and production dropped (approxmately ) 25 KW down. | 1. SR095073
Ridgeway #2 | NY | SOL-11027 | 79273 | 0 | 79273 |  | 219945.2 | -140672.2 | -63.96% | 1.Site tripped offline from 11:40 to 14:10 on 01/23 due to technician checked in along with Sungrow representatives to collect data. 2.Site was offline at 16:30 on 01/23 and back online at 15:30 on 01/28 due to snowfall. | 1.SR095678 2.SR096054 | SR096054
Spencer | NY | SOL-11017 | 414005 | 0 | 414005 |  | 306010.6 | 107994.4 | 35.29% | 1.Trackers 138, 141, & 147 are stuck. GenC says to hold on dispatch | 1. SR095821
Reisender | NY | SOL-10886 | 103860 | 170531.493 | -66671.493 | -39.1% | 141381.5 | -37521.5 | -26.54% | 1. Low generation due to weather/snow.
Finney | NY | SOL-10999 | 454350 | 0 | 454350 |  | 423916.4 | 30433.6 | 7.179%
Davis Solar | NY | SOL-10958 | 113022 | 215455 | -102433 | -47.54% | 182746 | -69724 | -38.15% | 1.Inverter went offline from 15:46 to 15:55 briefly with AC Separating Point failure later attempted remote clear error and inverter back online | 1.SR095558
Genesee | NY | SOL-10951 | 195743 | 0 | 195743 |  | 223003.4 | -27260.4 | -12.22% | 1. Inverter 2 tripped offline at 10:00 on 01/02 and reporting "AC Breaker Switch Open and technician was re-energized inverter at 14:30 on 01/02. 2. Inverter 2 is underperforming its peer by approx 50% from 01/20. Possibly weather related, area is reporting 4 inches snow accumulation and inverter producing as expected from 01/26 | 1.SR095213 2.SR095794 | SR095794
Landau I | NY | SOL-10891 | 128600 | 0 | 128600 |  | 183280 | -54680 | -29.83% | 1. Low generation due to weather/snow.
Landau II | NY | SOL-10895 | 273640 | 0 | 273640 |  | 345100.3 | -71460.3 | -20.71% | 1.Inverter 2 offline due to insulation measurement event on 01/01 and the insulation fault eventually cleared inverter back online on 01/02 2. POA sensor is reporting 0 W/m2 from 11/25/24. Will investigate next time onsite | 1. SR094986 2. SR095304 | SR095304
New Beginnings | NY | SOL-10890 | 139570 | 236173.087 | -96603.087 | -40.9% | 183796 | -44226 | -24.06% | 1.Inverter tripped offline at 13:40 due to 9023 DC overcurrent fault with sporadic Amperage measurements and back online at 15:20 on 01/09 again tripped offline at 11:45 due to technician at site and back online at 16:00 on 01/28. | 1.SR095185
Bullitt Farm Solar, LLC | NY | SOL-10998 | 233704 | 370127.43 | -136423.43 | -36.86% | 381120.6 | -147416.6 | -38.68% | 1. Trackers 1, 4, 29, 35, 49, 56, 67, 68, 72, & 89 were stucked from 12/08 | 1.SR094262
Brodhead Solar, LLC | NY | SOL-10899 | 199162 | 235454.7 | -36292.7 | -15.41% | 225874.51 | -26712.51 | -11.83% | 1.NCU 1 tracker 25 was stuck at -59.67 on 01/16 and 28kw production was lost. 2.NCU 2 Tracker 1 was stuck at 60.48 from 11/18/24 and has a production loss of 9.5kw. | 1.SR095624 2.SR093637 | SR093637
Svenski | NY | SOL-10894 | 110333 | 0 | 110333 |  | 143761.4 | -33428.4 | -23.25% | 1. Low generation due to weather/snow.
Bantam | NY | SOL-10986 | 106590 | 0 | 106590 |  |  |  |  | 1.POA1 is not accurately reporting - technician need to visit for further troubleshooting | 1. SR096042
Bogart | NY | SOL-10887 | 163390 | 224512.078 | -61122.078 | -27.22% | 167525.6 | -4135.6 | -2.469% | 1. CBs 1.12 & 1.13 are underperforming from 01/27. | 1.SR096006
Dubois | NY | SOL-10892 | 121698.49 | 0 | 121698.49 |  |  |  |  | 1.Site was offline on 01/29 due to AC breaker open. Technician was able to close the AC breaker site back online at 13:00 on 01/30 | 1.SR096107
Salt Point | NY | SOL-10888 | 169980 | 0 | 169980 |  | 135218.2 | 34761.8 | 25.71% | 1. Inverter started late for production at 09:05am with fauli 24:HVDC on 01/03. Fault was cleared through powerSupervisor. | 1.SR095269
Wheatland 2A | NY | SOL-10971 | 294880 | 0 | 294880 |  | 282852.6 | 12027.4 | 4.252% | 1. 12 trackeers are stuck in different dates due to Several actuators adjusted from 01/06, need to contact slater to reset. Sent Slater an Email, 6 more trackers need TS | 1.SR094820
Wheatland 2B | NY | SOL-10961 | 283280 | 0 | 283280 |  | 279044.7 | 4235.3 | 1.518% | 1. 29 trackers are stuck on different dates from 01/06 due to actuators need replacement and the technician Requested update from Slater. Tech adjusted actuators, but Spc 2410 still needs troubleshooting from Nextracker | 1. SR095759
Brickchurch | NY | SOL-10889 | 69810 | 119057.518 | -49247.518 | -41.36% | 79341.5 | -9531.5 | -12.01% | 1.Trackers 253 & 329, 230, 338 are currently stuck from 06/24/24 | 1.SR093842
McCarthy Solar | NY | SOL-10992 | 140810 | 0 | 140810 |  | 199506 | -58696 | -29.42% | 1. Site tripped offline due to utility outage at 09:30 on 01/15 and site back online at 16:45 on 01/16 | 1.SR095582
Costanza | NY | SOL-10907 | 128370 | 0 | 128370 |  | 161660.6 | -33290.6 | -20.59% | 1.Site was tripped offline due to relay open at 03:22am Technician closed the relay,site back online at 12:10 on 01/23 2.Site was tripped offline due to relay open at 10:00am Technician closed the realy, site back online at14:30 on 01/26 3.Site was tripped offline due to relay open on 01/30 and technician closed the realy site back online on 01/31 | 1.SR095886 2.SR095986 3.SR096141 | SR095986 | SR096141
Lockenhurst Pond | NY | SOL-11000 | 175059 | 204006.8 | -28947.8 | -14.19% | 160367 | 14692 | 9.161%
Drinkwater | NY | SOL-10896 | 124560 | 0 | 124560 |  | 167148 | -42588 | -25.48% | 1. Low generation due to weather/snow.
Altamont | NY | SOL-11085 | 265275 | 472996.8 | -207721.8 | -43.92% | 348142.2 | -82867.2 | -23.8% | 1. Low generation due to weather/snow.
Krumkill North | NY | SOL-11086 | 203628 | 375941 | -172313 | -45.84% | 466230.1 | -262602.1 | -56.32% | 1. Low generation due to weather/snow.
Krumkill South | NY | SOL-11087 | 210392 | 367457.4 | -157065.4 | -42.74% | 365510.3 | -155118.3 | -42.44% | 1. Low generation due to weather/snow.
X092 | NY | SOL-11189
X093 | NY | SOL-10932 | 2111.4856 | 0 | 2111.4856 |  | 0 | 2111.4856 |  | 1. Many optimizers on SE are offline, EPC to complete. | 1. SR095945
X095 | NY | SOL-10929 | 5841.4006 | 0 | 5841.4006 |  | 0 | 5841.4006 |  | 1. Optimizers on SE are offline, EPC to complete. | 1. SR095946
X181 | NY | SOL-10428 | 4382.1068 | 0 | 4382.1068 |  | 0 | 4382.1068 |  | 1. Optimizers are offline, EPC to complete. | 1. SR095948
X415 | NY | SOL-10429 | 7232.0394 | 0 | 7232.0394 |  | 0 | 7232.0394 |  | 1. Optimizers are offline, EPC to troubleshoot. | 1. SR095950
K198 | NY | SOL-10930 | 5586.1182 | 0 | 5586.1182 |  | 0 | 5586.1182 |  | 1. Multiple optimizers are offline. | 1. SR095962
K203 | NY | SOL-11190
K213 | NY | SOL-11191
K217 | NY | SOL-10933 | 3763.5269 | 0 | 3763.5269 |  | 0 | 3763.5269 |  | 1. Multiple optimizers are offline. | 1. SR095960
K307 | NY | SOL-10876 | 6600.8426 | 0 | 6600.8426 |  | 0 | 6600.8426
K610 | NY | SOL-11158
M025 | NY | SOL-10392 | 6835.8961 | 0 | 6835.8961 |  | 0 | 6835.8961 |  | 1. Multiple optimizers are offline. | 1. SR095956
M028 | NY | SOL-10381 | 2615.2417 | 0 | 2615.2417 |  | 0 | 2615.2417 |  | 1. Appears no optimizers are connected. | 1. SR095955
Q030 | NY | SOL-10878 | 8979.27 | 0 | 8979.27 |  | 0 | 8979.27
Q130 | NY | SOL-10877 | 3425.508 | 0 | 3425.508 |  | 0 | 3425.508 |  | 1. Many optimizers are offline on the SE portal, working with EPC to complete. | 1. SR095937
Q196 | NY | SOL-10879 | 3235.96 | 0 | 3235.96 |  |  |  |  | 1. Many optimizers are offline on the SE portal, working with EPC to complete. | 1. SR095938
Q220 | NY | SOL-10873 | 6469.201 | 0 | 6469.201 |  |  |  |  | 1. Many optimizers are offline on the SE portal, working with EPC to complete. | 1. SR095939
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871 | 8851.6523 | 0 | 8851.6523 |  | 0 | 8851.6523 |  | 1. A few strings are offline. EPC to complete. 2. Inverter 2 tripped offline at 06:30 AM on 01/17. | 1. SR095941 2. SR095940 | SR095940
R003 | NY | SOL-10416 | [7 empty] | 1. Optimizers are offline, EPC to complete. | 1. SR095942
R007 | NY | SOL-10417 | 14021.9 | 0 | 14021.9 |  | 0 | 14021.9
BK16 | NY | SOL-11093 | 14917.8164 | 0 | 14917.8164 |  | 0 | 14917.8164 |  | 1. Multiple optimizers are offline. | 1. SR095961
Trenton - Trenton East | IL | SOL-11060
Trenton - Trenton West | IL | SOL-11061
Dakota - Dakota Solar 1 | IL | SOL-11113
X018 | NY | SOL-10418 | 6974.78 | 9491.525 | -2516.745 | -26.52% | 0 | 6974.78 |  | 1. Low generation due to weather/snow.
Janiak Solar | NY | SOL-10898 | 171787.774 | 248610.101 | -76822.327 | -30.9% | 209672.823 | -37885.049 | -18.07% | 1. Low generation due to weather/snow.
County Route 11B | NY | SOL-10983 | 314905 | 0 | 314905 |  | 0 | 314905 |  | 1.Inverter 2 tripped offline at 12:45PM on 01/02 and reporting "Overall work state as STOP" and later self resolved on 01/03. | 1.SR095242
Barone | NY | SOL-11034 | 246714 | 0 | 246714 |  | 210690 | 36024 | 17.1% | 1.Site tripped offline at 09:50AM on 01/12 due to relay opened later technician closed the relay on 01/13 at 08:45AM. 2.Site tripped offline at 15:45 on 01/31 due to relay opened. | 1.SR095500 2.SR096195 | SR096195
Cedarville | IL | SOL-11069 | 192250.1 | 230003.1 | -37753 | -16.41% | 193682.4 | -1432.3 | -0.7395% | 1.TCU tracker 56 position stuck at 7.29 Degrees,TCU 10 is stuck at -16 degrees, TCU 15 is also stuck at 0.34 degrees and setpoint stuck at 7.9 degrees from 08:00AM on 01/08. 2.Inverter 9 was offline on 01/21 and later self resolved on 01/22. | 1.SR095099 2.SR095797 | SR095797
O'Brien Hill #1 | NY | SOL-11098 | 286395 | 0 | 286395 |  | 0 | 286395 |  | 1.Trackers T01.A.29, 31, 33, 35, & 37 Tracker T02.E.11 are stuck from 01/17. This is EPC item per GenC during call 2.Site tripped offline on 01/29 at 17:25due recloser was open with a B and C phase fault, later technician closed the relay on 01/31 at 14:55 | 1.SR095644 2.SR096127 | SR096127
O'Brien Hill #2 | NY | SOL-11099 | 286189 | 0 | 286189 |  | 0 | 286189 |  | 1.Tracker T01 B27 stuck at -54 degrees from 1/2/25. 2.Inverter 1 tripped offline at 12:35 on 01/26 and reporting "Over all work state as STOP" later technician cleared a ground fault on Inverter 1 3.Combiner box 21 is was kept offline by EV solar on 01/15 4.Site tripped offline on 01/29 at 17:25 due recloser was open with a B and C phase fault, later technician closed the relay on 01/31 at 14:55 | 1.SR095284 2.SR095992 3.SR095328 4.SR096127 | SR095992 | SR095328 | SR096127
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036 | 1103 | 1699.803 | -596.803 | -35.11% | 2153.158 | -1050.158 | -48.77% | 1. Low generation due to weather/snow.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 7974 | 8441.895 | -467.895 | -5.543% | 9806.328 | -1832.328 | -18.69% | 1. The inverter was offline from 01/01 as it was being RMA'd. After the inverter was replaced, it came back online on 01/16 at 11:00 AM. | 1.SR095581
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 10130 | 8193.353 | 1936.647 | 23.64% | 9801.081 | 328.919 | 3.356%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Feb
Generate Capital |  |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  |  | 9904560.3573 | 4894424.509 | 5010135.8483 | 102.4% | 15070074.835 | -5165514.4777 | -34.28% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 17315.75 | 21363.42 | -4047.67 | -18.95% | 15170.88 | 2144.87 | 14.14% | 1.Low generation due to weather/snow.
K041 | NY | SOL-10357 | 13320.7812 | 17186.99 | -3866.2088 | -22.49% | 13859 | -538.2188 | -3.884% | 1.Low generation due to weather/snow.
K043 | NY | SOL-10358 | 15518.3438 | 18500.95 | -2982.6063 | -16.12% | 3061 | 12457.3438 | 407% | 1.Estimated values are low in AE we have also verified the file which was given GC
K058 | NY | SOL-10360 | 4162.5625 | 9281.183 | -5118.6205 | -55.15% | 12005.22 | -7842.6575 | -65.33% | 1.The inverters experienced multiple tripping events on 02/14,17,18,19,20 due to intermittent voltage on phase B. The site tripped offline at 08:52 AM on 02/21. The technician arrived and stated that the cause was a blown phase C fuse and thermal damage to the AC disconnect. The site will remain offline until the parts are replaced. | 1.SR097569
K115 | NY | SOL-10361 | 3372.4181 | 7965.901 | -4593.4829 | -57.66% | 7488.091 | -4115.6729 | -54.96% | 1. 96 optimizers are down for site construction. 2. Low generation due to weather/snow. | 1.SR093291
K152 | NY | SOL-10362 | 4885.5938 | 5681.248 | -795.6542 | -14% | 4676 | 209.5938 | 4.482% | 1. Low generation due to weather/snow.
K166 | NY | SOL-10363 | 17203.5 | 21280.06 | -4076.56 | -19.16% | 16417.23 | 786.27 | 4.789% | 1. Low generation due to weather/snow.
K206 | NY | SOL-10927 | 10148.3241 | 12619.81 | -2471.4859 | -19.58% | 9232 | 916.3241 | 9.926% | 1.Low generation due to weather/snow.
K251 | NY | SOL-10365 | 11751.0625 | 0 | 11751.0625 |  | 11033.06 | 718.0025 | 6.508% | 1.Weather station is not communicating since 11/22/2024. | 1.SR093633
K269 | NY | SOL-10366 | 10325.6875 | 14133.12 | -3807.4325 | -26.94% | 10722.85 | -397.1625 | -3.704%
K273 | NY | SOL-10367 | 10878.625 | 0 | 10878.625 |  | 12777 | -1898.375 | -14.86% | 1. Weather station is not communicating since 06/30/2024. 2. 26 optimizers are down for roof repair. | 1.SR086842 2.SR093294 | SR093294
K287 | NY | SOL-10919 | 9429.75 | 9596.787 | -167.037 | -1.741% | 9504 | -74.25 | -0.7812%
K298 | NY | SOL-10368 | 9181.5 | 12211.43 | -3029.93 | -24.81% | 9465 | -283.5 | -2.995% | 1.Low generation due to weather/snow.
K335 | NY | SOL-10370 | 9894.3125 | 13143.68 | -3249.3675 | -24.72% | 10841 | -946.6875 | -8.732% | 1.Low generation due to weather/snow.
K345 | NY | SOL-10920 | 12057.6312 | 9026.366 | 3031.2652 | 33.58% | 11577 | 480.6312 | 4.152%
K445 | NY | SOL-10373 | 9972.625 | 13155.89 | -3183.265 | -24.2% | 9461.312 | 511.313 | 5.404% | 1.Low generation due to weather/snow.
K495 | NY | SOL-10374 | 576 | 39846.9 | -39270.9 | -98.55% | 42524 | -41948 | -98.65% | 1.Due to shunt trips of the switchgear and overcurrent faults, the site has been offline since 11/20/2024. It came back online at 10:25 AM on 02/12 and again tripped offline at 05:25 PM on 02/13 till date. | 1.SR093196
M020 | NY | SOL-10380 | 10867.5312 | 12814.96 | -1947.4287 | -15.2% | 11685 | -817.4688 | -6.996% | 1. Low generation due to weather/snow.
M092 | NY | SOL-10383 | 10232.6875 | 12943.67 | -2710.9825 | -20.94% | 10669.36 | -436.6725 | -4.093% | 1.Low generation due to weather/snow.
M143 | NY | SOL-10384 | 11888.4375 | 14631.46 | -2743.0225 | -18.75% | 11479.42 | 409.0175 | 3.563% | 1. Low generation due to weather/snow.
M144 | NY | SOL-10385 | 17687.0312 | 0 | 17687.0312 |  | 18132 | -444.9688 | -2.454%
M167 | NY | SOL-10386 | 12276.0625 | 12046.86 | 229.2025 | 1.903% | 13350.32 | -1074.2575 | -8.047%
M188 | NY | SOL-10387 | 9166.4375 | 0 | 9166.4375 |  | 9611 | -444.5625 | -4.626%
EMHC | NY | SOL-10351 | 3579.1094 | 2980.918 | 598.1914 | 20.07% | 3438.427 | 140.6824 | 4.091%
Q008 | NY | SOL-10397 | 10602.4375 | 13743.77 | -3141.3325 | -22.86% | 14789 | -4186.5625 | -28.31% | 1.The site went offline at 09:45 on 02/14 due to the AC breaker tripping. The technician reset the breaker, and the site came back online at 11:00 on 02/18. 2.The site was offline from 13:15 on 02/21 due to the main breaker tripping. The technician reset the breaker, and the site came back online at 08:45 on 02/24. | 1. SR097083 2. SR097636 | SR097636
Q018 | NY | SOL-10398 | 10195.875 | 10582.87 | -386.995 | -3.657% | 8701.015 | 1494.86 | 17.18%
Q021 | NY | SOL-10399 | 7999.0625 | 9770.419 | -1771.3565 | -18.13% | 7091 | 908.0625 | 12.81% | 1. Low generation due to weather/snow.
Q025 | NY | SOL-10400 | 13488.125 | 15603.33 | -2115.205 | -13.56% | 9540 | 3948.125 | 41.38% | 1. Low generation due to weather/snow.
Q074 | NY | SOL-10402 | 8712.375 | 9652.334 | -939.959 | -9.738% | 8010.304 | 702.071 | 8.765%
Q115 | NY | SOL-10872 | 11579.0625 | 13986.53 | -2407.4675 | -17.21% | 10682.2 | 896.8625 | 8.396% | 1. Low generation due to weather/snow.
Q139 | NY | SOL-10403 | 6671.9375 | 7652.461 | -980.5235 | -12.81% | 6752 | -80.0625 | -1.186% | 1. Low generation due to weather/snow.
Q157 | NY | SOL-10404 | 11403.1875 | 14877.12 | -3473.9325 | -23.35% | 12206.92 | -803.7325 | -6.584% | 1.Low generation due to weather/snow.
Q192 | NY | SOL-10406 | 18821 | 23040.39 | -4219.39 | -18.31% | 17990.99 | 830.01 | 4.613% | 1. Low generation due to weather/snow.
Q210 | NY | SOL-10407 | 15487.5 | 16908.57 | -1421.07 | -8.404% | 15013 | 474.5 | 3.161%
Q229 | NY | SOL-10408 | 6297.9062 | 8488.41 | -2190.5037 | -25.81% | 5292.695 | 1005.2113 | 18.99% | 1.Low generation due to weather/snow.
Q231 | NY | SOL-10870 | 25056.625 | 32973.33 | -7916.705 | -24.01% | 23657 | 1399.625 | 5.916% | 1.Low generation due to weather/snow.
Q405 | NY | SOL-10409 | 28712.875 | 33159.45 | -4446.575 | -13.41% | 26589.46 | 2123.415 | 7.986% | 1. Low generation due to weather/snow.
Q435 | NY | SOL-10923 | 38240.625 | 33165.41 | 5075.215 | 15.3% | 34507 | 3733.625 | 10.82%
Q485 | NY | SOL-10869 | 30533.75 | 31458.8 | -925.05 | -2.941% | 32755.35 | -2221.6 | -6.782% | 1. Inverter 1 right unit offline from 02/03 due to comms card being RMAD and came back online on 02/28 | 1. SR096249
Q490 | NY | SOL-10411 | 24146.5 | 0 | 24146.5 |  | 22664.36 | 1482.14 | 6.54% | 1. optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline | 1.SR093326
Q620 | NY | SOL-10867 | 36470.75 | 40130.17 | -3659.42 | -9.119% | 36602.33 | -131.58 | -0.3595%
QMOA | NY | SOL-10415 | 3286.3 | 0 | 3286.3 |  | 3713.027 | -426.727 | -11.49%
X024 | NY | SOL-10419 | 13357.0312 | 17555.58 | -4198.5488 | -23.92% | 11514 | 1843.0312 | 16.01% | 1.Inverter 2 central unit offline and reporting "DC Isolation on 02/04 and again resolved on 02/05 | 1.SR096294
X026 | NY | SOL-10420 | 10799.6 | 13459.43 | -2659.83 | -19.76% | 15192.76 | -4393.16 | -28.92% | 1.Inverter 2 left unit technician was swapped and is back online on 02/03 | 1.SR095758
X090 | NY | SOL-10925 | 10677.875 | 8915.463 | 1762.412 | 19.77% | 9953 | 724.875 | 7.283%
X117 | NY | SOL-10422 | 8069 | 11399.76 | -3330.76 | -29.22% | 8666.424 | -597.424 | -6.894% | 1.Low generation due to weather/snow.
X125 | NY | SOL-10423 | 15785 | 18886.62 | -3101.62 | -16.42% | 15455.69 | 329.31 | 2.131% | 1. Low generation due to weather/snow.
X134 | NY | SOL-10424 | 15055.5625 | 0 | 15055.5625 |  | 15137 | -81.4375 | -0.538%
X135 | NY | SOL-10425 | 12885.6875 | 15852.51 | -2966.8225 | -18.72% | 13152 | -266.3125 | -2.025%
X139 JHS 222 | NY | SOL-10426 | 19027.0214 | 21977.34 | -2950.3186 | -13.42% | 17714 | 1313.0214 | 7.412%
X140 | NY | SOL-10926 | 11175.4375 | 10393.82 | 781.6175 | 7.52% | 10945 | 230.4375 | 2.105%
X166 | NY | SOL-10427 | 11556.1 | 14445.19 | -2889.09 | -20% | 11066 | 490.1 | 4.429% | 1.Low generation due to weather/snow.
Murphy | MN | SOL-10094 | 460150 | 753001.2 | -292851.2 | -38.89% | 667564.9 | -207414.9 | -31.07% | 1.Low generation due to weather/snow.
Terning | MN | SOL-10093 | 350130 | 749173.8 | -399043.8 | -53.26% | 630205.7 | -280075.7 | -44.44% | 1.Low generation due to weather/snow.
Boas Road 04 | NY | SOL-10908 | 126816 | 236439.995 | -109623.995 | -46.36% | 221381.46 | -94565.46 | -42.72% | 1.Inverter 1 tripped offline at 07:35 AM on 02/05/25 due to an SE INTERCOOLER SYS (104) fault and came back online at 11:50 AM the same day. | 1. SR096330
Kelly Bridge Farm | NY | SOL-10911 | 129392 | 222534.077 | -93142.077 | -41.86% | 209678.4 | -80286.4 | -38.29% | 1.Inverter 30 came back online at 15:35 on 02/19/25 after the technician replaced the fuses and re-energized 2. Inverter 4 came back online at 10:00AM on 02/04/25 after the technician replaced the blown fuses. | 1. SR095473 2. SR096164 | SR096164
Pool Brook Road | NY | SOL-10909 | 103676 | 166624.153 | -62948.153 | -37.78% | 197019.95 | -93343.95 | -47.38% | 1. Site was offline from 09:05 to 13:35 on 02/13/25 due to an brife utility outage. | 1.SR096701
Sackett Lake | NY | SOL-10910 | 133417 | 238769.59 | -105352.59 | -44.12% | 223751.3 | -90334.3 | -40.37% | 1.Inverter 1 started late at 13:30 on 02/12/25 due to an AC contactor fault and went offline again on 02/21/25. On 02/22/25, the technician swapped the CCU between Inverters 1 and 2 as per Ingeteam's instructions, but the issue persisted. The fiber cables are fine, and further investigation is needed to get Inverter 1 online. On 02/24/25, the technician shut down the site, swapped the CPU boards between Inverters 1 and 2, and both inverters resumed production with no alarms. However, both showed a "LVRT board fail" warning. Ingeteam confirmed that this warning can be ignored as the LVRT boards are disabled on all inverters. Inverters 1 and 2 are now back online at 15:30 the same day. | 1. SR096750
Burritt Road | NY | SOL-10913 | 70080 | 0 | 70080 |  | 176195.64 | -106115.64 | -60.23% | 1.POA Pyranometer is not communicating from 07:00AM on 11/09/24 and throughout the month due to a malfunctioning NPort, where the POA and GHI are connected. | 1. SR093972
Villa Roma 1 | NY | SOL-10914 | 108474 | 143425.427 | -34951.427 | -24.37% | 154660.6 | -46186.6 | -29.86% | 1. Inverter 2 back online at 13:40 on 02/03/25, after technician Installed missing termination connector. 2. Inverter 1 tripped offline at 08:35 on 02/12/25 due to a DC contactor fault. The technician checked the DC contactor and power-cycled the inverter, bringing it back online at 12:55 the same day. 3. Inverter 2 Combiner Box 8 has been offline since 02/13/25. On 02/18/25, the technician found open fuses in CB 8 and closed them. While on-site, Inverter 1 tripped offline at 08:40AM due to a DC contactor fault. After troubleshooting, the technician reset the inverter, restoring production. Both the combiner and inverter are producing as expected from 10:30AM the same day. 4. Inverter 1 tripped offline at 11:15 AM on 02/22/25 due to a DC contactor fault and came back online at 13:10 the same day after Ingeteam reset it. On 02/24/25, the technician shut down the inverter at 08:15 AM, opened the cabinets, found no loose connections or heat damage, disengaged the e-stop, and the inverter resumed production at 10:05 AM the same day. | 1. SR095919 2. SR096726 3. SR096907, SR097233 4. SR097643 | SR096726 | SR096907 | SR097233 | SR097643
Villa Roma 2 | NY | SOL-10915 | 116176 | 202602.862 | -86426.862 | -42.66% | 149735.1 | -33559.1 | -22.41% | 1.Low generation due to weather/snow.
Washington 1 | NY | SOL-10912 | 91690 | 180993.099 | -89303.099 | -49.34% | 174362.65 | -82672.65 | -47.41% | 1. Inverter 1 was offline on 02/02/25 due to an AC contactor fault. On 02/03/25, the technician found the panel door blown off with bent hinges, reattached it, and temporarily supported it. New hinges are needed. After power cycling and resetting, an AC contactor alarm cleared, but a Fan 2 warning remains. It was back online at 12:55pm the same day. 2. Site tripped offline at 15:45 on 02/28/25 and came back online after a brief communication outage at 21:15 on the same day | 1. SR095483 2. SR097935 | SR097935
Washington 3 | NY | SOL-10828 | 114033 | 0 | 114033 |  | 213534.97 | -99501.97 | -46.6% | 1. POA sensor continues to read inaccurately. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. 2.Inverter 2 was offline all day on 02/02/25 due to an AC contactor fault. On 02/03/25, it came back online at 14:30 after the technician closed the breaker, tested voltages, and verified the D134 LED was on. It was offline again all day on 02/20/25. On 02/21/25, the technician found damaged wiring on J15 with a broken wire jacket. Voltage for Q4 tested around 490VAC, and the breakers were power cycled. It was back online at 10:45 AM on 02/22/25. | 1. SR093024 2. SR095445, SR097568 | SR095445 | SR097568
Washington 4 | NY | SOL-10829 | 72393 | 214328.826 | -141935.826 | -66.22% | 213201.1 | -140808.1 | -66.04% | 1. Meter has been capturing full production since 02/25/25, after the technician adjusted the blade and confirmed that all three phases are reporting production. 2. Site was taken offline from 13:25 to 15:40 on 02/03/25. The technician changed the tap from E/5 to C/3 on the transformer. 3. Inverter 1 tripped offline at 14:15 on 02/02/25 due to an AC contactor fault. On 02/03/25, the technician swapped the CCu boards between Inverters 1 and 2, bringing it back online at 15:40 the same day. It tripped offline again at 08:10 AM on 02/08/25 due to a DC contactor fault and was back online at 15:25 the same day. It tripped offline once more at 07:55 on 02/14/25, and after Ingeteam remotely reset it, it was brought back online at 07:40 on 02/15/25. 4. Inverter 2 tripped offline at 15:15 on 02/14/25 due to Iac out of range and Inst. Iac overcurrent faults. The technician replaced all 3 AC fuses with new 350A fuses from inventory, power cycled the system, and brought it back online at 12:50 on 02/15/25. | 1. SR096121 2. SR096150 3. SR096230, SR096525 & SR097011 4. SR097121 | SR096150 | SR096230 | SR096525 | SR097011 | SR097121
Big Tree | NY | SOL-10966 | 72637 | 0 | 72637 |  | 174248.8 | -101611.8 | -58.31% | 1.Low generation due to weather/snow.
Canoga | NY | SOL-10965 | 371320 | 0 | 371320 |  | 542311.13 | -170991.13 | -31.53% | 1. Weather station has reported 0 since 8/21. New UP POA and Down POA need replacement. Gen Cap advised holding off dispatch. 2. Inverter 3 had been offline since 01/26 due to an IAC out-of-range issue. On 02/27 AC cap bank was replaced with new RMA parts (cap bank, wires, and fuses). Verified with Sahith/Ingeteam that 350A fuses (the new standard) are suitable replacements for the 250A fuses. Inverter 3 is back online at 12:50. 3. Inverter 4 tripped offline intermittently throughout the month due to 'IAC out of range,' but self-resolved each time. | 1. SR094278 2. SR095991 3. SR096215 | SR095991 | SR096215
County Route 84 | NY | SOL-10967 | 490380 | 0 | 490380 |  | 565014.13 | -74634.13 | -13.21% | 1. The site tripped offline at 10:02 AM and came back online at 11:50 AM on 02/14. The utility had two circuits in a parallel configuration. | 1. SR097025
Donati | NY | SOL-10968 | 145850 | 0 | 145850 |  | 242335.08 | -96485.08 | -39.81% | 1. Weather station Reporting 0 value from 05/31. POA sensors need to be replaced. Quote provided to Gen Cap for approval. 2. Inverter 2 did not start production, and Inverter 1 tripped offline at 12:50 on 02/16. Both inverters self-resolved and came back online on 02/17. 3. Trackers A01, A05, A06, A07, A10, B17, D20, F19, F21, F22, F32, F33, and G14 have been stuck since various dates, totaling 13 trackers. Gen Cap advised holding off on dispatch | 1. SR092964 2. SR097169 3. SR095253 | SR097169 | SR095253
Henrietta | NY | SOL-10972 | 284330 | 0 | 284330 |  | 435403 | -151073 | -34.7% | 1. Inverter 1 tripped offline at 13:25 due to an 'Insulation fault' and later self-resolved, came back online at 2:20 PM on 02/19. | 1. SR097524
NY 70 | NY | SOL-10970 | 381710 | 0 | 381710 |  | 546198.4 | -164488.4 | -30.12% | 1. Inverter 1 started late for production at 12:05 on 02/14 due to Hardware error. 2. Site tripped offline at 11:20AM and later self resolved , came back online at 4:2PM on 02/16. 3. Inverter 1 was offline since the morning of 02/21 due to a hardware error. The technician swapped NTC boards between Inverters 1 and 2, then re-energized both units. Inverters 1 and 2 are now online and producing. 4. The site tripped offline at 8:15 AM due to utility work and came back online at 10:20 AM on 02/24. Again site tripped offline at 13:05 and back online at 05:10PM on 02/26. | 1. SR097010 2. SR097162 3. SR097599 4. SR097684, SR097701 | SR097162 | SR097599 | SR097684 | SR097701
Reid | NY | SOL-10991 | 100770.982 | 356493.2 | -255722.218 | -71.73% | 430708 | -329937.018 | -76.6% | 1. Inverter 5 tripped offline on 02/28 at 13:45 due to Grid Line Voltage Out of Range. 2. Inverter 23 was offline since 11/29 reporting Grid Phase Voltage Out of Range. Gen Cap advised holding off dispatch. | 1. SR097930 2. SR093436 | SR093436
Sangolqui | NY | SOL-10975 | 149355 | 0 | 149355 |  | 234644.93 | -85289.93 | -36.35% | 1. Inverter 1 started production late at 11:40 AM and went offline again from 12:05 PM to 12:50 PM while the technician was onsite for the head tracker replacement. 2. Inverter 1 didn't started for production on 02/16 and self resolved started for production on 02/17. 3. Inverter 1 didn't started for production due to Isolation fault on 02/27 and self resolved started for production on 02/28. | 1. SR096416 2. SR097158 3. SR097883 | SR097158 | SR097883
State Highway 17B | NY | SOL-10988 | 360290 | 0 | 360290 |  | 472300.06 | -112010.06 | -23.72% | 1. Inverter 4 has been offline since 11/13/24 and reporting Fault elect. supply. On 02/03 tech Installed missing hardware stacks, inverter 4 was back online at 2:55 PM on same day. Later technician replaced few fuses for combiner boxes 30 & 35 on 02/04 | 1. SR093375
State Route 14A | NY | SOL-10997 | 403215 | 0 | 403215 |  | 539717.54 | -136502.54 | -25.29% | 1. Inverter 1 experienced multiple tripping events between 02/11 t0 02/19. On 02/19 technician was onsite and replaced a fan, inverter 1 back online at 2:05PM on 02/19. | 1. SR096675
West Creek | NY | SOL-10995 | 448900 | 0 | 448900 |  | 504797.7 | -55897.7 | -11.07% | 1.Low generation due to weather/snow.
Wildflower | NY | SOL-10982 | 369846.5 | 0 | 369846.5 |  | 608235.16 | -238388.66 | -39.19% | 1. On 02/09, Inverter 1 tripped offline at 13:10, and Inverter 2 tripped offline at 09:25 due to SE IAC FILTER RMS UNBALANCED HIGH. Ingeteam remotely reset the inverters, and both were back online at 16:15 on 02/09 On 02/18, Inverter 1 tripped offline again at 07:45 due to an IAC Overcurrent fault and started late for production because of a DC Contactor fault. The technician found and replaced one AC fuse with thermal damage, and the inverters were back online at 11:35 2. Inverter 3 tripped offline at 11:20AM and back online at 12:20PM on 02/04. Technician was onsite replaced harmonics filter/capacitor bank. 3. On 02/19, Inverter 2 did not start production due to an AC Contactor fault. Ingeteam reset the inverter, bringing it online at 2:05 PM. On 02/18–02/21, Inverters 1 and 2 had multiple tripping events that self-resolved by day’s end. On 02/25, tech checked all inverters online. Inverter 2 has been stable since 02/21. No AC contactor issues, but minor water on the bus bar (wiped dry) and thermal damage on an AC fuse wire. Parts received and dispatch has been Assigned for march. | 1. SR096552 2. SR095852 3. SR097526 | SR095852 | SR097526
Glen Mary 1 | NY | SOL-10993 | 474210 | 0 | 474210 |  | 580930 | -106720 | -18.37% | 1.Low generation due to weather/snow.
Glen Mary 2 | NY | SOL-10994 | 15960 | 0 | 15960 |  | 242369.3 | -226409.3 | -93.42% | 1. Inverter 1 has been offline since 01/16 reporting Overall work status as "STOP". On 02/26 technician installed fuse and repaired affected Combiner boxes. Inverter 1 back online at 1:00PM on 02/26. | 1. SR095635
Telegraph 1 | NY | SOL-11003 | 205099 | 0 | 205099 |  | 385388.91 | -180289.91 | -46.78% | 1. The site tripped offline at 8:10 AM on 02/24 due to a utility outage. Utility power was restored on 02/26, and the site came back online at 3:25 PM. | 1. SR097667
Telegraph 2 | NY | SOL-11004 | 117513 | 0 | 117513 |  | 199344.36 | -81831.36 | -41.05% | 1. The site tripped offline at 3:45AM on 02/24 due to a utility outage. Utility power was restored on 02/26, and the site came back online at 6:05PM. | 1. SR097668
Cafferty Hill | NY | SOL-10996 | 430610 | 0 | 430610 |  | 487273.3 | -56663.3 | -11.63% | 1.Low generation due to weather/snow..
Dunkleman | NY | SOL-11008 | 357280 | 0 | 357280 |  | 577807.1 | -220527.1 | -38.17% | 1. Currently, the following trackers are stuck Group 1: 11–12, 23, 37–38, 57 & 59, 75 & 76, 106 & 119 Group 2: 10, 24, 27, 32, 36, 38–39, 43, 52, 54, 59, 61 & 66, 86 & 97, 114 & 124 A total of 9 tracker control units have been RMA'd. | 1. SR095109
Route 19 1 | NY | SOL-11001 | 153320 | 0 | 153320 |  | 230848.08 | -77528.08 | -33.58% | 1. The site tripped offline between 8:05AM to 3.25PM on 02/26 due to utility outage. | 1. SR097685
Route 19 2 | NY | SOL-11002 | 399420 | 0 | 399420 |  | 591330.4 | -191910.4 | -32.45% | 1. The site tripped offline between 8:05AM to 3.25PM on 02/26 due to utility outage. 2. Inverter 1 was offline on 01/31 and technician was unable to access the site due to heavy snowbank at the access road, inverter self resolved and back online on 02/01. | 1. SR097686 2. SR096177 | SR096177
Yellow Mills 1 | NY | SOL-11006 | 0 | 0 | 0 |  | 176276.8 | -176276.8 | -100% | 1. The site tripped offline at 11:20AM on 01/29. Two 2PA1 boards need to be replaced. One board has been received and replaced, and are waiting for the other board. Further troubleshooting with Sungrow is required. | 1. SR096106, SR095599 | SR095599
Yellow Mills 2 | NY | SOL-11005 | 95037 | 0 | 95037 |  | 181688.5 | -86651.5 | -47.69% | 1.Low generation due to weather/snow.
Yellow Mills 3 | NY | SOL-11007 | 57876 | 0 | 57876 |  | 169042.26 | -111166.26 | -65.76% | 1. Inverter is producing low due to CB's 1,2,3,4 are showing negative production values and CB's 5,6,7,8,9 are producing barely from 02/14. Further troubleshooting with Sungrow is required. | 1. SR097829
Catskill | NY | SOL-11021 | 321660 | 0 | 321660 |  | 378964.03 | -57304.03 | -15.12% | 1. Inverter 2 experienced intermittent tripping events throughout the month. On 02/28 technician was onsite and replaced the CB PV wire and connectors. CB 21 is back online, and Inverter 2 is showing no faults. 2. The site tripped offline at 10:50AM and later back online at 11:40AM on 02/12. | 1.SR094307 2. SR096751 | SR096751
Eddy Ridge | NY | SOL-11054 | 161167.3 | 0 | 161167.3 |  | 261685 | -100517.7 | -38.41% | 1.Low generation due to weather/snow.
Ridgeway #1 | NY | SOL-11018 | 355256 | 0 | 355256 |  | 585713.2 | -230457.2 | -39.35% | 1. Currently total of 40 trackers are being struck due to snowfall in the area. Will need to be investigated. | 1. SR097457
Rivard 1 | NY | SOL-11011 | 309993.4211 | 396616.5 | -86623.0789 | -21.84% | 398747.4 | -88753.9789 | -22.26% | 1.Low generation due to weather/snow.
Rivard 2 | NY | SOL-11012 | 313341.1813 | 304931.1 | 8410.0813 | 2.758% | 381926.8 | -68585.6187 | -17.96% | 1.Tracker control 33 - 90, 129 - 136, 148 , 20-32, 123-128, 172-183 are not communicating & tracker 156 , 121 is stuck and production dropped (approxmately ) 25 KW down. | 1.SR095073
Ridgeway #2 | NY | SOL-11027 | 178480 | 0 | 178480 |  | 302945.3 | -124465.3 | -41.09% | 1. Trackers 25 & 59 are currently stuck from 02/14.Tech cleared alarms and recalibrated snow sensor. Will need to return to calibrate snow sensor again once snow has melted 2. 12 trackers are currently stuck: 13, 20, 25, 52, 54, 56, 59, 70, 72, 76, 85, & 88 due to residual snow onsite. As per Per GenC, hold on dispatch | 1. SR097015 , SR097436 2.SR097751 | SR097436 | SR097751
Spencer | NY | SOL-11017 | 506432 | 0 | 506432 |  | 640780 | -134348 | -20.97% | 1.Trackers 138, 141, & 147 are stuck. GenC says to hold on dispatch 2. Inverter 2 tripped offline at 9:25AM on 02/16 and selfresolved on 02/17 3. Inverter 1 tripped offline at 1:55PM on 02/22 and selfresolved on 02/23 | 1. SR095821 2. SR097157 3.SR097647 | SR097157 | SR097647
Reisender | NY | SOL-10886 | 164650 | 227955.559 | -63305.559 | -27.77% | 200588.3 | -35938.3 | -17.92% | 1.Low generation due to weather/snow.
Finney | NY | SOL-10999 | 468670 | 0 | 468670 |  | 630586.74 | -161916.74 | -25.68% | 1.Low generation due to weather/snow.
Davis Solar | NY | SOL-10958 | 197368 | 259655 | -62287 | -23.99% | 249300 | -51932 | -20.83% | 1.Low generation due to weather/snow.
Genesee | NY | SOL-10951 | 203639.4 | 0 | 203639.4 |  | 365270.6 | -161631.2 | -44.25% | 1. Inverter 2 is currently offline and reporting “AC Breaker switch open from 02/20 | 1. SR097565
Landau I | NY | SOL-10891 | 210150 | 0 | 210150 |  | 248827.5 | -38677.5 | -15.54%
Landau II | NY | SOL-10895 | 390900 | 0 | 390900 |  | 529946.01 | -139046.01 | -26.24% | 1.Low generation due to weather/snow.
New Beginnings | NY | SOL-10890 | 190730 | 265677.15 | -74947.15 | -28.21% | 247191.04 | -56461.04 | -22.84% | 1.Low generation due to weather/snow.
Bullitt Farm Solar, LLC | NY | SOL-10998 | 239278 | 412605.85 | -173327.85 | -42.01% | 538628.5 | -299350.5 | -55.58% | 1.Low generation due to weather/snow.
Brodhead Solar, LLC | NY | SOL-10899 | 266505 | 276256.89 | -9751.89 | -3.53% | 258251.13 | 8253.87 | 3.196% | 1. NCU 1 tracker 10 is currently stuck and has a production loss of 9.5kw. 2.NCU 2 tracker 1 stuck again, tracker 35 remains stuck and has a production loss of 19kw. | 1. SR097725 2. SR095624 | SR095624
Svenski | NY | SOL-10894 | 190306 | 0 | 190306 |  | 239078.53 | -48772.53 | -20.4% | 1.Low generation due to weather/snow.
Bantam | NY | SOL-10986 | 72770 | 0 | 72770 |  | 574351.3 | -501581.3 | -87.33% | 1.POA1 is not accurately reporting - technician need to visit for further troubleshooting 2.currently 9 additional stuck trackers. Tech found stuck trackers - possibly snow related. Will need to wait for snow to melt | 1. SR096042 2.SR096682 | SR096682
Bogart | NY | SOL-10887 | 212200 | 234482.041 | -22282.041 | -9.503% | 227697.5 | -15497.5 | -6.806% | 1. CBs 1.12 & 1.13 are underperforming from 01/27. | 1.SR096006
Dubois | NY | SOL-10892 | 180310 | 0 | 180310 |  |  |  |  | 1.Modules 3 and 4 offline from 02/05. After troubleshooting the inverter modules back online on 02/21 | 1.SR096934
Salt Point | NY | SOL-10888 | 218340 | 0 | 218340 |  | 214083.4 | 4256.6 | 1.988% | 1.NCU 2 tracker 151 is stuck on 02/19 | 1.SR097471
Wheatland 2A | NY | SOL-10971 | 318700 | 0 | 318700 |  | 408837.7 | -90137.7 | -22.05% | 1.12 trackers are stuck in different dates due to Several actuators adjusted from 01/06, need to contact slater to reset. Sent Slater an Email, 6 more trackers need TS | 1.SR094820
Wheatland 2B | NY | SOL-10961 | 320430 | 0 | 320430 |  | 403613.2 | -83183.2 | -20.61% | 1. 29 trackers are stuck on different dates from 01/06 due to actuators need replacement and the technician requested update from Slater. Tech adjusted actuators, but Spc 2410 still needs troubleshooting from Nextracker | 1.SR095759
Brickchurch | NY | SOL-10889 | 85870 | 136599.924 | -50729.924 | -37.14% | 119208.74 | -33338.74 | -27.97% | 1.Trackers 253 & 329, 230, 338 are currently stuck from 06/24/24 2. The majority of trackers on-site are currently stuck. This event coincides with recent snowfall in the area and as a result, site production is minimal | 1. SR096669 2.SR097454 | SR097454
McCarthy Solar | NY | SOL-10992 | 226670 | 0 | 226670 |  | 243726.4 | -17056.4 | -6.998% | 1.Inverter 1 tripped offline at 14:25 and reporting " AC Breaker switch open on 02/04 selfresolved on 02/05. | 1. SR096303
Costanza | NY | SOL-10907 | 160740 | 0 | 160740 |  | 235079.29 | -74339.29 | -31.62% | 1.Site offline from 09:35 to 15:42 on 02/13 due to relay tripped later technician closed in the relay to reenergize the site . 2.site was offline at 20:04 on 2/16 due to the recloser tripping. Later, the technician closed the SEL to reenergize the site, bringing it back online at 12:14 on 02/18 3.Site offline from 10:00 to 12:53 on 02/28 due to SEL relay was open. Later, the technician closed the SEL to reenergize the site, bringing it back online | 1.SR096906 2. SR097179 3.SR097913 | SR097179 | SR097913
Lockenhurst Pond | NY | SOL-11000 | 235272 | 255015.6 | -19743.6 | -7.742% | 218702 | 16570 | 7.577%
Drinkwater | NY | SOL-10896 | 135100 | 0 | 135100 |  | 227553.66 | -92453.66 | -40.63% | 1.Low generation due to weather/snow.
Altamont | NY | SOL-11085 | 381372 | 496237.5 | -114865.5 | -23.15% | 452003.8 | -70631.8 | -15.63% | 1.Site offline due to relay open from 06:30 to 11:00 on 02/14 later SEL auto reclosed. Site back online. 2.Site was offline from 05:15 to 15:00 on 02/17. Later self resolved | 1.SR097024 2.SR097188 | SR097188
Krumkill North | NY | SOL-11086 | 331760 | 482100.4 | -150340.4 | -31.18% | 577126.7 | -245366.7 | -42.52% | 1.Low generation due to weather/snow.
Krumkill South | NY | SOL-11087 | 308273 | 399017.4 | -90744.4 | -22.74% | 452450.3 | -144177.3 | -31.87% | 1.Low generation due to weather/snow.
X092 | NY | SOL-11189
X093 | NY | SOL-10932 | 5962.3919 | 0 | 5962.3919 |  | 0 | 5962.3919 |  | 1. Many optimizers on SE are offline, EPC to complete. 2. Inverter 2 offline at 13:00 on 02/21 and back online at 11:45AM on 02/25. | 1. SR095945 2. SR097637 | SR097637
X095 | NY | SOL-10929 | 7581.9853 | 0 | 7581.9853 |  | 0 | 7581.9853 |  | 1. Optimizers on SE are offline, EPC to complete. | 1. SR095946
X181 | NY | SOL-10428 | 12161.1869 | 0 | 12161.1869 |  | 0 | 12161.1869 |  | 1. Optimizers are offline, EPC to complete. | 1. SR095948
X415 | NY | SOL-10429 | 6531.1523 | 0 | 6531.1523 |  | 0 | 6531.1523 |  | 1. Optimizers are offline, EPC to troubleshoot. | 1. SR095950
K198 | NY | SOL-10930 | 8238.6279 | 0 | 8238.6279 |  | 0 | 8238.6279 |  | 1. Multiple optimizers are offline. | 1. SR095962
K203 | NY | SOL-11190 | [7 empty] | 1. Multiple optimizers are offline. | 1. SR095954
K213 | NY | SOL-11191
K217 | NY | SOL-10933 | 5661.9753 | 0 | 5661.9753 |  | 0 | 5661.9753 |  | 1. Multiple optimizers are offline. | 1. SR095960
K307 | NY | SOL-10876 | 12916.7617 | 0 | 12916.7617 |  | 0 | 12916.7617
K610 | NY | SOL-11158
M025 | NY | SOL-10392 | 11939.3408 | 0 | 11939.3408 |  | 0 | 11939.3408 |  | 1. Multiple optimizers are offline. 2. Inverter 2 tripped offline at 09:15 on 02/07. | 1. SR095956 2. SR096424 | SR096424
M028 | NY | SOL-10381 | 8250.1923 | 0 | 8250.1923 |  | 0 | 8250.1923 |  | 1. Appears no optimizers are connected. | 1. SR095955
Q030 | NY | SOL-10878 | 12842.9084 | 0 | 12842.9084 |  | 0 | 12842.9084
Q130 | NY | SOL-10877 | 6870.1665 | 0 | 6870.1665 |  | 0 | 6870.1665 |  | 1. Many optimizers are offline on the SE portal, working with EPC to complete. | 1. SR095937
Q196 | NY | SOL-10879 | 8604.3925 | 0 | 8604.3925 |  | 0 | 8604.3925 |  | 1. Many optimizers are offline on the SE portal, working with EPC to complete. | 1. SR095938
Q220 | NY | SOL-10873 | 10122.7874 | 0 | 10122.7874 |  | 0 | 10122.7874 |  | 1. Many optimizers are offline on the SE portal, working with EPC to complete. 2. Weather station stopped communication at 17:00 on 02/22. | 1. SR095939
Q205 | NY | SOL-10922
Q400 | NY | SOL-10871 | 6925.4609 | 0 | 6925.4609 |  | 0 | 6925.4609 |  | 1. A few strings are offline. EPC to complete. 2. Inverter 2 tripped offline at 06:30 AM on 01/17 and back online at 11:00AM on 02/26. 3. Inverter 1 is underperforming by 20 kW from 02/04. | 1. SR095941 2. SR095940 3. SR095940 | SR095940 | SR095940
R003 | NY | SOL-10416 | 20656.6328 | [6 empty] | 1. Optimizers are offline, EPC to complete. | 1. SR095942
R007 | NY | SOL-10417 | 21665.457 | 0 | 21665.457 |  | 0 | 21665.457
BK16 | NY | SOL-11093 | 19771.3448 | 0 | 19771.3448 |  | 0 | 19771.3448 |  | 1. Multiple optimizers are offline. 2. Inverter 1 is underperforming by 21 kW from 02/19, possibly due to one unit tripping offline. | 1. SR095961 2. SR097620 | SR097620
Trenton - Trenton East | IL | SOL-11060 | 277433 | 272748.7 | 4684.3 | 1.717% | 250258 | 27175 | 10.86% | 1. Site tripped offline at 8:30 and later self resolved at 12:30 on 02/13. | 1. SR096931
Trenton - Trenton West | IL | SOL-11061 | 286335 | 245107.1 | 41227.9 | 16.82% | 252415.004 | 33919.996 | 13.44%
Dakota - Dakota Solar 1 | IL | SOL-11113 | 540549 | 358197.969 | 182351.031 | 50.91% | 0 | 540549 |  | 1. The site went offline at 1:30 PM on 02/27 due to a utility outage and came back online at 3:30 PM on the same day. 2. Tracker TCU 81 was stuck at 12.993 degrees with a set point of 14.276 degrees on 02/21. Later, all trackers became stuck at 0 degrees on 02/21. | 1.SR097882 2.SR097602 | SR097602
X018 | NY | SOL-10418 | 8177 | 11217.399 | -3040.399 | -27.1% | 0 | 8177 |  | 1. Inverter 2 isunderperforming compared to its peers and is reporting generic and device communication faults. 2. Low generation due to weather/snow. | 1.SR096257
Janiak Solar | NY | SOL-10898 | 206037.052 | 269225.697 | -63188.645 | -23.47% | 256159.246 | -50122.194 | -19.57% | 1.Low generation due to weather/snow.
County Route 11B | NY | SOL-10983 | 385858 | 0 | 385858 |  | 0 | 385858 |  | 1.Site was taken offline by CES on 02/12 at 14:55 and later back online at 11:10AM on 0/13 | 1.SR095492
Barone | NY | SOL-11034 | 359132 | 0 | 359132 |  | 314249.5 | 44882.5 | 14.28% | 1.Site was back online at 10:30AM on 02/01 after technician re-enerzing the site. 2.Site tripped offline at12:30PM on 02/16 due to relay opened later technician closed the relay at 11:55AM on 02/17 | 1.SR096195 2.SR097168 | SR097168
Cedarville | IL | SOL-11069 | 228799.9 | 250182.1 | -21382.2 | -8.547% | 248354.5 | -19554.6 | -7.874% | 1.Inverter 9 was offline on 02/14 and self resolved on 02/15 and again offline on 02/17 and later self resolved on 02/18 at 14:15 | 1.SR095797
O'Brien Hill #1 | NY | SOL-11098 | 416554 | 0 | 416554 |  | 0 | 416554
O'Brien Hill #2 | NY | SOL-11099 | 392818 | 0 | 392818 |  | 0 | 392818 |  | 1.Tracker T01 B27 stuck at -54 degrees are back to normal position from 02/19 | 1.SR095284
Trinity - Freeport | IL | SOL-11057
Ransom | NY | SOL-11157
Horseheads - Wedge | NY | SOL-11160
Otisville - Shoddy Hollow | NY | SOL-11185
Wellsville - Chenunda Creek | NY | SOL-11187
DC: Washington - Essex Condominium | DC | SOL-10036 | 2025 | 2433.958 | -408.958 | -16.8% | 2639.58 | -614.58 | -23.28% | 1.Low generation due to weather/snow.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 8933 | 9233.761 | -300.761 | -3.257% | 10227.1 | -1294.1 | -12.65%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 10740 | 8722.245 | 2017.755 | 23.13% | 10221.62 | 518.38 | 5.071%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Mar
Generate Capital |  |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  |  | 21280133.7171 | 7062289.49 | 14217844.2271 | 201.3% | 22138674.387 | -858540.6699 | -3.878% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 30245.625 | 32051.82 | -1806.195 | -5.635% | 24603.88 | 5641.745 | 22.93%
K041 | NY | SOL-10357 | 22872.6406 | 25521.62 | -2648.9794 | -10.38% | 22285 | 587.6406 | 2.637% | 1. Site production was low on 03/05, 03/15 to 03/17 due to bad weather.
K043 | NY | SOL-10358 | 26995.0625 | 28403.98 | -1408.9175 | -4.96% | 4961 | 22034.0625 | 444.1% | 1.Inverter 1 right unit has been derating since 02/23 due to a fan fault. The technician replaced the external fan on 03/26, and all units are producing in line. | 1.SR098810
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 18804 | -18804 | -100% | 1.SIte was offline from 02/21 due to Phase C fuse was blown and parts were needed. | 1.SR097569
K115 | NY | SOL-10361 | 5929.1797 | 10638.23 | -4709.0503 | -44.27% | 12280.17 | -6350.9903 | -51.72% | 1.96 optimizers are down for site construction. Need to investigate | 1.SR093291
K152 | NY | SOL-10362 | 8515.5938 | 8763.652 | -248.0583 | -2.831% | 7172 | 1343.5938 | 18.73%
K166 | NY | SOL-10363 | 30869.625 | 32488.02 | -1618.395 | -4.982% | 25933.76 | 4935.865 | 19.03%
K206 | NY | SOL-10927 | 17927.3023 | 18527.81 | -600.5077 | -3.241% | 15907 | 2020.3023 | 12.7%
K251 | NY | SOL-10365 | 19829.9375 | 0 | 19829.9375 |  | 16761.96 | 3067.9775 | 18.3% | 1.Wether station stopped communicating since 11/22/24. | 1.SR093633
K269 | NY | SOL-10366 | 18251.1875 | 21299.75 | -3048.5625 | -14.31% | 17272.78 | 978.4075 | 5.664% | 1. Site production was low on 03/05, 03/15 to 03/17 and 03/30 due to bad weather.
K273 | NY | SOL-10367 | 19471.3125 | 0 | 19471.3125 |  | 19892 | -420.6875 | -2.115% | 1.Weather station stopped communicating since 06/15/24. 2.26 optimizers are down for roof repair. 3.Inverter 2 left unit was offline on 03/24 due to DC Isolation fault and back online on 03/26. | 1.SR086842 2.SR093294 3.SR098958 | SR093294 | SR098958
K287 | NY | SOL-10919 | 15894.4375 | 14108.52 | 1785.9175 | 12.66% | 15141 | 753.4375 | 4.976%
K298 | NY | SOL-10368 | 16928.4688 | 18337.65 | -1409.1813 | -7.685% | 16617 | 311.4688 | 1.874% | 1.Site was offline from 11:30AM to 12:15PM on 03/21 due to technician checked-in. 2.Inverter 2 tripped offline and DC voltages dropped from 850V to 522V at 16:15 and back online at 17:30 on 03/31. | 1.SR098114, PM7943 2.SR099228 | SR099228
K335 | NY | SOL-10370 | 18093.6875 | 19835.33 | -1741.6425 | -8.781% | 16751 | 1342.6875 | 8.016%
K345 | NY | SOL-10920 | 21064.0312 | 13042.92 | 8021.1112 | 61.5% | 19934 | 1130.0312 | 5.669%
K445 | NY | SOL-10373 | 17147.2656 | 19226.17 | -2078.9044 | -10.81% | 15923.85 | 1223.4156 | 7.683% | 1. Site production was low on 03/05, 03/15 to 03/17 and 03/24 due to bad weather.
K495 | NY | SOL-10374 | 0 | 61161.43 | -61161.43 | -100% | 69499 | -69499 | -100% | 1.Due to shunt trips of the switchgear and overcurrent faults, the site has been offline since 11/20/2024. It came back online at 10:25 AM on 02/12 and again tripped offline at 05:25 PM on 02/13 till date. | 1.SR093196
M020 | NY | SOL-10380 | 18159.5 | 19883.75 | -1724.25 | -8.672% | 18985 | -825.5 | -4.348%
M092 | NY | SOL-10383 | 18077.375 | 19419.65 | -1342.275 | -6.912% | 17567.24 | 510.135 | 2.904%
M143 | NY | SOL-10384 | 21360.3125 | 23405.1 | -2044.7875 | -8.737% | 19950.93 | 1409.3825 | 7.064%
M144 | NY | SOL-10385 | 30927.9688 | 0 | 30927.9688 |  | 29347 | 1580.9688 | 5.387%
M167 | NY | SOL-10386 | 22510.7031 | 17030.17 | 5480.5331 | 32.18% | 23574.3 | -1063.5969 | -4.512%
M188 | NY | SOL-10387 | 15924.0938 | 0 | 15924.0938 |  | 15347 | 577.0938 | 3.76% | 1. Inverter 2's left unit on SolarEdge is offline and reporting a possible three-phase arc detection. 2. Inverter 1 was underperforming by 13 kW on 03/29, but after remotely resetting the inverter, it was back online on 03/31. | 1. SR099136 2. SR099136 | SR099136
EMHC | NY | SOL-10351 | 6079.1641 | 4893.405 | 1185.7591 | 24.23% | 6450.771 | -371.6069 | -5.761%
Q008 | NY | SOL-10397 | 18071.7812 | 19410.6 | -1338.8187 | -6.897% | 24376 | -6304.2188 | -25.86% | 1.The site is offline at 12:30 PM on 03/17 due to the AC breaker tripping. The technician reset the breaker, and the site came back online at 08:45 AM on 02/20. 2. The site is offline at 16:00 on 03/25 due to the main breaker tripping. The site will remain offline until the new main breaker is replaced. | 1. SR098734 2. SR098981 | SR098981
Q018 | NY | SOL-10398 | 17500.5625 | 17083.96 | 416.6025 | 2.439% | 13142.78 | 4357.7825 | 33.16%
Q021 | NY | SOL-10399 | 13787.4375 | 14154.27 | -366.8325 | -2.592% | 10812.43 | 2975.0075 | 27.51%
Q025 | NY | SOL-10400 | 23143.375 | 23053.17 | 90.205 | 0.3913% | 12738 | 10405.375 | 81.69%
Q074 | NY | SOL-10402 | 15292.875 | 14719.13 | 573.745 | 3.898% | 12449.42 | 2843.455 | 22.84%
Q115 | NY | SOL-10872 | 19693.25 | 20852.42 | -1159.17 | -5.559% | 16426.55 | 3266.7 | 19.89%
Q139 | NY | SOL-10403 | 11658.4375 | 11682.37 | -23.9325 | -0.2049% | 10385 | 1273.4375 | 12.26%
Q157 | NY | SOL-10404 | 20207.5625 | 22493.83 | -2286.2675 | -10.16% | 18648.05 | 1559.5125 | 8.363% | 1.Inverter 4 tripped offline at 07:00 AM on 03/16 due to an isolation fault and was back online at 07:00 AM on 03/17. 2. Inverter 2 is derating by 8 kW compared to its peers. On 03/18, a technician was onsite to investigate the underperformance of Inverter 2. After swapping strings between Inverter 1 and Inverter 2, Inverter 1 started producing, but Inverter 2 remained offline. It came back online at 10:30 AM on 03/20. The powerhead of the inverters has been RMA'd. | 1. SR096202 2. SR098365 | SR098365
Q192 | NY | SOL-10406 | 32225.375 | 34607.25 | -2381.875 | -6.883% | 27228.61 | 4996.765 | 18.35%
Q210 | NY | SOL-10407 | 26236.5 | 25645.07 | 591.43 | 2.306% | 22706 | 3530.5 | 15.55%
Q229 | NY | SOL-10408 | 11364.2812 | 12968.02 | -1603.7388 | -12.37% | 923 | 10441.2812 | 1131% | 1. Site production was low on 03/05, 03/15 to 03/17 due to bad weather.
Q231 | NY | SOL-10870 | 42833.5 | 45218.45 | -2384.95 | -5.274% | 40060 | 2773.5 | 6.923%
Q405 | NY | SOL-10409 | 49504 | 53188.06 | -3684.06 | -6.926% | 40273.41 | 9230.59 | 22.92%
Q435 | NY | SOL-10923 | 61922.625 | 48511 | 13411.625 | 27.65% | 57626 | 4296.625 | 7.456% | 1.Inverter 3 right unit has tripped offline between 11AM to 13:15 on 03/19, 03/22, 03/23 and 03/29 due to AC Voltage Too High (Line 3) fault. Inverter 3 middlie unit tripped offline between 13:15 to 14:00 on 03/01, 03/22 and 03/23 due to AC Voltage Too High (Line 3) fault. 2.Inverter 5 left unit tripped offline between 11Am to 16:00 on 03/01,03/08, 03/09 03/19,03/21, 03/22, 03/23, 03/25, 03/26, 03/28 and 03/29. 3.Inverter 1 left unit tripped offline at 15:00 on 03/23 and back online on 03/24. | 1.SR098781 2.SR098781 3.SR098905 | SR098781 | SR098905
Q485 | NY | SOL-10869 | 54507.75 | 46347.05 | 8160.7 | 17.61% | 53986.78 | 520.97 | 0.965% | 1.Inverter 1's right unit was offline on 03/07 due to low voltage. On 03/11, a technician was on-site and paired the strings individually to the unit's production at 11:15 AM. However, the unit went offline again on 03/13 and remained offline throughout the month. | 1. SR098312, SR099139 | SR099139
Q490 | NY | SOL-10411 | 41569.75 | 0 | 41569.75 |  | 35051.72 | 6518.03 | 18.6% | 1. optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. | 1. SR093326
Q620 | NY | SOL-10867 | 62270.25 | 62074.84 | 195.41 | 0.3148% | 56876.59 | 5393.66 | 9.483%
QMOA | NY | SOL-10415 | 5425.9 | 0 | 5425.9 |  | 5132.896 | 293.004 | 5.708%
X024 | NY | SOL-10419 | 23840.25 | 24902.66 | -1062.41 | -4.266% | 18167 | 5673.25 | 31.23%
X026 | NY | SOL-10420 | 20262.1 | 20134.12 | 127.98 | 0.6356% | 24639.36 | -4377.26 | -17.77% | 1. Site production was low on 03/05, 03/15 to 03/17 and 03/24 due to bad weather.
X090 | NY | SOL-10925 | 18244.25 | 14195.7 | 4048.55 | 28.52% | 17046 | 1198.25 | 7.03%
X117 | NY | SOL-10422 | 14903.1 | 16892.23 | -1989.13 | -11.78% | 13357.89 | 1545.21 | 11.57% | 1. Site production was low on 03/05, 03/15 to 03/17 and 03/24 due to bad weather.
X125 | NY | SOL-10423 | 27866.1875 | 29401.67 | -1535.4825 | -5.222% | 25413.95 | 2452.2375 | 9.649%
X134 | NY | SOL-10424 | 26652 | 0 | 26652 |  | 26095 | 557 | 2.135%
X135 | NY | SOL-10425 | 20342.2188 | 22903.47 | -2561.2513 | -11.18% | 20962 | -619.7812 | -2.957% | 1.Inverters were offline on 03/27 due to Grid voltage unbalance and were back online at 12:30 on 03/28 | 1.SR099036
X139 JHS 222 | NY | SOL-10426 | 33468.3213 | 35713.1 | -2244.7787 | -6.286% | 30257 | 3211.3213 | 10.61%
X140 | NY | SOL-10926 | 16923.2969 | 15830.34 | 1092.9569 | 6.904% | 17584 | -660.7031 | -3.757% | 1.Right unit of inverter 3 is reporting low voltage from 02/28/25 due to Fuse blown in inverter, will replace with spares once received. | 1.SR098313
X166 | NY | SOL-10427 | 20069.5 | 20878.42 | -808.92 | -3.874% | 19078 | 991.5 | 5.197%
Murphy | MN | SOL-10094 | 894400 | 930300.6 | -35900.6 | -3.859% | 809101.4 | 85298.6 | 10.54% | 1. Inverter 3 tripped offline at 9:00 AM on 03/26. On 03/28, a technician investigated and found a broken module causing the GFI to trip. He removed and bypassed it, restoring power at 12:45 PM the same day. | 1. SR099002
Terning | MN | SOL-10093 | 847404.795 | 939875.7 | -92470.905 | -9.839% | 792912.7 | 54492.095 | 6.872% | 1. Inverter 4 stopped communicating at 9:00 AM on 03/05 and was offline according to meter data. It came back online at 9:15 AM on 03/09 after PE reset the faults. 2. Inverter 1 tripped offline on 03/26, 03/27, and 03/28, self-resolving by the end of each day. However, on 03/28, it tripped again after resolving and remained offline for the rest of the month. Hunt MV Crew investigation is required. | 1. SR098155 2. SR098987 | SR098987
Boas Road 04 | NY | SOL-10908 | 142690 | 300105.541 | -157415.541 | -52.45% | 301351.8 | -158661.8 | -52.65% | 1. Inverters 1 and 2 are started late for the production at 2:55PM on 03/29. 2. Meter stopped communicating from 2:05PM on 03/17. | 1. SR099130 2. SR098641 | SR098641
Kelly Bridge Farm | NY | SOL-10911 | 158244 | 324553.713 | -166309.713 | -51.24% | 306228.1 | -147984.1 | -48.32% | 1. Inverter 20 tripped offline at 2:20PM on 03/07. On 03/26 technician replaced fues and prodction back at 10:25AM. 2. Inverter 28 tripped offline at 10:45AM and back online at 1:10PM after technician replaced blown fuse on 03/18. 3. Site tripped offline at 8:00AM due to utility outgae and back online at 9:35AM on 03/21. 4. Inverters 7,10 tripped offline at 15:00 on 03/22. On 03/25 technician replaced fuses for both inverters and production was back at 03:25PM. 5.The meter stopped communicating at 14:05 on 03/16. On 03/26, the technician investigated the issue, checked the fuses, tested the watch battery on the board, and will process the meter board RMA on the next visit. | 1. SR098279 2. SR098699 3. SR098853 4. SR098892 | SR098699 | SR098853 | SR098892
Pool Brook Road | NY | SOL-10909 | 284618 | 298602.119 | -13984.119 | -4.683% | 259081.23 | 25536.77 | 9.857%
Sackett Lake | NY | SOL-10910 | 314608 | 327404.692 | -12796.692 | -3.909% | 308336.22 | 6271.78 | 2.034% | 1. Inverter 2 tripped offline at 9:45 AM on 03/30 due to "FAULT PHASE 3" and "VBUS DERIVATE FAULT." On 03/31, a technician swapped the CCU, but the fault persisted, requiring a stack replacement. Inverter 2 remains offline until the stack is received. | 1. SR099149
Burritt Road | NY | SOL-10913 | 244160 | 0 | 244160 |  | 262360.5 | -18200.5 | -6.937% | 1.POA Pyranometer is not communicating from 07:00AM on 11/09/24 due to a malfunctioning NPort, where the POA and GHI are connected. 2. Inverters 1 to 5 tripped offline at 10:05 AM on 03/18 and came back online at 16:30 on 03/19 after resetting the switchgear. However, they tripped again on 03/20 and came back online at the end of the day on 03/21. On 03/22, the inverters tripped again and were back online on 03/27 after troubleshooting. On 03/31, the inverters tripped offline again, and technician found a malfunctioning breaker that needs to be replaced and inverters remains offline. 3. The site was taken offline on 03/21 from 2:15 PM to 3:40 PM and on 03/27 from 11:10 AM to 2:50 PM and from 4:10 PM to 5:10 PM due to a technician being onsite on both days to investigate inverters 1 to 5. | 1. SR093972 2. SR098708 3. SR098708 | SR098708 | SR098708
Villa Roma 1 | NY | SOL-10914 | 292460 | 795.601 | 291664.399 | 36660% | 230513.34 | 61946.66 | 26.87% | 1. On 03/20, technician was onsite for a PM inspection, and the site was de-energized from 12:25 PM to 1:00 PM. Additionally, the technician replaced a string fuse for Combiner Box 7. 2. Expected energy values are reporting very low. Created a case #66639 with GPM | 1. PM7628, SR098869 2.SR099403 | SR099403
Villa Roma 2 | NY | SOL-10915 | 282446 | 290530.561 | -8084.561 | -2.783% | 223617.6 | 58828.4 | 26.31% | 1. On 03/27 technician was onsite for PM inspection and site was taken offline from 11:45AM to 12:45PM. | 1. PM7642
Washington 1 | NY | SOL-10912 | 284470 | 297807.874 | -13337.874 | -4.479% | 258096.13 | 26373.87 | 10.22%
Washington 3 | NY | SOL-10828 | 342949 | 0 | 342949 |  | 317573.3 | 25375.7 | 7.991% | 1. POA sensor continues to read inaccurately. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. 2. The site was offline from 10:00AM to 3:45PM due to medium voltage work. | 1. SR093024 2. SR098551 | SR098551
Washington 4 | NY | SOL-10829 | 343118 | 355062.712 | -11944.712 | -3.364% | 316864.2 | 26253.8 | 8.286%
Big Tree | NY | SOL-10966 | 273687 | 0 | 273687 |  | 288104.5 | -14417.5 | -5.004% | 1. Inverters 1 and 2 experienced multiple tripping events from 10:45 to 14:30 on 03/18 due to technician was onsite for PM work. | 1. PM7676
Canoga | NY | SOL-10965 | 596020 | 0 | 596020 |  | 721909.99 | -125889.99 | -17.44% | 1.On 03/04, inverters 1 and 2 experienced tripping events from 9:30 to 15:20, and on 03/05, inverter 2 experienced tripping from 8:05 AM to 10:35 AM due to technicians being onsite for Ingeteam field-based training. 2. Weather station has reported 0 since 8/21. New UP POA and Down POA need replacement. 3. Inverters 1 and 4 experienced derating of approximately 260 kW on 03/11. On 03/21, technician replaced the power stack unit for phase S of inverter 4. The output was compared to sister inverter 3, and both were producing the same. Both inverters have returned to normal production. 4. On 03/14, inverter 4 was offline from 12:05 PM to 1:05 PM. On 03/18, inverter 4 went offline at 9:05 AM, and inverter 3 went offline at 10:20 AM; both came back online at 1:50 PM on the same day. However, on 03/21, inverter 3 was offline from 11:20 AM to 2:00 PM. These offline events occurred because technician was onsite working on the Inverter 1 and 4 derating issue. 5. The site tripped offline at 9:45 AM on 03/26 due to a utility outage and came back online at 11:35 AM. However, it tripped offline again at 9:55 AM on 03/27 due to utility work at the substation and has remained offline throughout the month. No ETA has been provided. | 1. SR096004, SR098071 2. SR094278 3. SR098510 4. SR098510 5. SR098998 | SR098071 | SR094278 | SR098510 | SR098510 | SR098998
County Route 84 | NY | SOL-10967 | 765110 | 0 | 765110 |  | 801935.5 | -36825.5 | -4.592% | 1. Site tripped offline at 9:20 AM on 03/13 due to utility work and came back online at 9:30 AM on 03/14 after utility power was restored. | 1. SR098500
Donati | NY | SOL-10968 | 126381 | 0 | 126381 |  | 341064.1 | -214683.1 | -62.95% | 1. Weather station Reporting 0 value from 05/31/24. POA sensors need to be replaced. 2. All trackers have been struck from various dates. Followed up with Soltec and they are working on it. 3. Site tripped offline at 4:35PM on 03/13 due to utility work and came back online at 11:50AM on 03/26 after utility power was restored. 4. Site tripped offline at 1:30 PM due to utility work and came back online at 2:20pm on 03/27 after utility power was restored. | 1. SR092964 2. SR097603, SR095253 3. SR098558 4. SR099047, SR099053 | SR097603 | SR095253 | SR098558 | SR099047 | SR099053
Henrietta | NY | SOL-10972 | 657820 | 0 | 657820 |  | 670835.98 | -13015.98 | -1.94%
NY 70 | NY | SOL-10970 | 692500 | 0 | 692500 |  | 842989.16 | -150489.16 | -17.85% | 1. All trackers lost communication on 02/27. On 03/17, the technician reset a UPS fault and restored tracking, but T01.A.19, D.15, and T02.D.31 remain stuck. Further investigation is needed next visit. 2. On 03/21 inverter 3 was offline from 2:40PM to 3:40PM due to technician was onsite for a PM inspection 3. Site tripped offline at 8:30AM on 03/26 due to utility outage and back online at 1:00PM on the same day after utility power restored. | 1. SR096238, SR097926 2. PM7743 3. SR098992 | SR097926 | SR098992
Reid | NY | SOL-10991 | 598905.0006 | 628321.1 | -29416.0994 | -4.682% | 657607 | -58701.9994 | -8.927% | 1. Inverter 5 has been offline since 02/28 due to a "Grid Line Voltage Out of Range" error. On 03/06, the technician turned on the breaker, restoring inverter production at 9:30 AM. 2. Inverter 9 tripped offline at 9:30AM on 03/03 due to "Grid Line Voltage Out of Range". On 03/06 breaker was reset and inverter back online at 9:30AM. 3. Inverter 23 has been offline since 11/19 due to a "Grid Line Voltage Out of Range" error. On 03/06, breaker was reset and inverter back online at 9:30AM. 4. Inverter 4 didn't started on 03/08. On 03/25 technician replaced powerhead and inverter back online at 11:30AM. 5. Inverter 18 tripped offline at 14:00 on 03/10 due to Bus Imbalance fault. On 03/25 technician replaced powerhead and inverter back online at 11:30AM. 6. Inverter 28 tripped offline at 14:00 on 03/11 due to " Grid Phase Voltage Out of Range". On 03/12 breaker was reset and inverter back online at 9:15AM on 03/12. 7. Inverter 24 was derating by 50kW since 03/10. On o3/25 technician replaced fan and inverter back to normal production. 8. Inverter 30 tripped offline at 14:30 on 03/14. On 03/17 breaker was reset and inverter back online at 15:15. 9. Inverter 32 tripped offline at 14:35 on 03/19. On 03/25 breaker was reset and inverter back online at 9:45AM. 10. inverter 05 tripped offline at 14:35 on 03/23. On 03/25 breaker was reset and inverter back online at 11:15AM. | 1. SR097930 2. SR098005 3. SR093436 4. SR098295 5. SR098354 6. SR098414 7. SR098415 8. SR098594 9. SR098779 10.SR098902 | SR098005 | SR093436 | SR098295 | SR098354 | SR098414 | SR098415 | SR098594 | SR098779 | SR098902
Sangolqui | NY | SOL-10975 | 304250 | 0 | 304250 |  | 332621.63 | -28371.63 | -8.53% | 1. Inverter 1 tripped offline at 9:15AM on 03/05 due to Isolation fault and self resolved resumed production on 03/06. 2. Inverter 1 tripped offline at 4:40PM on 03/16 due to Low voltage fault and self resolved resumed production on 03/17. 3. Inverter 1 tripped offline at 3:20PM on 03/22 due to Insulation fault and later it was back online at 4:55PM after remotely reset by Ingeteam. 4. Site had a brief utility outage between 1:30PM to 2:20PM on 03/27. 5. Inverter 1 did not start on 03/29. On 03/30, the technician cleared the ground fault, but the inverter experienced tripping events throughout the day. It came back online at 9:45 AM on 03/31. | 1. SR097883 2. SR098644 3. SR098891 4. SR099054 5. SR099129 | SR098644 | SR098891 | SR099054 | SR099129
State Highway 17B | NY | SOL-10988 | 720970 | 0 | 720970 |  | 638001.97 | 82968.03 | 13% | 1. Inverter 4 tripped offline at 9:11AM and self resolved at 9:20AM on 03/14. | 1. SR098570
State Route 14A | NY | SOL-10997 | 738375 | 0 | 738375 |  | 723566.05 | 14808.95 | 2.047%
West Creek | NY | SOL-10995 | 783200 | 0 | 783200 |  | 745081.94 | 38118.06 | 5.116%
Wildflower | NY | SOL-10982 | 617179 | 0 | 617179 |  | 744170.26 | -126991.26 | -17.06% | 1. Inverter 1 tripped offline at 7:40AM on 03/03 and inverter 2 didn't started for production. On 03/03 technician installed fuses and parts and both inverters production was back at 3:30 PM. 2. Inverters 1 and 2 did not start production on 03/10 due to an insulation fault. On 03/11, inverter 1 self-resolved but went offline again at 11:55 AM, then self-resolved at 5:00 PM, while inverter 2 remained offline. On 03/12, inverter 1 went offline again. On 03/13, the technician replaced fuses for both inverters, restoring them at 2:15 PM. | 1. SR097526 2. SR098462 | SR098462
Glen Mary 1 | NY | SOL-10993 | 788220 | 0 | 788220 |  | 769129.73 | 19090.27 | 2.482%
Glen Mary 2 | NY | SOL-10994 | 347560 | 0 | 347560 |  | 324262.76 | 23297.24 | 7.185%
Telegraph 1 | NY | SOL-11003 | 566859 | 0 | 566859 |  | 528951.26 | 37907.74 | 7.167% | 1. Site tripped offline from 08:40AM on 03/26 due to utility outage and back online at 1:00PM after utility restores power. 2. Site tripped offline at 03:15pm due to utility outage on 03/16 and back online at 04:25am on 03/17 after utility power restored. | 1. SR098994 2. SR098630 | SR098630
Telegraph 2 | NY | SOL-11004 | 298925 | 0 | 298925 |  | 274538.3 | 24386.7 | 8.883% | 1. Site lost communication at 1:40PM on 03/06 and regained at 12:00AM on 03/07. 2. Site tripped offline at 03:15pm due to utility outage on 03/16 and back online at 04:25am on 03/17 after utility power restored. 3. Site tripped offline from 08:40AM on 03/26 due to utility outage and back online at 1:00PM after utility restores power. | 1. SR098222 2. SR098632 3. SR098995 | SR098632 | SR098995
Cafferty Hill | NY | SOL-10996 | 765350 | 0 | 765350 |  | 688149.3 | 77200.7 | 11.22% | 1. Inverter 2 was offline between 12:30PM to 1:05PM due to technician was onsite for PM inspection. 2. Site had a brief utility outage between 5:40PM to 6:45PM on 03/18. | 1. PM6987 2. SR098731
Dunkleman | NY | SOL-11008 | 739710 | 0 | 739710 |  | 879842.6 | -140132.6 | -15.93% | 1. 13 trackers are stuck, with 1 tracker having no communication. 11 trackers are disabled due to no movement, likely caused by snow, and 1 is in e-stop. Investigation needed. 2. Meter and relay voltages stopped communicating at 2:00 AM, and inverter voltages dropped to zero at 12:10 AM on 03/11, reporting a "SMOKE DETECTOR FAULT." On 03/12, the technician found the recloser in the open position and closed it. The site came back online at 4:40 PM | 1. SR095109 2. SR098366 | SR098366
Route 19 1 | NY | SOL-11001 | 346210 | 0 | 346210 |  | 349283.18 | -3073.18 | -0.8799% | 1. Site lost communication at 3:05PM possibly offline on 03/16. The site back online at 10:30AM on 03/17. 2. Site lost communication at 8:30AM possibly offline on 03/26. The site back online at 1:05PM after utility restores power. | 1. SR098629 2. SR098996 | SR098996
Route 19 2 | NY | SOL-11002 | 835500 | 0 | 835500 |  | 874096.22 | -38596.22 | -4.416% | 1. Site tripped offline at 3:15PM on 03/16 due to utility outage and back online at 10:25AM after utility restores power. 2. Site tripped offline at 8:30AM due to utility outage and back online at 1:05PM on 03/26. | 1. SR098631 2. SR098997 | SR098997
Yellow Mills 1 | NY | SOL-11006 | 173566 | 0 | 173566 |  | 290227.42 | -116661.42 | -40.2% | 1. Site was offline since 01/29, on 03/06 technician installed new PT board and site back online at 4:05PM. 2. Site was offline on 03/07, and back online at 6:25PM on 03/11 after technician troubleshooted. 3. Site tripped offline at 3:50AM and restored at 5:05PM on 03/16. On 03/17 technician found site was online an producing but no communication. After a powercycle communications were restored at 6:25AM. | 1. SR097854 2. SR098349 3. SR098635 | SR098349 | SR098635
Yellow Mills 2 | NY | SOL-11005 | 307599 | 0 | 307599 |  | 300328.5 | 7270.5 | 2.421% | 1. Site tripped offline at 3:50PM and restored at 5:05PM on 03/16. On 03/17 technician found site was online an producing but no communication. After a powercycle communications were restored at 6:25AM. | 1. SR098636
Yellow Mills 3 | NY | SOL-11007 | 280998 | 0 | 280998 |  | 278412.03 | 2585.97 | 0.9288% | 1. On 03/03, the site was offline from 11:10 AM to 3:40 PM as the technician was onsite replacing PL and PD boards for the inverter. 2. Site tripped offline at 3:50PM and restored at 5:05PM on 03/16. On 03/17 technician found site was online an producing but no communication. After a powercycle communications were restored at 6:25AM. | 1. SR097829 2. SR098637 | SR098637
Catskill | NY | SOL-11021 | 521640 | 0 | 521640 |  | 536089.1 | -14449.1 | -2.695% | 1. Site was tripped offline at 17:55 on 03/16 due to MV switchgear door open and the latch bent the technician corrected the bent latch and closed the site back in at 09:40am on 03/19. 2. The site was taken offline on 03/21 at 01:45 AM. Later, a technician found that the MV switch had tripped open. The technician closed the switch, and the site was re-energized at 16:31 on 03/21. | 1. SR098643 2. SR098841 | SR098841
Eddy Ridge | NY | SOL-11054 | 378194.1 | 0 | 378194.1 |  | 410935 | -32740.9 | -7.967%
Ridgeway #1 | NY | SOL-11018 | 822442 | 0 | 822442 |  | 876074.3 | -53632.3 | -6.122%
Rivard 1 | NY | SOL-11011 | 621057 | 665956.3 | -44899.3 | -6.742% | 649817.4 | -28760.4 | -4.426% | 1. Site was tripped offline at 11:15 on 03/24 , Upon tech arrival on same day stated that recloser was open and was able to close the recloser by target reset and brought back online at 18:00 on 03/24 | 1.SR098930
Rivard 2 | NY | SOL-11012 | 630307.9104 | 622072.8 | 8235.1104 | 1.324% | 625090.8 | 5217.1104 | 0.8346% | 1.Tracker control 33 - 90, 129 - 136, 148 , 20-32, 123-128, 172-183 are not communicating & tracker 156 , 121 is stuck and production dropped (approxmately ) 25 KW down. | 1.SR095073
Ridgeway #2 | NY | SOL-11027 | 377170 | 0 | 377170 |  | 447116.81 | -69946.81 | -15.64% | 1.12 trackers are stuck: 13, 20, 25, 52, 54, 56, 59, 70, 72, 76, 85, and 88. EV Solar troubleshot the trackers and confirmed they are operating as expected since 03/24 | 1.SR097436 , SR097751 | SR097751
Spencer | NY | SOL-11017 | 806445 | 0 | 806445 |  | 821870 | -15425 | -1.877% | 1. Trackers 141 and 147 have resolved, but 138 still struck. GenC says to hold on dispatch 2.Inverter 2 tripped offline at 12:50 on 03/12 with no alarm codes. Technician troubleshot Inverter 2, and it came back online at 12:35 on 03/13. | 1.SR095821 2.SR098459 | SR098459
Reisender | NY | SOL-10886 | 306480 | 313723.489 | -7243.489 | -2.309% | 317126.86 | -10646.86 | -3.357%
Finney | NY | SOL-10999 | 746680 | 0 | 746680 |  | 907159.04 | -160479.04 | -17.69% | 1. All trackers are stuck and are reporting an encoder feedback error. On 03/27 technician installing the down drive shafts and calibrating the motors, all trackers are tracking from 03/27 2.Site was taken offline from 08:25 to 09:16 on 03/14 by USNE due to transformer work. | 1.SR098259 2. SR098259 | SR098259
Davis Solar | NY | SOL-10958 | 313814 | 348972.2 | -35158.2 | -10.07% | 368855 | -55041 | -14.92% | 1.Inverter offline on 03/15 from 07:00 to 11:00. Inverter is back online by remote reset. Inverter tripped offline on 03/16 at 13:30. After remote reset inverter back online on 03/17. Inverter tripped offline at 15:15 on 03/18 and reporting "STOP".After remote reset inverter back online at 18:15 on same day. Inverter tripped offline at 17:00 on 03/20 and reporting "Stop'.Inverter back online on 03/21 Inverter tripped offline from 13:00 to 14:15 on 03/22 and reporting "STOP". After remote reset inverter back online on same day Inverter tripped offline at 17:30 and reporting "STOP" on 03/23. After remote reset inverter back online on 03/24 Inverter offline from 14:15 to 15:00 on 03/25. After remote reset inverter back online same day Inverter tripped offline from 10:45 to 11:45 03/26. After remote reset back online on same day | 1. SR098612
Genesee | NY | SOL-10951 | 428631.1 | 0 | 428631.1 |  | 636841.14 | -208210.04 | -32.69% | 1.Inverter 2 back online from 03/12 after replacing the fuse. 2.Site went offline at 16:00 on 03/22. On 03/23, technician was able to close the recloser, and the site came back online at 10:25 AM. 3.Inverter 1 tripped offline at 13:10 on 03/23 due to the AC breaker switch being in the open state and reporting a 'Ground Fault.' On 03/24, technician closed the breaker, and the inverter came back online at 14:00 4.CB 19 offline from 02/15 and CB 6 are offline from 03/07. Isolated and removed damaged materials. Stored hardware in storage container. Flexrack to RMA or quote replacement parts. | 1. SR097565 2.SR098893 3.SR098901 4.SR098959 | SR098893 | SR098901 | SR098959
Landau I | NY | SOL-10891 | 311080 | 0 | 311080 |  | 354234.71 | -43154.71 | -12.18%
Landau II | NY | SOL-10895 | 439890 | 0 | 439890 |  | 764399.74 | -324509.74 | -42.45% | 1.Inverter 2 offline due to insulation failure from 07:10 to 08:15 on 03/06. Able to reset remotely, inverter in operation. 2.Inverters tripped offline from 12:30 to 14:45 on 03/07. Inverters are back online remote reset on same day 3.Inverter 1 tripped offline at 14:15 PM on 03/13, reporting 'AC breaker switch open.' On 03/14, after a remote reset, the inverter started production again. However, it tripped offline multiple times on 03/14 and came back online at 16:25 on 03/17. Inverter 1 again offline on 03/20,03/23 back online on 03/24. Again iverter tripped offline from 10:30 to 15:55 on 03/28 technician troubleshooting it was determined the canbus cable is what needed to be replaced and further troubleshooting is needed. The inveter 1 is currently back online on sam eday. 3. Inverter 2 tripped offline at 11:35 AM and reporting "Isolation error" and AC breaker switch is in open state. After remote reset inverter back online at 15:30 on 03/17. Again inverter 2 offline at 09:55 from 03/25 | 1.SR098196 2.SR098275 , SR098655 3.SR098626 | SR098275 | SR098655 | SR098626
New Beginnings | NY | SOL-10890 | 323110 | 335667.993 | -12557.993 | -3.741% | 334299.71 | -11189.71 | -3.347%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 725711 | 799215.324 | -73504.324 | -9.197% | 853019.18 | -127308.18 | -14.92% | 1. Site production was low on 03/05, 03/16, 03/17, 03/29 and 03/30 due to bad weather.
Brodhead Solar, LLC | NY | SOL-10899 | 357970 | 382903.054 | -24933.054 | -6.512% | 395846.83 | -37876.83 | -9.569% | 1. NCU 2 tracker 1 stuck since 11/19 and tracker 35 stuck at 11:45 since 01/31 2. NCU 1 tracker 10 stuck at 09:15 since 02/23. | 1. SR095624 2.SR097725 | SR097725
Svenski | NY | SOL-10894 | 311430 | 0 | 311430 |  | 352038.56 | -40608.56 | -11.54% | 1. Site production was low on 03/05, 03/16, 03/17 and 03/30 due to bad weather.
Bantam | NY | SOL-10986 | 709630 | 0 | 709630 |  | 887808 | -178178 | -20.07% | 1.POA 1 is not accurately reporting - technician need to visit for further troubleshooting. 2. Inverter 2 tripped offline at 07:40 AM on 03/04 and was reporting an insulation error. The technician found that the inverter's auxiliary switch had tripped, and after resetting the switch, the inverter was back online at 10:40 AM on 03/06. 3.All trackers were stopped between -56.93 degrees and -60.7 degrees on 03/20 due to very high winds on-site. After the technician was on-site, it was reported that they were in 'stow mode' due to the heavy wind, which caused all trackers to lock in snow mode. The trackers will resume tracking once the wind ends. POA 1 is not accurately reporting - technician need to visit for further troubleshooting 4. currently 7 additional stuck trackers. the techs found a motor that may be binding, and it requires a motor testing tool. | 1. SR096042 2. SR098021 3. SR098809 4. SR096682 | SR098021 | SR098809 | SR096682
Bogart | NY | SOL-10887 | 315720 | 315255.319 | 464.681 | 0.1474% | 333711.4 | -17991.4 | -5.391% | 1.Combiner boxes 1.12 and 1.13 have been underperforming since 01/27, with an approximate loss of 79 kW. Will investigate during the next onsite visit. | 1. SR096006
Dubois | NY | SOL-10892 | 327643.21 | 0 | 327643.21
Salt Point | NY | SOL-10888 | 316940 | 0 | 316940 |  | 346868.17 | -29928.17 | -8.628% | 1. Trackers- NCU 1 SPC 103 through 115 were stucked from 03/18. ON 03/19, technician checked in and found that TCU breaker tripped and also found broken panel which is need to be replaced. Created a ticket and Further Trouble Shooting required. | 1.SR098692
Wheatland 2A | NY | SOL-10971 | 678330 | 0 | 678330 |  | 717427.66 | -39097.66 | -5.45% | 1.SIte tripped offline at 14:20 on 03/16 and back online at 12PM on 03/17 after technician closed relay and re-energize the site. 2.12 trackers were stuck due to actuator issues on different days from 01/06; NCU 1 self-resolved on 03/04, and on 03/07, the technician power cycled NCU 2, cleared the fault light, and notified Slater, but 12 rows still need troubleshooting. On 03/19, technician was unable to perform troubleshooting the trackers due to not getting access to connect with NCU and created a case with the manufacturer and further troubleshooting is required with NEXTracker. | 1.SR098627 2.SR094820 | SR094820
Wheatland 2B | NY | SOL-10961 | 646300 | 0 | 646300 |  | 710713.62 | -64413.62 | -9.063% | 1.Site was offline from 14:20 to 16:20 on 03/16. 2.Inverter 1 tripped offline at 11:10AM on 03/22 due to AC breaker switch open and back online at 14:40 on 03/23 after technician closed the breaker. Again tripped offline at 13:00 on 03/24 due to "GFDI Tripped" and back online at 11:10AM on 03/25 after technician isolated ground fault and reset breaker. 3.Combiner box 1.6(1.6 as per GPM plus 2.6 as per GPM portal) has tripped offline from 03/25 till date. 4. Around 50-60% of the site was not tracking since 01/06. On 03/07 technician checked in and power cycled NCU 1, restoring most rows. NCU 1’s door was found broken nearby. Zip ties were used as a temporary fix, but a proper repair is needed to prevent water damage. | 1.SR098628 2.SR098888, SR098955 3.SR099024 4.SR095759 | SR098888 | SR098955 | SR099024 | SR095759
Brickchurch | NY | SOL-10889 | 279160 | 272209.648 | 6950.352 | 2.553% | 284745.5 | -5585.5 | -1.962% | 1.All NCU 2 trackers have lost communication, while NCU 1 trackers 115-127 remain stuck from 03/27. Previous stuck trackers included 18 on 03/24 and specific units on 03/17. | 1.SR097454, SR099118 | SR099118
McCarthy Solar | NY | SOL-10992 | 331190 | 0 | 331190 |  | 331631.3 | -441.3 | -0.1331%
Costanza | NY | SOL-10907 | 327210 | 0 | 327210 |  | 356619.2 | -29409.2 | -8.247% | 1.Site tripped offline at 12:54PM on 03/16 due to utility outage and back online after technician closed relay at 08:52AM on 03/17. | 1.SR098624
Lockenhurst Pond | NY | SOL-11000 | 363202 | 392130.7 | -28928.7 | -7.377% | 349576 | 13626 | 3.898%
Drinkwater | NY | SOL-10896 | 330170 | 0 | 330170 |  | 343578.1 | -13408.1 | -3.902%
Altamont | NY | SOL-11085 | 679998 | 718428.2 | -38430.2 | -5.349% | 594010.6 | 85987.4 | 14.48% | 1.Inverter 2.21 is derating by 17KW down from 01/27 by comparing to its peers and awaiting for the response. | 1. SR098733
Krumkill North | NY | SOL-11086 | 600802 | 680752 | -79950 | -11.74% | 686018.1 | -85216.1 | -12.42% | 1. Site production was low on 03/05, 03/16, 03/17, 03/24 and 03/30 due to bad weather.
Krumkill South | NY | SOL-11087 | 522344 | 540569.7 | -18225.7 | -3.372% | 537817.5 | -15473.5 | -2.877%
X092 | NY | SOL-11189 | 15832.4 | 15885.47 | -53.07 | -0.3341% | 16758 | -925.6 | -5.523%
X093 | NY | SOL-10932 | 5362.8212 | 0 | 5362.8212 |  | 11061 | -5698.1788 | -51.52% | 1. Many optimizers on SE are offline, EPC to complete. 2. Inverter 2 tripped offline at 13:15 on 03/10 and dispatch has been holded due to EPC to complete. 3. The site went offline at 13:15 on 03/18 and remained down throughout the month, awaiting for EPC to address. | 1.SR095945 2.SR097637 3.SR098724 | SR097637 | SR098724
X095 | NY | SOL-10929 | 12809.3174 | 0 | 12809.3174 |  | 15084 | -2274.6826 | -15.08% | 1. Optimizers on SE are offline, EPC to complete. 2.Inverter 1 right unit was offline from 02/10/25. | 1.SR095946 2.SR098988 | SR098988
X181 | NY | SOL-10428 | 29508.9875 | 0 | 29508.9875 |  | 27420 | 2088.9875 | 7.618% | 1. Optimizers are offline, EPC to complete. | 1.SR095948
X415 | NY | SOL-10429 | 17466.5605 | 0 | 17466.5605 |  | 15528 | 1938.5605 | 12.48% | 1. Optimizers are offline, EPC to troubleshoot. | 1.SR095950
K198 | NY | SOL-10930 | 14187.0566 | 0 | 14187.0566 |  | 12752 | 1435.0566 | 11.25% | 1. Multiple optimizers are offline. | 1.SR095962
K203 | NY | SOL-11190 | 13616 | 0 | 13616 |  | 0 | 13616 |  | 1. Multiple optimizers are offline. 2. Actual energy value was taken from solaredge as site not configured in Also Energy. | 1.SR095954
K213 | NY | SOL-11191 | 19107.2 | 20224.73 | -1117.53 | -5.526% | 18782 | 325.2 | 1.731% | 1.Modules 7.2,1-7.2.8, 7.2.13-7.2.16, 2.4.11, and 3.1.15 are offline (64 modules) . 2. Site tripped offline at 08:30AM and back online at 09:00AM on 03/13. | 1.SR095951
K217 | NY | SOL-10933 | 10504.9746 | 0 | 10504.9746 |  | 9298 | 1206.9746 | 12.98% | 1. Multiple optimizers are offline. | 1.SR095960
K307 | NY | SOL-10876 | 22224.3597 | 0 | 22224.3597 |  | 19546 | 2678.3597 | 13.7%
K610 | NY | SOL-11158 | 25056.5 | 24720.24 | 336.26 | 1.36% | 24582 | 474.5 | 1.93%
M025 | NY | SOL-10392 | 8008.9453 | 0 | 8008.9453 |  | 21500 | -13491.0547 | -62.75% | 1.Inverter 1 has tripped offline at 13:30 on 03/06 and reporting "Fault" and continued throught the month. 2. Inverter 3 has tripped offline at 12:15 on 03/07 and reporting a "Generic Fault" and continued throught the month. 3.Multiple optimizers are offline. | 1.SR098235 2.SR098264 3.SR095956 | SR098264 | SR095956
M028 | NY | SOL-10381 | 17546.9861 | 0 | 17546.9861 |  | 15744 | 1802.9861 | 11.45% | 1. Appears no optimizers are connected. | 1.SR095955
Q030 | NY | SOL-10878 | 21809.5741 | 0 | 21809.5741 |  | 19517 | 2292.5741 | 11.75%
Q130 | NY | SOL-10877 | 12271.6041 | 0 | 12271.6041 |  | 10779.37 | 1492.2341 | 13.84% | 1. Many optimizers are offline on the SE portal, working with EPC to complete. | 1.SR095937
Q196 | NY | SOL-10879 | 15423.1352 | 0 | 15423.1352 |  | 14155 | 1268.1352 | 8.959% | 1. Many optimizers are offline on the SE portal, working with EPC to complete. | 1.SR095938
Q220 | NY | SOL-10873 | 18632.9177 | 0 | 18632.9177 |  | 15807 | 2825.9177 | 17.88% | 1. Many optimizers are offline on the SE portal, working with EPC to complete. 2. Weather station stopped communication at 17:00 on 02/22. | 1.SR095939
Q205 | NY | SOL-10922 | 22716.957 | 25173.09 | -2456.133 | -9.757% | 19352 | 3364.957 | 17.39% | 1. Inverters 1 and 2 underperformed 16 kW down on 03/23, Possibly one of the unit tripped offline. Site visibility not available in SolarEdge.and later self resolved on 02/24. | 1.SR098903
Q400 | NY | SOL-10871 | 24511.8867 | 0 | 24511.8867 |  | 30789 | -6277.1133 | -20.39% | 1. A few strings are offline. EPC to complete. 2.Inverter 1 is are underperforming by 20 kW from 02/04. 3.Inverter 2 was tripped offline at 10:45 on 03/01 and back online at 09:00 on 03/03 4.Inverter 3 tripped offline at 14:45 on 03/12 and continued throughout the month. 5.Inverter 1 middle unit has tripped offline at 16:00 on 03/19 and reporting "Ground Current RCD" andcontinued throughout the month and adressing this issue under EPC. | 1.SR095941 2.SR095940 3.SR095940 4.SR098413,SR098490 5.SR099138 | SR095940 | SR095940 | SR098413 | SR098490 | SR099138
R003 | NY | SOL-10416 | 33952.8754 | 0 | 33952.8754 |  | 29898 | 4054.8754 | 13.56% | 1. Optimizers are offline, EPC to complete. | 1.SR095942
R007 | NY | SOL-10417 | 35228.1172 | 0 | 35228.1172 |  | 29854 | 5374.1172 | 18%
BK16 | NY | SOL-11093 | 33612.4861 | 0 | 33612.4861 |  | 31346 | 2266.4861 | 7.231% | 1. Multiple optimizers are offline. 2. Inverter 1 is underperforming by 17 kW from 02/19, possibly due to one unit tripping offline and later resolved on 03/25. | 1.SR095961 2.SR097620 | SR097620
Trenton - Trenton East | IL | SOL-11060 | 211494 | 225513.7 | -14019.7 | -6.217% | 362877 | -151383 | -41.72% | 1.Tracker A1 S 65 is stuck at -1 degrees. Setpoint is at 0 degrees on 03/03. On 03/04 Tracker A1 S 65 tracking. 2.Inverters 9,10,12,13,14 tripped offline at 13:00 to 13:24 on 03/05 and reporting "Grid Phase Voltage Out of Range. Self resolved on same day. | 1.SR098003 2.SR098172 | SR098172
Trenton - Trenton West | IL | SOL-11061 | 225476 | 234876 | -9400 | -4.002% | 363840 | -138364 | -38.03% | 1.Tracker A1 S 43 and A1 S 70 are stuck from 03/06 2.Site tripped offline at 09:15Am from 03/17. It remains offline as major repairs are ongoing with the EPC. | 1.SR098251 2.SR098665 | SR098665
Dakota - Dakota Solar 1 | IL | SOL-11113 | 369540 | 463142.3 | -93602.3 | -20.21% | 0 | 369540 |  | 1.All trackers are stuck no error code reported since 02/21 and all trackers are tracking from 03/28 2.Inverter 4 offline at 12:45 from 03/14 and self resolved came back online at 11:45 on 03/31 | 1.SR098315 2.SR098593 | SR098593
X018 | NY | SOL-10418 | 11486.864 | 15507.42 | -4020.556 | -25.93% | 15457 | -3970.136 | -25.69% | 1.Inverter 2 still underperforming compared to its peers and reporting a device communication fault.since 01/22. 2. Inverter 1 is underperforming by 13kW compared to its peers since 03/26 | 1.SR096257 2.SR099018 | SR099018
Janiak Solar | NY | SOL-10898 | 344324.1741 | 359649.1 | -15324.9259 | -4.261% | 346875 | -2550.8259 | -0.7354% | 1.Site tripped offline from 8:00 AM to 09:30AM. Recloser voltages dropped, and later auto - reclosed at 9:15 AM on 03/09/25. 2.Site tripped offline due to utility outage from 06:30 AM to 08:20AM on 03/23 | 1.SR098319 2.SR098898 | SR098898
County Route 11B | NY | SOL-10983 | 880286 | 0 | 880286 |  | 0 | 880286 |  | 1. Trackers 3, 13, 16, 76, 82, 83, 142, 166, & 183 are stuck since 02/26. | 1. SR097816
Barone | NY | SOL-11034 | 469114 | 0 | 469114 |  | 519583 | -50469 | -9.713% | 1.Site tripped offline at 22:45 on 03/01 and relay Y-Phase voltages are dropped to zero. On 03/02 technician closed in the recloser site came back online at 13:10 on 03/02. 2.Site tripped offline at 06:20AM and utility voltages are also dropped to zero. On 03/24 technician closed the recloser and the site was re-energized at 08:45AM. 3.All trackers are currently not tracking and stuck at 0degrees from 03/14 at 11:45AM. Remote reset did not work. On site visit needed | 1. SR097951 2.SR098899 3.SR097600 | SR098899 | SR097600
Cedarville | IL | SOL-11069 | 355589 | 362281.6 | -6692.6 | -1.847% | 365444 | -9855 | -2.697%
O'Brien Hill #1 | NY | SOL-11098 | 67337 | 0 | 67337 |  | 0 | 67337 |  | 1.Site tripped offline at 08:05 AM on 03/04 due to the utility recloser opening. On 03/06, the technician closed the recloser, and the site came back online at 15:25. The site tripped offline again at 11:20 on 03/07. The utility was contacted again to close the recloser, but the closure was not successful. Further troubleshooting is needed. | 1.SR098029, SR098028 , SR098278 | SR098028 | SR098278
O'Brien Hill #2 | NY | SOL-11099 | 126051 | 0 | 126051 |  | 0 | 126051 |  | 1.Site tripped offline at 08:05 AM on 03/04 due to the utility recloser opening. On 03/06, Site 2 was not accepting remote commands from the utility, and they needed to dispatch a technician to investigate. On 03/27, the technician closed the recloser, and the site came back online at 02:30 PM. | 1. SR098029
Trinity - Freeport | IL | SOL-11057 | 380764 | 262931.7 | 117832.3 | 44.81% | 0 | 380764 |  | 1.TCU 55, 62, 64 are back online from 03/06 | 1.SR098066
Ransom | NY | SOL-11157 | 573181.7 | 0 | 573181.7 |  | 0 | 573181.7 |  | 1. Inverter 1 tripped offline at 08:55am on 03/06 and reporting "ISLAND PROTECTION" fault and selfresolve don 033/07 at 09:00AM 2.Site tripped offline at 22:20 on 03/16, and the meter voltages dropped to zero. However, the recloser voltages remained available. The site self resolved and came back online on 03/21 at 17:45. It tripped offline again at 17:05 on 03/23, with meter voltages dropping to zero, and the site was back online on 03/24. | 1.SR098233 2.SR098646 | SR098646
Horseheads - Wedge | NY | SOL-11160 | 351172 | 0 | 351172 |  | 0 | 351172 |  | 1.Site offline at 03:15PM on 03/16 and back online at 15:35 on 03/21 2.Trackers 101-114 are stuck since the site went live on 02/01 | 1.SR098634 2. SR099014 | SR099014
Otisville - Shoddy Hollow | NY | SOL-11185 | 770722.7 | 0 | 770722.7 |  | 0 | 770722.7 |  | 1. Site tripped offline multiple times at 08:15 on 03/12 due Y-Phase voltages dropped to zero and Auto-reclosed at 15:45 on 03/12. | 1. SR098433
Wellsville - Chenunda Creek | NY | SOL-11187 | 367949.8 | 0 | 367949.8 |  | 0 | 367949.8 |  | 1.Site offline at 03:15PM on 03/16 and self resolved & back online on 03/17 at 11:20AM | 1. SR098638
DC: Washington - Essex Condominium | DC | SOL-10036 | 3125 | 3748.763 | -623.763 | -16.64% | 4003.581 | -878.581 | -21.94% | 1.Site stopped communication at 23:45 on 03/27 and continued throught the month.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 12007 | 11698.62 | 308.38 | 2.636% | 12392.76 | -385.76 | -3.113% | 1. The site went offline at 12:15 AM on 03/09 after the technician restarted it, and the site was back online at 11:00 AM on 03/10. 2. Inverter 2 tripped offline at 15:15 on 03/17 due to a fault current and was back online at 07:30 AM on 03/18. It then tripped offline again at 15:15 on 03/28 due to a fault current and issue occurs through out the month. 3. The site was offline from 02:45 AM to 08:30 AM on 03/30 and then tripped offline again at 19:45 on 03/30, coming back online at 09:30 AM on 03/31. | 1. SR098317 2. SR095581 3. SR099162
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 13948 | 11218.65 | 2729.35 | 24.33% | 12386.12 | 1561.88 | 12.61%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Apr
Generate Capital |  |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  |  | 30893478.1548 | 10291122.959 | 20602355.1958 | 200.2% | 37349149.895 | -6455671.7402 | -17.28% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 26899.125 | 34350.14 | -7451.015 | -21.69% | 33051.22 | -6152.095 | -18.61% | 1. Site production was low on 04/07 , 04/11 , 04/12 due to rain
K041 | NY | SOL-10357 | 24174.125 | 27175.15 | -3001.025 | -11.04% | 26573 | -2398.875 | -9.027% | 1. Site production was low on 04/07 , 04/11 , 04/12 due to rain
K043 | NY | SOL-10358 | 30214.1875 | 30097.14 | 117.0475 | 0.3889% | 5845 | 24369.1875 | 416.9% | 1.Estimated values are low in AE we have also verified the file which was given GC
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was offline from 02/21 due to Phase C fuse was blown and parts were needed. | 1.SR097569
K115 | NY | SOL-10361 | 6317.3125 | 10208.2 | -3890.8875 | -38.12% | 15164.8 | -8847.4875 | -58.34% | 1.96 optimizers were down for site construction. | 1.SR093291
K152 | NY | SOL-10362 | 8946.0312 | 9193.901 | -247.8697 | -2.696% | 9488 | -541.9688 | -5.712%
K166 | NY | SOL-10363 | 32963.625 | 35000.76 | -2037.135 | -5.82% | 34655.66 | -1692.035 | -4.882%
K206 | NY | SOL-10927 | 19081.7969 | 18878.37 | 203.4269 | 1.078% | 19705 | -623.2031 | -3.163%
K251 | NY | SOL-10365 | 20736.1875 | 0 | 20736.1875 |  | 21903.15 | -1166.9625 | -5.328% | 1.Weather station stopped communicating since 11/22/24 | 1.SR093633
K269 | NY | SOL-10366 | 19317.125 | 22321.96 | -3004.835 | -13.46% | 20834.2 | -1517.075 | -7.282% | 1. Site production was low on 04/07 , 04/11 , 04/12 due to rain
K273 | NY | SOL-10367 | 20828.125 | 0 | 20828.125 |  | 26398 | -5569.875 | -21.1% | 1.Weather station stopped communicating since 06/14/24 2.26 optimizers are down for roof repair 3.Inverter-2 left unit was offline from 04/12 reporting "DC Isolation" fault and was back online at 15:15 on 04/16,again was offline on 04/26 and back online at 07:00 on 04/28 | 1.SR086842 2.SR093294 3.SR098958 | SR093294 | SR098958
K287 | NY | SOL-10919 | 16925.2812 | 14857.87 | 2067.4112 | 13.91% | 18269 | -1343.7188 | -7.355%
K298 | NY | SOL-10368 | 18291.0938 | 19537.97 | -1246.8763 | -6.382% | 20871 | -2579.9062 | -12.36% | 1.Inverter-2 tripped offline at 13:45 on 04/15 and was back online at 15:30 on 04/15 | 1.SR099824
K335 | NY | SOL-10370 | 19606.1875 | 21354.86 | -1748.6725 | -8.189% | 21969 | -2362.8125 | -10.76% | 1. Site production was low on 04/07 , 04/11 , 04/12 due to rain
K345 | NY | SOL-10920 | 22556.4062 | 13563.33 | 8993.0763 | 66.3% | 24273 | -1716.5938 | -7.072% | 1.Site production was low on 04/07 , 04/11 , 04/12 due to rain
K445 | NY | SOL-10373 | 18283.4375 | 19900.89 | -1617.4525 | -8.128% | 19373.38 | -1089.9425 | -5.626%
K495 | NY | SOL-10374 | 38230.5 | 77931 | -39700.5 | -50.94% | 89545.34 | -51314.84 | -57.31% | 1All inverters stopped communicating at 05:52 AM on 02/14. After the technician checked in and re-energized the switchgear, the inverters came back online at 11:51 AM on 04/18. 2. Inverters 2 and 5 (right units) were offline starting from 04/18, reporting a "DC Voltage Low" fault. They came back online at 10:00 AM on 04/23 after a technician checked in and isolated string 8 of Inverter 2 and string 9 of Inverter 5, which were causing the inverters to stop producing. Inverter 11 (left unit) was also offline since 04/18, reporting a "DC Isolation Fault." During troubleshooting, it was discovered that following a firmware update, the inverter no longer displayed fault codes and continued to fail to produce power. SolarEdge technical support was contacted, and a callback was received. Case number 5713468 was created. | 1.SR099648,SR093196 2.SR100035 | SR093196 | SR100035
M020 | NY | SOL-10380 | 18382.4688 | 21440.02 | -3057.5513 | -14.26% | 22928 | -4545.5312 | -19.83% | 1. Inverter 2 middle unit was tripped offline at 15:15 on 04/27 due to a "3 Phase Possible Arc Detection" fault. It came back online at 09:45 on 04/30 after the technician updated the firmware. | 1.SR100481
M092 | NY | SOL-10383 | 20002.3125 | 21125.88 | -1123.5675 | -5.318% | 22220.51 | -2218.1975 | -9.983%
M143 | NY | SOL-10384 | 23438.6875 | 26600.75 | -3162.0625 | -11.89% | 24656.4 | -1217.7125 | -4.939% | 1.Inverter modules 1.0.19 and 1.0.46 are offline, reporting no communication with power optimizer. GenC asks to address during PM | 1. SR093306
M144 | NY | SOL-10385 | 33364.5625 | N/A |  |  | 35364 | -1999.4375 | -5.654%
M167 | NY | SOL-10386 | 24800.4062 | 18540.54 | 6259.8662 | 33.76% | 29218.68 | -4418.2738 | -15.12% | 1.Site production was low on 04/07 , 04/11 , 04/12 due to rain
M188 | NY | SOL-10387 | 15083.375 | N/A |  |  | 18637 | -3553.625 | -19.07% | 1.Inverter 1 tripped offline at 15:15 on 04/08 due to 3 Phase Possible Arc Detection fault and back online at 12:30PM on 04/10 after technician did firmware update. 2.Inverter 1 left unit has tripped offline at 12:45 on 04/13 due to 3 Phase Possible Arc Detection fault and back online at 10:00AM on 04/16. 3. Inverter 2 left and right units tripped offline at 15:00 on 04/13 due to 3 Phase Possible Arc Detection fault and back online at 10:00AM on 04/16 after technician reset fault and updated firmware. 4.Inverter 1 left,middle units and inverter 2 all units tripped offline between 11:30 AM and 15:30 on 04/27 due to 3 Phase Possible Arc Detection. Inverter 1 left and middle units back online at 07:15AM on 04/28. | 1.SR099539 2.SR099754 3.SR099858 4.SR100476 | SR099754 | SR099858 | SR100476
EMHC | NY | SOL-10351 | 6770.2578 | 5752.708 | 1017.5498 | 17.69% | 8755.639 | -1985.3812 | -22.68% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline | 1.SR093236
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site stopped communicating from 03/25. On 03/27 Technician stated that main breaker tripped and malfunctioning. Site was remained offline till date. | 1.SR098981
Q018 | NY | SOL-10398 | 18729.875 | 19231.93 | -502.055 | -2.611% | 17292.69 | 1437.185 | 8.311%
Q021 | NY | SOL-10399 | 14665.9375 | 14406.07 | 259.8675 | 1.804% | 14385.87 | 280.0675 | 1.947%
Q025 | NY | SOL-10400 | 25002.125 | 24715.96 | 286.165 | 1.158% | 13314 | 11688.125 | 87.79%
Q074 | NY | SOL-10402 | 16554.25 | 16150.24 | 404.01 | 2.502% | 16444.09 | 110.16 | 0.6699%
Q115 | NY | SOL-10872 | 20844.875 | 21900.79 | -1055.915 | -4.821% | 21477.78 | -632.905 | -2.947%
Q139 | NY | SOL-10403 | 12667.0312 | 13725.07 | -1058.0387 | -7.709% | 13801 | -1133.9688 | -8.217%
Q157 | NY | SOL-10404 | 22285.3125 | 24006.62 | -1721.3075 | -7.17% | 24481.19 | -2195.8775 | -8.97% | 1.Inverter 2 was derating by 8 kW compared to its peers. On 03/18, the technician identified the inverter as faulty and RMA'd its power head. On 04/22, the technician replaced the RMA unit with a new one, and the inverter is now producing in line with its peers. 2.Inverter 2 is underperforming. String 2.0 is overproducing (14.6 kW) and not tracking irradiance, while strings 2.2 and 2.3 are underproducing (max 1.5 kW and 1 kW, respectively), indicating potential string-level issues. 3.Inverter 5 was offline at 19:45 on 04/27 and back online at 18:30 on 04/28. | 1.SR098365 2.SR100362 3.SR100496 | SR100362 | SR100496
Q192 | NY | SOL-10406 | 34496 | 36955.21 | -2459.21 | -6.655% | 35580.41 | -1084.41 | -3.048%
Q210 | NY | SOL-10407 | 28207.625 | 28315.17 | -107.545 | -0.3798% | 29628 | -1420.375 | -4.794%
Q229 | NY | SOL-10408 | 12297.0938 | 13702.72 | -1405.6262 | -10.26% | 12576.04 | -278.9463 | -2.218% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. 2.Site production was low 04/07, 04/11, 04/12 due to bad weather | 1. SR088813
Q231 | NY | SOL-10870 | 45258.625 | 47488.82 | -2230.195 | -4.696% | 48847 | -3588.375 | -7.346%
Q405 | NY | SOL-10409 | 50011.75 | 57219.12 | -7207.37 | -12.6% | 52997.85 | -2986.1 | -5.634% | 1. 4 Inverter modules are offline. Will investigate next time on site Module 1.0.64 Module 4.0.39 , 3.0.20 ,1.0.64 | 1.SR093324
Q435 | NY | SOL-10923 | 66318.25 | 51348.37 | 14969.88 | 29.15% | 70048 | -3729.75 | -5.325% | 1. Inverter 5 (left unit) experienced multiple tripping events during the middle of the day throughout the month; however, the issue later resolved itself. 2. Inverter 3 (right unit) experienced multiple tripping events during the middle of the day on 04/18 and 04/19, reporting a "Ground Current - RCD" fault. However, the issue later resolved itself. 3.Inverter 1 left unit has tripped offline at 12:45PM on 04/30. | 1.SR099970 2.SR099971 3.SR100732 | SR099971 | SR100732
Q485 | NY | SOL-10869 | 59771.25 | 48000.36 | 11770.89 | 24.52% | 65592.8 | -5821.55 | -8.875% | 1.Inverter 1 (right unit) came back online at 9:00AM after the technician power-cycled the inverter on 04/07. 2Inverter 1 (right unit) went offline on 04/15, reporting a Ground Current RCD error on SolarEdge. The technician reset the inverter on 04/21, and it came back online at 07:00. | 1. SR099139 2.SR099856 | SR099856
Q490 | NY | SOL-10411 | 44293.5 | N/A |  |  | 46036.53 | -1743.03 | -3.786% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1. SR093326
Q620 | NY | SOL-10867 | 66703 | 66971.2 | -268.2 | -0.4005% | 69242.32 | -2539.32 | -3.667%
QMOA | NY | SOL-10415 | 5623.6 |  |  |  | 6308.026 | -684.426 | -10.85% | 1.Site production was low on 04/07 , 04/11 , 04/12 due to bad weather
X024 | NY | SOL-10419 | 25538.5938 | 26404.74 | -866.1463 | -3.28% | 24516 | 1022.5938 | 4.171%
X026 | NY | SOL-10420 | 23114.9 | 21577.1 | 1537.8 | 7.127% | 33098.88 | -9983.98 | -30.16% | 1.Optimizer 1.0.124 is offline. Will investigate combinely with other modules. 2. Site production was low on 04/05 , 04/07 , 04/11 , 04/12 due to rain | 1.SR095662
X090 | NY | SOL-10925 | 19359.6875 | 17087.05 | 2272.6375 | 13.3% | 20356 | -996.3125 | -4.894%
X117 | NY | SOL-10422 | 16727.6 | 18316.15 | -1588.55 | -8.673% | 17700.56 | -972.96 | -5.497%
X125 | NY | SOL-10423 | 30152.75 | 31320.93 | -1168.18 | -3.73% | 31615.96 | -1463.21 | -4.628%
X134 | NY | SOL-10424 | 29330.9062 | N/A |  |  | 31287 | -1956.0938 | -6.252%
X135 | NY | SOL-10425 | 22792.75 | 23516.71 | -723.96 | -3.078% | 25004 | -2211.25 | -8.844% | 1. Inverter 2 left unit tripped offline at 14:00 from 04/25 with AC line voltage too high fault and remains offline throughout the month. | 1. SR100434
X139 JHS 222 | NY | SOL-10426 | 36186.6166 | 39537.84 | -3351.2234 | -8.476% | 38484 | -2297.3834 | -5.97%
X140 | NY | SOL-10926 | 20803.4844 | 17164.1 | 3639.3844 | 21.2% | 20901 | -97.5156 | -0.4666% | 1.Right unit of inverter 3 is reporting low voltage from 02/28/25 due to Fuse blown in inverter. On 04/01, technician de-energized the inverter, verified and replaced the defective fuse with a stock unit and inverter started for production. | 1.SR098313
X166 | NY | SOL-10427 | 21565.7 | 21010.73 | 554.97 | 2.641% | 23280 | -1714.3 | -7.364%
Murphy | MN | SOL-10094 | 864010 | 922487.8 | -58477.8 | -6.339% | 882116.8 | -18106.8 | -2.053% | 1.Inverter 3 tripped offline at 14:50 CDT on 04/01, reporting "Emergency stop button has been pushed", later PE was able to remotely reset the inverter on 04/08 at 12:00CDT 2.Inverter 1 is derating by 130 kW from 4/21/25 on high irradiance days | 1.SR099293 2.SR100141 | SR100141
Terning | MN | SOL-10093 | 909272 | 948523.9 | -39251.9 | -4.138% | 883558.1 | 25713.9 | 2.91% | 1.While Hunt Electric was onsite the site was taken offline from 10:00 AM to 10:30 AM on 04/01 and replaced the fuse on Phase B of the utility pole and also Inverter A is back online at 04/01 at 10:30am. | 1.SR098987
Boas Road 04 | NY | SOL-10908 | 0 | 349319.05 | -349319.05 | -100% | 331584.58 | -331584.58 | -100% | 1. Meter stopped communicating from 2:05PM on 03/16 till date. | 1.SR098641
Kelly Bridge Farm | NY | SOL-10911 | 0 | 331817.21 | -331817.21 | -100% | 342312.31 | -342312.31 | -100% | 1.The meter stopped communicating at 14:05 on 03/16. On 03/26, the technician investigated the issue, checked the fuses, tested the watch battery on the board, Meter is being RMA'd. 2.Multiple inverters are experiencing frequent tripping's and reporting "Grid Voltage imbalance" on 04/04 and resolved on 04/05. The site was taken offline from 09:55 AM to 11:40AM on 04/08 to inspected the power supply from the transformer to DAS cabinet to find the route cause of the inverters frequent tripping.Issue again occurred on 04/18 & 04/19 even after utility has lowered their voltages 3.Numerous inverters are experiencing multiple tripping's on 04/26 and resolved on 04/27 again occurred on 04/29 4.Inverter 30 (6.30) is derating at 41.8KW compared to its peers from 15:15 to 16:50 on 04/28 and again from 14:05 to 16:15 on 04/29. | 1.SR098640 2.SR099427 3.SR100447 4.SR100604 | SR099427 | SR100447 | SR100604
Pool Brook Road | NY | SOL-10909 | 295639 | 304056.86 | -8417.86 | -2.769% | 317202.12 | -21563.12 | -6.798%
Sackett Lake | NY | SOL-10910 | 177037 | 313070.33 | -136033.33 | -43.45% | 334933.92 | -157896.92 | -47.14% | 1. Inverter 2 tripped offline at 9:45 AM on 03/30 due to "FAULT PHASE 3" and "VBUS DERIVATE FAULT." to replace the stack for inverter 2 and also to replace string cards technician have taken the site offline from 12:30 to 17:10 on 04/17. later the technician has bypassed and re-energized inverter 2 and inverter was back online at 15:40 on 04/18 2.Inverter 1 didn't start for production and reported "SE AC CONTACTOR (94)" fault on 04/09, later Ingeteam remotely reset the inverter and it is back online at 12:30 on 04/09. Inverter 1 is again offline and reported “SE AC CONTACTOR (94)” on 04/14 later technician has power cycled the inverter and inverter 1 is back online at 16:55 on 04/15 3.Site has a brief outage from 11:55 to 13:10 on 04/24 4.Based on meter data, one of the inverters is offline from 04/26, as inverters lost communication to DAS, the technician found that Inverter 2 was offline due to a Phase 3 fault and a DC hardware fault. The technician contacted Ingecon for remote assistance and determined that additional troubleshooting is required to re-energize Inverter 2. | 1.SR099149 2.SR099576 3.SR100361 4.SR100623 | SR099576 | SR100361 | SR100623
Burritt Road | NY | SOL-10913 | 280190 | 116936.81 | 163253.19 | 139.6% | 329579.98 | -49389.98 | -14.99% | 1.POA Pyranometer is not communicating from 07:00AM on 11/09/24 due to a malfunctioning NPort, where the POA and GHI are connected. 2. Inverters 1-5 has tripped offline on 03/31 at 10:15 as the malfunctioning breaker needs to be replaced, technician has replaced and re-energized the inverters on 04/16 at 13:00 while onsite the site was taken offline from 10:25 to 13:00 to work on inverters. 3. Site was tripped offline from 08:40 to 14:00 on 04/21 due to utility outage. | 1.SR093972 2.SR098708 3.SR100079 | SR098708 | SR100079
Villa Roma 1 | NY | SOL-10914 | 286622 | 194.46 | 286427.54 | 147294% | 298485.22 | -11863.22 | -3.974% | 1.Expected energy values are reporting very low. Created a case #66639 with GPM, As per GPM the BOM has been frozen from 02/27 | 1.SR099403
Villa Roma 2 | NY | SOL-10915 | 279010 | 291410.62 | -12400.62 | -4.255% | 290604.43 | -11594.43 | -3.99%
Washington 1 | NY | SOL-10912 | 315950 | 331351.51 | -15401.51 | -4.648% | 326068.02 | -10118.02 | -3.103%
Washington 3 | NY | SOL-10828 | 371264 | 55062.59 | 316201.41 | 574.3% | 398873.79 | -27609.79 | -6.922% | 1.Inverter 1 tripped offline at 06:50am on 04/29 and is reporting an "Inductor Blower" fault. On 04/30 Technician swapped the inductor fan of inverter 1 with inverter 2. Inverter 1 has been re-energized at 12:50pm , but inverter 2 is derating at 382kW. Inductor fan is being RMA'd by ingeteam until inverter 2 has tripped offline at 13:05 2. POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1.SR100629 2.SR093024 | SR093024
Washington 4 | NY | SOL-10829 | 381372.7 | 396735.8 | -15363.1 | -3.872% | 399701.27 | -18328.57 | -4.586%
Big Tree | NY | SOL-10966 | 321144 | N/A |  |  | 323746.35 | -2602.35 | -0.8038% | 1.Combiner box 7, string 1 is underperforming. Needs further investigation | 1.SR098866
Canoga | NY | SOL-10965 | 0 | N/A | [5 empty] | 1. Site tripped offline at 9:55 AM on 03/27 due to utility work at the substation and has remained offline throughout the month. | 1.SR098998
County Route 84 | NY | SOL-10967 | 854850 | N/A |  |  | 857242.25 | -2392.25 | -0.2791% | 1. Site had a brief utility outage between 20:00 to 20:50 on 04/16. | 1.SR099911
Donati | NY | SOL-10968 | 338220 | N/A |  |  | 408878.12 | -70658.12 | -17.28% | 1. Weather station Reporting 0 value from 05/31/24. POA sensors need to be replaced. 2. All trackers have been struck from various dates. Followed up with Soltec and they are working on it.Soltec will be conducting a site visit 3. Site had a brief utility outage between 08:50am to 10:00am on 04/03. 4.Inverters are offline from 08:25am to 09:55am on 04/29 while technician onsite for Preventive maintenance | 1.SR092964 2.SR097603,SR098877 3.SR099353 4.PM7740 | SR097603 | SR098877 | SR099353
Henrietta | NY | SOL-10972 | 414260 | N/A |  |  | 858985.29 | -444725.29 | -51.77% | 1.Inverters 3 & 4 are experiencing multiple tripping’s and reporting “SE VAC3 RMS H1" on 04/01 and inverter 3 is tripped offline on 04/01 at 16:15 later technician has reenergized the inverter on 04/02 at 14:10. Again Inverters 3 & 4 are experiencing multiple tripping’s on 04/03, on 04/07 technician contacted Ingeteam and they recommended testing the transformer DGA samples, as they observed an increase in reactive power injection. On 04/29 technician has estopped both the inverters and inverter 3 & 4 are back online at 17:25 on 04/29 2.USNE has taken the site offline for transformer testing from 11:50 am to 16:00 on 04/28. 3. Inverter 1 tripped offline from 14:00 to 15:10 on 04/25 due to "SE INSULATION FAULT" 4.All trackers and gateways stuck in wind stow and not accepting commands on 04/01 at 10:50am, some of the trackers has back to tracking but some trackers are still stuck | 1.SR099272, SR099864 2.SR099864 3.SR100426 4.SR099490 | SR099864 | SR099864 | SR100426 | SR099490
NY 70 | NY | SOL-10970 | 756760 | N/A |  |  | 978510.51 | -221750.51 | -22.66% | 1.Site tripped offline at 14:20 on 04/15 due to utility outage later technician has closed the switch gear at 10:00 on 04/17 2. Inverter 1 was offline on 04/25 due to fatal alaram, later on 04/28 technician has Inverters 1 and 2 were de-energized, and the relay from Inverter 2 was swapped with that of Inverter 1. Both inverters were re-energized. However, Inverter 1 faulted again with a “DC Contactor Fault.” and inverter 1 will reamin offline as it required further troubleshooting. 3.Inverter 3 & 4 experiencing multiple tripping's drastically on 04/30 | 1.SR099828 2.SR100395 3.SR100721 | SR100395 | SR100721
Reid | NY | SOL-10991 | 661842.9428 | 631012 | 30830.9428 | 4.886% | 766909 | -105066.0572 | -13.7% | 1. Inverters 5 and 30 tripped offline at 12:15 AM on 04/04and reporting "Grid Line Voltage Out of Range" and later technician has reset the breaker at 08:15 on 04/08 2.Inverter 4 is derating its peers by approx 50% and reporting "Temperature Sensor Fault - Warn0050", inverter being RMA'd 3. Inverter 18 is producing but with a temperature sensor abnomaly alarm from 03/25 later technician installed a new Powerhead on 04/14. 4.Inverter 9 tripped offline at 13:15 on 04/20 and reporting "Grid Line Voltage Out of Range" and back online at 08:15 on 04/22. Again inverter 9 tripped offline at 16:00 on 04/22 and back online at 12:00 on 04/25 by resetting the breakers. 5.Inverter 30 tripped offline at 13:15 on 04/20 and reporting "Grid Line Voltage Out of Range" and back online at 08:15 on 04/22 by resetting the breakers 6.Inverter 30 tripped offline at 11:00 AM on 04/23 and reporting "Grid Phase Voltage Out of Range" & Inverter 5 tripped offline at 14:15 and reporting "Grid Phase Voltage Out of Range" and back online at 12:00 on 04/25 by resetting the breakers 7.Inverter 28 tripped offline at 14:45 on 04/28 and reporting "Grid Phase Voltage Out of Range". Inverter 9 tripped offline at 11:05AM and inverter 30 tripped offline at 12:50PM on 04/28 reporting "Grid Phase Voltage Out of Range" and technician has reset the breakers at 09:45am on 04/30. Again Inverters 9 & 30 tripped have tripped offline and reporting "Grid Phase Voltage Out of Range" at 14:00 on 04/30 8.Inverters 1 to 20 have tripped offline at 17:45 on 04/29 and reporting a "Loss of Main - GridV.OutLim", technician has reset the inverters 1 to 20, 28 at 09:45am on 04/30. Additionally, technician replaced the fuse on string 12 | 1.SR099418 2.SR100197 3.SR098354 4.SR100037,SR100198 5.SR100038 6.SR100212 7.SR100544 8.SR100674 | SR100197 | SR098354 | SR100037 | SR100198 | SR100038 | SR100212 | SR100544 | SR100674
Sangolqui | NY | SOL-10975 | 351500 | N/A |  |  | 400067.19 | -48567.19 | -12.14% | 1. Inverter 1 tripped offline at 08:55 AM on 04/05, reporting an "Isolation Alarm." It came back online at 11:40 AM the same day. On 04/11, the inverter started late in the morning and tripped offline again at 11:10 AM with the same "Isolation Alarm," but was back online by 12:10 PM. Later that day, it tripped offline at 17:50 and self-resolved at 14:35 on 04/12. The inverter then started late again at 08:35 on 04/13. 2.Site had a brief utility outage between 08:50AM to 10:00AM on 04/03. 3.Inverter 1 tripped offline due to Isolation resistance fault from 08:10AM to 10:55AM on 04/19 . | 1.SR099129 2.SR099351 3.SR100013 | SR099351 | SR100013
State Highway 17B | NY | SOL-10988 | 690070 | N/A |  |  | 753209.8 | -63139.8 | -8.383%
State Route 14A | NY | SOL-10997 | 44015 | N/A |  |  | 848546.08 | -804531.08 | -94.81% | 1. Site tripped offline at 04:10am on 04/03 technician found that there surge damage to SEL, due to failed CT in the grounding transformer and remained offline through out the month. | 1.SR099347
West Creek | NY | SOL-10995 | 776940 | N/A |  |  | 828525.56 | -51585.56 | -6.226% | 1. The site tripped offline at 13:15 on 04/15 due to a utility outage caused by pole damage. The outage was later cleared, and site is back online at 16:15 on 04/15. | 1. SR099823
Wildflower | NY | SOL-10982 | 759563 | N/A |  |  | 842400.75 | -82837.75 | -9.834%
Glen Mary 1 | NY | SOL-10993 | 806620 | N/A |  |  | 858725.86 | -52105.86 | -6.068%
Glen Mary 2 | NY | SOL-10994 | 352610 | N/A |  |  | 366971.2 | -14361.2 | -3.913%
Telegraph 1 | NY | SOL-11003 | 609182 | N/A |  |  | 599655.38 | 9526.62 | 1.589% | 1. Site had a brief utility outage between 13:10 to 15:45 on 04/22. | 1. SR100152
Telegraph 2 | NY | SOL-11004 | 322296 | N/A |  |  | 311979 | 10317 | 3.307% | 1. The site went offline at 13:35 on 03/31 and back online at 02:00 AM on 04/01. The issue later self-resolved. 2. Site had a brief utility outage between 13:10 to 15:45 on 04/22. | 1. SR098995 2. SR100154 | SR100154
Cafferty Hill | NY | SOL-10996 | 768050 | N/A |  |  | 806343.49 | -38293.49 | -4.749%
Dunkleman | NY | SOL-11008 | 865550 | N/A |  |  | 1009142.13 | -143592.13 | -14.23% | 1. Currently, the following trackers are stuck Group 1: 57 & 119 Group 2: 24, 27, 32, 36, 39, 43, 54, 59, 61, 97, 114, & 124. A total of 14 tracker control units are struck. later 43 tracker is back online. 2. Inverter 1 tripped offline at 16:00 on 04/01 due to a 'Ground Fault'. A technician was on site to perform a preventive maintenance (PM) inspection and found that the inverter was offline. The technician cleared the ground fault, replaced the ground fault fuse, reset the AC breaker, and power-cycled the inverter. The inverter is back online at 11:25 on 04/03. | 1. SR095109 2. SR099284 (PM7482) | SR099284
Route 19 1 | NY | SOL-11001 | 377130 | N/A |  |  | 405489.67 | -28359.67 | -6.994% | 1. Site had a brief utility outage between 12:45 to 15:45 on 04/22. | 1. SR100161
Route 19 2 | NY | SOL-11002 | 925110 | N/A |  |  | 1002309.25 | -77199.25 | -7.702% | 1. Site had a brief utility outage between 13:00 to 15:45 on 04/22. | 1. SR100162
Yellow Mills 1 | NY | SOL-11006 | 344742 | N/A |  |  | 353655.16 | -8913.16 | -2.52%
Yellow Mills 2 | NY | SOL-11005 | 340313 | N/A |  |  | 363985.19 | -23672.19 | -6.504%
Yellow Mills 3 | NY | SOL-11007 | 335936 | N/A |  |  | 348598.8 | -12662.8 | -3.632%
Catskill | NY | SOL-11021 | 600100 | N/A |  |  | 621136.5 | -21036.5 | -3.387% | 1. The site tripped offline at 09:00 AM on 04/11. A technician found that the SEL relay had tripped. After resetting the relay and closed, the site is back online at 13:10 on 04/12.. | 1. SR099690
Eddy Ridge | NY | SOL-11054 | 434509 | N/A |  |  | 474615 | -40106 | -8.45%
Ridgeway #1 | NY | SOL-11018 | 902744 | N/A |  |  | 1036704.57 | -133960.57 | -12.92% | 1. Inverter 2 tripped offline at 07:25 AM on 04/11, possibly due to EPC activity on site. It later self-resolved and back online at 11:00 AM on 04/11. However, Inverter 2 tripped offline again at 11:55 AM on 04/12, reporting an overall work state of 'STOP'. A technician inspected the issue, removed the old modules, and replaced them with new ones. Then inverter back online at 13:10 on 04/14. 2. Currently , the following trackers 2,29,124 stuck at 1.17 Degrees at 11:55 on 04/19 . | 1. SR099687 2. SR100044 | SR100044
Rivard 1 | NY | SOL-11011 | 606969.7168 | 103072.2 | 503897.5168 | 488.9% | 838372.6 | -231402.8832 | -27.6% | 1. The site stopped communicating on 03/29. A technician replaced the cutout fuse on the Control Power Transformer, and communications were restored on 04/07. 2. The site lost communication at 9:15 AM on 04/12; however, meter production data remained available. On 04/24, the technician found that Pad 1 DAS had a blown 4A fuse. They removed a fuse from Pad 2, but it failed upon re-energization. The technician will need to return with additional fuses. 3. The site lost communication at 15:30 on 04/23, and production could not be verified. On 04/24, the technician checked in and identified that the DAS was offline due to a defective main breaker. The breaker was replaced, and a filler plate was added to the panel. The site is now back online. | 1. SR099146 2. SR099726 3.SR100241 | SR099726 | SR100241
Rivard 2 | NY | SOL-11012 | 739966.0896 | 739025.9 | 940.1896 | 0.1272% | 810690.4 | -70724.3104 | -8.724% | 1.1.Tracker control 33 - 90, 129 - 136, 148 , 20-32, 123-128, 172-183 are not communicating & tracker 156 , 121 is stuck and production dropped (approxmately ) 25 KW down. | 1.SR095073
Ridgeway #2 | NY | SOL-11027 | 403955 | N/A |  |  | 525809.26 | -121854.26 | -23.17% | 1. Inverter tripped offline at 14:30 on 04/10. On 04/11 Technicain replaced broken module and inv is back online at 12:10. 2. Tracker 53 stuck at -20Degress on 04/16 at 12:10 and additionally stopped communicating from 04/17 from 06:30AM. Will investigate next time onsite. 3.The site tripped offline at 10:20 on 04/25 due to a utility outage. On 04/28, the technician programmed the PT board, and the site was re-energized. The site was back online at 15:40. | 1.SR099656 2. SR100042 3.SR100303 , SR100429 | SR100042 | SR100303 | SR100429
Spencer | NY | SOL-11017 | 803402 | N/A |  |  | 1003955 | -200553 | -19.98% | 1. trackers 169 and 170 are not tracking from 04/02. 170 resolved, 138 stuck again, 169 stuck, these 3 are intermittent, sometimes working, sometimes stuck all day. 2.Tracker 81 currently stuck at 55.58deg & Tracker 81 and 170 stuck at 55 deg from 04/25. 3. The site tripped offline at 08:40 on 04/21 due to work on the substation at the GOAB. On 04/24, NYSEG closed in their circuit, and the site automatically reclosed and began producing at 14:05. 4.6 trackers tracking incorrectly based on the time of day. Trackers 1, 39, 49, 96, 115, & 139 are all reporting a positive tracking angle when the others are reporting a negative angle. Additionally, tracker 170 is stuck at 55 degrees from 04/25 | 1. SR095821 2. SR099986 3. SR100055 4. SR100400 | SR099986 | SR100055 | SR100400
Reisender | NY | SOL-10886 | 311820 | 324363.73 | -12543.73 | -3.867% | 345476.75 | -33656.75 | -9.742% | 1.The site tripped offline at 09:40 AM on 04/02. On 04/03, the technician closed the relay to re-energize the site at 08:35. | 1. SR099313
Finney | NY | SOL-10999 | 981210 | N/A |  |  | 1005784.59 | -24574.59 | -2.443%
Davis Solar | NY | SOL-10958 | 360765 | 355139.1 | 5625.9 | 1.584% | 402689 | -41924 | -10.41% | 1.Inverter offline from 06:00 to 09:45 on 04/20 later Inverter was back online by remote reset. | 1. SR100032
Genesee | NY | SOL-10951 | 353751 | N/A |  |  | 766542.12 | -412791.12 | -53.85% | 1.CB 19 offline from 02/15 and CB 6 are offline from 03/07. Isolated and removed damaged materials. Stored hardware in storage container. Flexrack to RMA or quote replacement parts. 2. The site tripped offline at 14:30 on 04/03. On 04/04, the technician closed the recloser. The site was back online and producing by 18:25 3.All inverters tripped offline at 17:20 on 04/17, reporting 'Supply Voltage Failed.' On 04/18, the technician closed in the recloser, and the site was re-energized at 12:25. 4. site tripped offline from 04/21 at 08:50 due to recloser is opened due to the circuit being out of normal configuration. This will be offline until circuit is returned to normal on 5/16. | 1.SR098959 2. SR099387 3. SR099967 4. SR100101 | SR099387 | SR099967 | SR100101
Landau I | NY | SOL-10891 | 338540 | N/A |  |  | 368283.57 | -29743.57 | -8.076%
Landau II | NY | SOL-10895 | 392870 | N/A |  |  | 825724.48 | -432854.48 | -52.42% | 1.Inverter 2 offline at 09:55 from 03/25. On 04/15, after completing network repairs, the technician was able to remotely access the inverter and reset it. The inverter was online and producing from 14:15 2. Inverter 1 is tripped offline at 11:00 from 04/03 showing an error, and thermal events were found on the contactors. Additional troubleshooting is required with SMA, and the inverter will remain offline. On 04/15, after a manual reset and parameter change by the technician, Inverter 1 began producing, and the firewall communication issue was also resolved. 3.Inverter was offline from 06:00 to 13:50 due an error from the pilot on 04/20 later back online by remote reset. 4.Inverter 1 tripped offline from 06:00 to 09:05 on 04/21 and again offline from 09:55 to 14:50 on 04/22. After remote reset inverter back online. 5.Inverter 2 tripped offline at 06:00 on 04/26. After remotely reset back online at 10:20. Inverter 2 tripped offline again at 17:30. Remote reset 18:00 and it is back online. 6. Inverter tripped offline from 06:00 to 09:15 on 04/27 and reporting AC Breaker Switch "OPEN", later back online by remote reset. | 1. SR098626 2.SR098559 3.SR100034 4. SR100067 5.SR100448 6.SR100460 | SR098559 | SR100034 | SR100067 | SR100448 | SR100460
New Beginnings | NY | SOL-10890 | 340660 | 352166.13 | -11506.13 | -3.267% | 358496.22 | -17836.22 | -4.975%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 822842 | 852227.3 | -29385.3 | -3.448% | 940853.4 | -118011.4 | -12.54%
Brodhead Solar, LLC | NY | SOL-10899 | 389556 | 404968.9 | -15412.9 | -3.806% | 465928.9 | -76372.9 | -16.39% | 1. NCU 2 tracker 1 stuck since 11/19 and tracker 35 stuck at 11:45 since 01/31 2. NCU 1 tracker 10 stuck at 09:15 since 02/23. | 1. SR095624 2.SR097725 | SR097725
Svenski | NY | SOL-10894 | 328257 | N/A |  |  | 401358.09 | -73101.09 | -18.21% | 1. Inverter is tripped offline at 16:40 on 04/03. On 04/04 Inverter is back online by remote reset at 08:35. 2.Site offline at 20:20 PM on 04/12. On 04/13 Site regained its communication at 13:05 and inverter was back online by remote reset at 14:30. 3. Inverter is tripped offline at 16:20 on 04/27 and reporting an "STOP: PARAMETER INVOPMOD" fault. 04/28 Inverter back online by remotely reset at 07:30 and again offline from 08:50 to 09:35. | 1.SR099393 2.SR099740 3.SR100471 | SR099740 | SR100471
Bantam | NY | SOL-10986 | 47670 | N/A |  |  | 981035.1 | -933365.1 | -95.14% | 1.POA 1 is not accurately reporting - technician need to visit for further troubleshooting. 2. All trackers were stopped between -56.93 degrees and -60.7 degrees on 03/20 due to very high winds on-site. on 04/28 technician NCU's connected to snow sensor power cycled, all trackers are now operating. 3. NCU 4 device 1035 stuck at -23.66 degrees from 11:35AM from 04/29. | 1. SR096042 2. SR099324 , SR096042 3.SR100652 | SR099324 | SR096042 | SR100652
Bogart | NY | SOL-10887 | 349160 | 349181.8 | -21.8 | -0.006243% | 356914.17 | -7754.17 | -2.173% | 1.Combiner boxes 1.12 and 1.13 have been underperforming since 01/27, with an approximate loss of 79 kW. Will investigate during the next onsite visit. | 1.SR096006
Dubois | NY | SOL-10892 | 330690 | N/A | [5 empty] | 1.Site tripped offline at 12:12AM on 04/17, Z and Y phase voltages dropped to zero. After utility outage is restored Site back online by remote reset at 12:06 on 04/17. | 1.SR099916
Salt Point | NY | SOL-10888 | 331500 | N/A |  |  | 419761.74 | -88261.74 | -21.03% | 1. Trackers- NCU 1 SPC 103 through 115 were stucked from 03/18. ON 03/19, technician checked in and found that TCU breaker tripped and also found broken panel which is need to be replaced. Created a ticket and Further Trouble Shooting required. | 1. SR098692
Wheatland 2A | NY | SOL-10971 | 778710 | N/A |  |  | 839262.6 | -60552.6 | -7.215% | 1.12 additional trackers stuck. On 03/19, technician was unable to perform troubleshooting the trackers due to not getting access to connect with NCU and created a case with the manufacturer and further troubleshooting is required with NEXTracker. On 04/08 technician after replacing two HVPS. Currently multiple trackers are still struck and requires additional troubleshooting along with NEXTracker's assistance. 2.14 trackers are currently stuck from 01/06 NCU 1 SPC 111, 112, 118, 205, 305, 307, 310, & 311 & NCU 2 SPC 125, 126, 136, 242, 338, & 341. On 04/15 Technician worked on the trackers, multiple trackers are still not reporting and require further troubleshooting with NexTracker. 3.Site tripped offline at 15:20 on 04/03 and relay Z and Y phase voltages are dropped to 0V due to utility outage. Site back online at 17:00 on same day after the utility outage was cleared and utility voltages are back online. | 1.SR094820 2.SR099686 3.SR099386 | SR099686 | SR099386
Wheatland 2B | NY | SOL-10961 | 784270 | N/A |  |  | 833219.63 | -48949.63 | -5.875% | 1.Site tripped offline at 15:20 on 04/03 and relay Z and Y phase voltages are dropped to 0V due to utility outage. Site back online at 17:00 on same day after the utility outage was cleared and utility voltages are back online. 2.15 trackers are currently stuck from 03/21 NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 | 1. SR099385 2. SR098860 | SR098860
Brickchurch | NY | SOL-10889 | 289240 | 278002.32 | 11237.68 | 4.042% | 411677.08 | -122437.08 | -29.74% | 1.All NCU 2 trackers have lost communication, while NCU 1 trackers 115-127 remain stuck from 03/27. Previous stuck trackers included 18 on 03/24 and specific units on 03/17. 2.Site tripped offline at 08:40 on 04/07. On 04/11 Ameresco was able to remotely confirm proper utility voltages were present onsite and closed the site in. It is online and producing at 15:30. | 1. SR099118 , SR097454 2. SR099466 | SR097454 | SR099466
McCarthy Solar | NY | SOL-10992 | 342590 | N/A |  |  | 359833.18 | -17243.18 | -4.792%
Costanza | NY | SOL-10907 | 360380 | N/A |  |  | 375749.63 | -15369.63 | -4.09% | 1.The site went offline at 20:46 on 04/02. On 04/03, the technician closed the relay, and the site was back online and producing as expected by 08:59am. 2. Site offline at 22:41 on 04/23. 04/24 the technician closed the relay, and the site was back online and producing as expected by 13:41 | 1.SR099345 2. SR100252 | SR100252
Lockenhurst Pond | NY | SOL-11000 | 368615 | 393092.2 | -24477.2 | -6.227% | 397088 | -28473 | -7.17%
Drinkwater | NY | SOL-10896 | 347150 | N/A |  |  | 359295.77 | -12145.77 | -3.38%
Altamont | NY | SOL-11085 | 724960 | 765286.5 | -40326.5 | -5.269% | 639559.6 | 85400.4 | 13.35% | 1. The site tripped offline at 07:15 AM on 04/18 and later self-resolved and back online at 09:30 AM on 04/18. | 1. SR099977
Krumkill North | NY | SOL-11086 | 687550 | 744225.3 | -56675.3 | -7.615% | 744683.1 | -57133.1 | -7.672%
Krumkill South | NY | SOL-11087 | 571189 | 585762.4 | -14573.4 | -2.488% | 583809.6 | -12620.6 | -2.162%
X092 | NY | SOL-11189 | 17692.4 | 17742.88 | -50.48 | -0.2845% | 19404 | -1711.6 | -8.821%
X093 | NY | SOL-10932 | 839.665 | 0 | 839.665 |  | 13699 | -12859.335 | -93.87% | 1. The site went offline at 13:15 on 03/18 and later self-resolved and back online on 08:00 AM on 04/15 and again tripped offline at 12:00 PM on 04/17 and offline throughout the month, awaiting for EPC to address. 2. Inverter 2 tripped offline at 13:15 on 03/10 and later self-resolved and back online on 08:00 AM on 04/15. 3. Many optimizers on SE are offline and later back online on 04/15. Additionally 1 optimizer on SE is offline , EPC to complete. | 1. SR098724 2. SR097637, SR098293 3. SR095945 | SR097637 | SR098293 | SR095945
X095 | NY | SOL-10929 | 17585.3164 | N/A |  |  | 18495 | -909.6836 | -4.919%
X181 | NY | SOL-10428 | 32407.2904 | N/A |  |  | 33412 | -1004.7096 | -3.007%
X415 | NY | SOL-10429 | 20488.8281 | N/A |  |  | 19306 | 1182.8281 | 6.127%
K198 | NY | SOL-10930 | 14934.1758 | N/A |  |  | 15025 | -90.8242 | -0.6045%
K203 | NY | SOL-11190 | 18670.1 | 17017.4 | 1652.7 | 9.712% | 20769 | -2098.9 | -10.11% | 1. Multiple optimizers are offline and later back online on 04/02. | 1.SR095954
K213 | NY | SOL-11191 | 19403.7 | 21842 | -2438.3 | -11.16% | 21777 | -2373.3 | -10.9% | 1. Inverter 3 tripped offline at 08:05 AM on 04/17. After the technician checked into the site, he found that the breaker was faulty and its connection to the busbar had overheated. The breaker is currently being replaced, and the inverter is offline throughout the month. | 1. SR099930
K217 | NY | SOL-10933 | 11456.6484 | 0 | 11456.6484 |  | 11653 | -196.3516 | -1.685%
K307 | NY | SOL-10876 | 23795.5938 | N/A |  |  | 24665 | -869.4062 | -3.525%
K610 | NY | SOL-11158 | 28474.6 | 27807.7 | 666.9 | 2.398% | 28774 | -299.4 | -1.041%
M025 | NY | SOL-10392 | 10017.5215 | N/A |  |  | 24960 | -14942.4785 | -59.87% | 1. Inverter 1 tripped offline at 13:30 on 03/06, reporting a "Fault" and later self-resolved and back online at 13:30 on 04/10. It again tripped offline at 15:00 on 04/13 and reporting '3 Phase Possible Arc Detection'. After remotely unlocking the inverter, it is back online at 07:00 AM on 04/14. and again Inverter 1 tripped offline at 14:45 on 04/17 and reporting '3 Phase Possible Arc Detection, and the continued throughout the month. This is currently being addressed under EPC. 2. Inverter 3 has tripped offline at 12:15 on 03/07 and reporting a "Generic Fault" and later self resolved and back online at 13:30 on 04/10. 3.Multiple optimizers are offline and pending EPC. 4. Inverter 1 right unit is tripped offline at 15:00 on 04/14, reporting a '3 Phase Possible Arc Detection' fault. Additionally, the middle unit tripped offline at 15:00 on 04/15 and continued throughout the month and adressing this issue under EPC. 5. Inverter 2 middle unit is tripped offline at 12:00 on 04/13, reporting a '3 Phase Possible Arc Detection' fault and continued throughout the month and adressing this issue under EPC. 6. Inverter 3 middle unit tripped offline at 13:00 on 04/13 and reporting "3 Phase Possible Arc Detection" fault, Additionally left unit has tripped offline at 16:00 on 04/15 and continued throughout the month and adressing this issue under EPC. | 1. SR098235, SR099791 2. SR098264 3. SR095956 4. SR099791 5. SR099792 6. SR099793 | SR099791 | SR098264 | SR095956 | SR099791 | SR099792 | SR099793
M028 | NY | SOL-10381 | 19247.7108 | N/A |  |  | 19348 | -100.2892 | -0.5183%
Q030 | NY | SOL-10878 | 23074.4142 | N/A |  |  | 23554 | -479.5858 | -2.036%
Q130 | NY | SOL-10877 | 13305.3633 | N/A |  |  | 13284.82 | 20.5433 | 0.1546%
Q196 | NY | SOL-10879 | 17258.2403 | N/A |  |  | 17187 | 71.2403 | 0.4145%
Q220 | NY | SOL-10873 | 20521.2734 | 0 | 20521.2734 |  | 19984 | 537.2734 | 2.689% | 1. Weather station stopped communication at 17:00 on 02/22 and adressing this issue under EPC. | 1. SR100524
Q205 | NY | SOL-10922 | 24109.1172 | 26692.9 | -2583.7828 | -9.68% | 23997 | 112.1172 | 0.4672% | 1. Inverter 2 middle unit tripped offline at 12:00 PM, reporting grid voltage. It experienced frequent and intermittent trips over several days during the month but later self-resolved on 04/20. | 1. SR100036
Q400 | NY | SOL-10871 | 27707.125 | N/A |  |  | 38017 | -10309.875 | -27.12% | 1. A few strings are offline. EPC to complete. 2. Inverter 3 tripped offline at 14:45 on 03/12 and reporting generic fault and later back online at 11:00 AM on 04/08 . 3. Inverter 1 middle unit has tripped offline at 16:00 on 03/19 and reporting "Ground Current RCD" and adressing this issue under EPC later self resolved at 10:00 AM on 04/08. additionally Inverter 1 left unit tripped offline at 12:00 PM on 04/17 and continued throughout the month and adressing this issue under EPC. 4. Inverter 3 middle unit offline on 04/14 and continued throughout the month and adressing this issue under EPC. 5. Inverter 2 middle unit tripped offline at 15:15 on 04/28 through out the month. | 1. SR095941 2. SR098413,SR098490 3. SR099138 4. SR099857 5. SR100587 | SR098413 | SR098490 | SR099138 | SR099857 | SR100587
R003 | NY | SOL-10416 | 34622.0386 | N/A |  |  | 35285 | -662.9614 | -1.879%
R007 | NY | SOL-10417 | 35700.6719 | N/A |  |  | 36329 | -628.3281 | -1.73%
BK16 | NY | SOL-11093 | 37304.8047 | N/A |  |  | 37404 | -99.1953 | -0.2652% | 1.Inverter 1 is underperforming from 02/19, possibly one unit tripped offline. EPC to address the issue. | 1.SR097620
Trenton - Trenton East | IL | SOL-11060 | 101250.4998 | 140508.7 | -39258.2002 | -27.94% | 444673 | -343422.5002 | -77.23% | 1.Site tripped offline at 15:45 on 03/14 due to a big windstorm. On 03/15 technician stated that multiple utility poles down and recloser opened. Site was back online at 17:00 on 04/18. Site was again tripped offline between 08:45 to 16:15 on 04/21 and between 07:30 to 14:00 on 04/22. 2.Inverter 1 underperforming by 100 kW Inverter 2 underperforming by 5 kW Inverter 7 underperforming by 15 kW Inverter 8 underperforming by 37 kW Trackers have not communicated since 04/23 due to storm damage; EPC is working on partial energization, with trackers in stow and inverters expected to be derated. | 1.SR098602 2.SR100220 | SR100220
Trenton - Trenton West | IL | SOL-11061 | 14787 | 48258.98 | -33471.98 | -69.36% | 445728 | -430941 | -96.68% | 1.Site tripped offline at 9:15AM on 03/17 due to windstorm and no utility and back online at 14:45 on 04/23. Again tripped offline between 7:30 to 16:30 on 04/24, between 08:30 to 16:30 on 04/25 and between 07:45 to 16:30 on 04/28. Again tripped offline between 17:30 to 17:45 on 04/30. | 1.SR098665, SR099161 | SR099161
Dakota - Dakota Solar 1 | IL | SOL-11113 | 404459 | 493295.8 | -88836.8 | -18.01% | N/A |  |  | 1.All trackers are intermittently getting stuck. | 1.SR098315
X018 | NY | SOL-10418 | 10373.8269 | 11138.39 | -764.5631 | -6.864% | 19186 | -8812.1731 | -45.93% | 1.Inverter 1 was underperforming by 13kW compared to its peers since 03/26. 2.Inverter 2 underperforming compared to its peers and reporting a device communication fault since 01/22. | 1.SR099018, SR099951 2.SR096257 | SR099951 | SR096257
Janiak Solar | NY | SOL-10898 | 322430 | 338915.4 | -16485.4 | -4.864% | 362726 | -40296 | -11.11% | 1.The site tripped offline at 4:00 on 04/09 due to an open relay and was brought back online at 8:00 on 04/10 after the technician closed the recloser. | 1.SR099547
County Route 11B | NY | SOL-10983 | 746347 | N/A |  |  | N/A |  |  | 1.Site tripped offline at 19:00 on 04/08 due to a utility recloser pole fire. On 04/15 at 9:05, the technician found the GOAB locked open, closed and locked it, and the site was re-energized and back online. 2.Both the inverters were offline on 04/25 due to Over all work state as stop and Grid voltage unbalance faults and back online at 10:50 on 04/27. On 04/27 technician found a fuse blown which is leading to a phase imbalance causing the inverters not to run. Additional troubleshooting and repairs will need to be scheduled and completed. 3.Several trackers (3, 13, 16, 76, 82, 83, 142, 183) were intermittently stuck since 02/26/25. By 04/25/25, all except trackers 76 and 142 had resolved or were reset during site visits. On 04/15, a technician confirmed that the trackers had been offline but resumed tracking after being powered on. Most alarms cleared, except for addresses 76 and 142. Despite following the TS guide to power cycle TCUs and clear faults, communication issues persist with these two. Due to bad weather, troubleshooting will continue later. | 1.SR099543 2.SR100403 3.SR097816 | SR100403 | SR097816
Barone | NY | SOL-11034 | 580700 | N/A |  |  | 550368.7 | 30331.3 | 5.511% | 1.Site tripped offline between 12:30AM to 10:40AM on 04/13 due to SEL Relay open later technician had reset the relay. 2.All trackers have been stuck at 0 degrees since 03/14 at 11:45 AM, and remote reset did not resolve the issue. The trackers resumed tracking on 04/09 after the issue with the Digi devices was fixed by GC on-site personnel, and the devices are now communicating properly. 3.Trackers 5, 11, 73, & 84 were stuck from 04/27. Tracker 11 resumed tracking on 04/30. | 1.SR099736 2.SR097600 3.SR100609 | SR097600 | SR100609
Cedarville | IL | SOL-11069 | 374283 | 381711.3 | -7428.3 | -1.946% | 419207.7 | -44924.7 | -10.72%
O'Brien Hill #1 | NY | SOL-11098 | 68017 | N/A |  |  | N/A |  |  | 1.Site was offline from 03/07. The utility was contacted again to close the recloser, but the closure was not successful. Further troubleshooting is needed. | 1.SR098278, SR098670 | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 682515.06 | N/A |  |  | N/A |  |  | 1.Site was taken offlline between 13:00 to 15:15 on 04/04 due to EV solar checked in to work on site communication issue. 2.All trackers are stuck in stow mode at 55 degrees from 04/10 and resumed production on 04/25 after technician found a ground wire had pulled out of a cable's fusible link inside Main DAS Cabinet 1 and installed a new crimp on the terminal. | 1.SR099416 2.SR099684, SR100485 | SR099684 | SR100485
Trinity - Freeport | IL | SOL-11057 | 391942 | 280122.1 | 111819.9 | 39.92% | N/A |  |  | 1. TCU 3, 33 through 66 are stuck from 4/24/25 at 13:00CDT. 2.Inverter 2 was derating by anywhere from 5 kW to ~20 kW in the afternoons from 03/28. | 1.SR098066 2.SR099545 | SR099545
Ransom | NY | SOL-11157 | 761571 | N/A |  |  | N/A |  |  | 1.Site tripped offline at 15:45 on 04/11. On 04/12 technician found the GOAB locked open with 2 locks(one was opened by NYSEG). Site back online at 14:00 on 04/14. Again site trippped offline at 18:40 on 04/14 due to utility work and back online at 9:00 on 04/17 after EVS repaired GOAB. 2.CB 14 was offline on multiple days of the month. 3.Tracker W-050, Trackers W-159 & W-166 are stuck at 45 deg & 0deg. Additionally, trackers E- 82, E-83, E-167, E-168, E-169 are deviating during 12:00PM to 17:00PM multiple days of the month. | 1.SR099715, SR099788 2.SR099974 3.SR099473 | SR099788 | SR099974 | SR099473
Horseheads - Wedge | NY | SOL-11160 | 504647 | N/A |  |  | N/A |  |  | 1.Trackers 101-114 were not tracking and the large group of trackers was the last and may be misconfigured. GC looking for tracker plans of the site. | 1.SR099014
Otisville - Shoddy Hollow | NY | SOL-11185 | 883361.3 | N/A |  |  | N/A |  |  | 1.Site was offline from 10:50 to 11:20 on 04/16. 2.Combiner box 15 was offline from 08:35 to 15:40 on 04/17. 3.Trackers 55 and 013 are stuck, while 063, 062, 110, and 111 consistently get stuck around 2–3 PM. On 04/24 EV Solar checked in and the CT has been replaced on inverter 1 Phase B, and the site has been taken offline from 09:10 AM to 11:00 AM during process. 4.Inverter 1 is underproducing 200kW due to module 1-2 is tripped offline at 14:40 on 04/29. | 1.SR099881 2.SR099943 3.SR098693 4.SR100729 | SR099943 | SR098693 | SR100729
Wellsville - Chenunda Creek | NY | SOL-11187 | 424764.9 | N/A |  |  | N/A |  |  | 1.Site was taken offline by EPC from 10:40 to 14:30 on 04/14 for repairs. 2. From 04/09 Tracker 46 stuck at -49.9 degrees and CB09 production is impacting end of the day. Tracker resumed tracking from 04/17. 3.All combiner boxes are tripping on and off on 04/17 due to EV solar performed IV Curve testing. 4.On 04/27, All trackers were stuck at 49.8° from 12:50 PM, impacting production. They resumed normal operation by 3:30 PM on same day. 5.Inverter tripped offline at 13:30 on 04/29 due to Over all work as STOP fault and back online at 17:50 on 04/30. | 1.SR099770 2.SR099595 3.SR099946 4.SR100462 5.SR100662 | SR099595 | SR099946 | SR100462 | SR100662
DC: Washington - Essex Condominium | DC | SOL-10036 | 3803 | 4645.736 | -842.736 | -18.14% | 5003.589 | -1200.589 | -23.99%
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 8225 | 10609.08 | -2384.08 | -22.47% | 12308.47 | -4083.47 | -33.18%
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 12389 | 9959.866 | 2429.134 | 24.39% | 12301.88 | 87.12 | 0.7082%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## May
Generate Capital |  |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  |  | 32404625.8206 | 12561028.138 | 19843597.6826 | 158% | 46534590.29 | -14129964.4694 | -30.36% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 21436.75 | 35068.5 | -13631.75 | -38.87% | 40520.26 | -19083.51 | -47.1% | 1. Low production/generation due to rain on 05/05, 05/09 & 05/14.
K041 | NY | SOL-10357 | 25124.5 | 28857.02 | -3732.52 | -12.93% | 30517 | -5392.5 | -17.67% | 1.Inverter module 1.0.71 is offline, reporting "No communication with Power Optimizer | 1.SR093289
K043 | NY | SOL-10358 | 31607.063 | 31512.477 | 94.586 | 0.3002% | 6701.39 | 24905.673 | 371.6% | 1.Estimated values are low in AE we have also verified the file which was given by GC
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 30639 | -30639 | -100% | 1.Site was offline from 02/21 due to Phase C fuse was blown and parts were needed. | 1.SR097569
K115 | NY | SOL-10361 | 5905.25 | 10305.36 | -4400.11 | -42.7% | 17376.71 | -11471.46 | -66.02% | 1. 96 optimizers are down for site construction. | 1.SR093291
K152 | NY | SOL-10362 | 9130.9688 | 9635.483 | -504.5143 | -5.236% | 11639 | -2508.0312 | -21.55% | 1. Low production/generation due to rain on 05/05, 05/09 & 05/14.
K166 | NY | SOL-10363 | 33771.875 | 36654.39 | -2882.515 | -7.864% | 42600.89 | -8829.015 | -20.72% | 1. Low production/generation due to rain on 05/05, 05/09 & 05/14.
K206 | NY | SOL-10927 | 20067.3125 | 19533.63 | 533.6825 | 2.732% | 22532 | -2464.6875 | -10.94% | 1. Low production/generation due to rain on 05/05, 05/09 & 05/14.
K251 | NY | SOL-10365 | 21288.375 | 0 | 21288.375 |  | 26796.3 | -5507.925 | -20.55% | 1.Weather station stopped communicating since 11/22/24 | 1.SR093633
K269 | NY | SOL-10366 | 19990.3125 | 23304.22 | -3313.9075 | -14.22% | 24102.37 | -4112.0575 | -17.06% | 1. Low production/generation due to rain on 05/05, 05/09 & 05/14.
K273 | NY | SOL-10367 | 21148.875 | 0 | 21148.875 |  | 32475 | -11326.125 | -34.88% | 1.26 optimizers are down for roof repair. 2.Inverter 2 unit 2.2 ( left unit) is offline since 05/04/25 due to "DC Isolation" and back online on 05/10 at 16:30 and again offline on 05/14 and back online on 05/18 on 08:15 again offline from 05/22 and self resolved on 05/25 at 13:00 3.Weather station stopped communicating since 06/14/24. | 1.SR093294 2.SR098958 3.SR086842 | SR098958 | SR086842
K287 | NY | SOL-10919 | 17273.5625 | 15150.06 | 2123.5025 | 14.02% | 21348 | -4074.4375 | -19.09% | 1. Low production/generation due to rain on 05/05, 05/09, 05/14 & 05/22.
K298 | NY | SOL-10368 | 18981.4688 | 19993.5 | -1012.0312 | -5.062% | 24419 | -5437.5312 | -22.27% | 1. Low production/generation due to rain on 05/05, 05/09, 05/14 & 05/22.
K335 | NY | SOL-10370 | 19889.5 | 22277.63 | -2388.13 | -10.72% | 26929 | -7039.5 | -26.14% | 1. Site was offline from 11:02 to 11:21 on 05/30 due to technician was onsite for preventive maintenace work. 2. Low production/generation due to rain on 05/05, 05/09, 05/14 & 05/22. | 1. PM8144
K345 | NY | SOL-10920 | 23306.2188 | 13816.51 | 9489.7087 | 68.68% | 28171 | -4864.7812 | -17.27% | 1. Low production/generation due to rain on 05/05, 05/09, 05/14 & 05/22.
K445 | NY | SOL-10373 | 19136.25 | 20974.76 | -1838.51 | -8.765% | 22605.72 | -3469.47 | -15.35% | 1. Low production/generation due to rain on 05/05, 05/09, 05/14 & 05/22.
K495 | NY | SOL-10374 | 77124.875 | 80257.29 | -3132.415 | -3.903% | 96985.07 | -19860.195 | -20.48% | 1.Inverter 11 (left unit) was offline since 04/18, reporting a "DC Isolation Fault." During troubleshooting, it was discovered that following a firmware update, the inverter no longer displayed fault codes and continued to fail to produce power. SolarEdge technical support was contacted, and a callback was received. Case number 5713468 was created. | 1.SR101786
M020 | NY | SOL-10380 | 18998.1562 | 22034.82 | -3036.6637 | -13.78% | 26418 | -7419.8438 | -28.09% | 1.Inverter 2 unit 2.3(middle unit) is didn't started for the production on 05/18, later technician has found defective optimizer causing inverter to fault. Replaced optimizer, inverter middle unit is back online on 05/22 at 12:00 | 1.SR101646
M092 | NY | SOL-10383 | 19958.3125 | 21332.72 | -1374.4075 | -6.443% | 25140.73 | -5182.4175 | -20.61% | 1. Site was offline from 10:46 to 11:06 and 11:54 to 12:08 on 05/22 due to technician was onsite for preventive maintenace work. 2. Low production/generation due to rain on 05/05, 05/14 & 05/22. | 1. PM8074
M143 | NY | SOL-10384 | 22306 | 26674.51 | -4368.51 | -16.38% | 28183.46 | -5877.46 | -20.85% | 1.Inverter 3 left unit is having multiple tripping from 05/10. On 05/23 technician has troubleshot with Solaredge and if inverter 3 left unit continues to trip a relay board will be shipped. | 1.SR101363
M144 | NY | SOL-10385 | 33062.0625 | 36664.14 | -3602.0775 | -9.825% | 48015.14 | -14953.0775 | -31.14% | 1. Low production/generation due to rain on 05/05, 05/14 & 05/22.
M167 | NY | SOL-10386 | 25394.9688 | 18995.12 | 6399.8488 | 33.69% | 34279.88 | -8884.9112 | -25.92% | 1. Low production/generation due to rain on 05/05, 05/14 & 05/22.
M188 | NY | SOL-10387 | 16312.0938 | 18711.31 | -2399.2163 | -12.82% | 24466.27 | -8154.1763 | -33.33% | 1. Inverter 2 is back online on 05/01 2.Inverter 1 (right, middle units) and Inverter 2 (left, middle units) has tripped offline due to "3 Phase Possible Arc Detection" on 05/10 at 12:45, later technician has toggled and disconnected the DC switches and turned to OFF positions and has covers removed and units are back online at 09:00 on 05/15. | 1.SR100476 2.SR101267 | SR101267
EMHC | NY | SOL-10351 | 7420.0156 | 6261.367 | 1158.6486 | 18.5% | 11538.26 | -4118.2444 | -35.69% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 34336 | -34336 | -100% | 1.Site stopped communicating from 03/25. On 03/27 Technician stated that main breaker tripped and malfunctioning. Site was remained offline till date. Will need to replace 400amp breaker and lugs for 500 KC MIL wire. | 1. SR098981
Q018 | NY | SOL-10398 | 18590.5625 | 18781.92 | -191.3575 | -1.019% | 21124.54 | -2533.9775 | -12% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q021 | NY | SOL-10399 | 14804.9688 | 14261.11 | 543.8587 | 3.814% | 17717.82 | -2912.8512 | -16.44% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q025 | NY | SOL-10400 | 25441.375 | 25325.86 | 115.515 | 0.4561% | 15072 | 10369.375 | 68.8%
Q074 | NY | SOL-10402 | 16785.8125 | 16862.68 | -76.8675 | -0.4558% | 20108.2 | -3322.3875 | -16.52% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q115 | NY | SOL-10872 | 20876.125 | 22397.69 | -1521.565 | -6.793% | 26296.24 | -5420.115 | -20.61% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q139 | NY | SOL-10403 | 12977.75 | 14622.39 | -1644.64 | -11.25% | 17028 | -4050.25 | -23.79% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q157 | NY | SOL-10404 | 22952.0625 | 24578.17 | -1626.1075 | -6.616% | 29961.49 | -7009.4275 | -23.39% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q192 | NY | SOL-10406 | 35333.875 | 38608.28 | -3274.405 | -8.481% | 43528.92 | -8195.045 | -18.83% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q210 | NY | SOL-10407 | 28812.875 | 29402.13 | -589.255 | -2.004% | 36236 | -7423.125 | -20.49% | 1. Site was offline from 09:07 to 10:07 on 05/14 due to technician was onsite for preventive maintenance work. 2. Site was offline from 10:56 TO 11:17 on 05/19 due to technician was onsite for preventive maintenance work. | 1. PM2173 2. PM8123
Q229 | NY | SOL-10408 | 12689.875 | 14323.36 | -1633.485 | -11.4% | 15713.58 | -3023.705 | -19.24% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1. SR088813
Q231 | NY | SOL-10870 | 46209.375 | 49357.63 | -3148.255 | -6.378% | 56670 | -10460.625 | -18.46% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q405 | NY | SOL-10409 | 50854.75 | 59419.38 | -8564.63 | -14.41% | 64917.55 | -14062.8 | -21.66% | 1. 4 Inverter modules are offline. Will investigate next time on site. Module 1.0.64 Module 4.0.39 , 3.0.20 ,1.0.64 | 1. SR093324
Q435 | NY | SOL-10923 | 66882.4375 | 56241.41 | 10641.0275 | 18.92% | 80887 | -14004.5625 | -17.31% | 1. Inverter 5 left unit tripped offline at 12:30 ON 05/25 and reporting "Grid Voltage" self resolved and back online on 05/27 2.Inverter 3 middle unit and inverter 5 left unit has tripped offline on 05/11 and reporting "AC Voltage Too High". On 05/12 middle unit and left units are back online. | 1.SR099970 2. SR101290 | SR101290
Q485 | NY | SOL-10869 | 62145.125 | 50337.7 | 11807.425 | 23.46% | 76614.21 | -14469.085 | -18.89% | 1.On 04/29 at 16:00, inverter 1 Right Unit tripped offline. On 05/01 at 07:45 AM, Inverter 1 tripped offline again and reported error code 03x9B in the SolarEdge monitoring system. On 05/02, both Inverter 1 Right and Left Units went offline , middle unit online. On 05/06, a technician tested the optimizers and replaced Inverter 1. 2. Inverter 3 middle unit offline. Reporting fault in AE and production issue detected in SE. On 05/16 technician found bad optimizer and replaced in the string 5. Middle unit is reenergized and all 3 units in inverter 3 are online. Inverter is now producing. Defective optimizer has been RMA'd. | 1. SR100803 2. SR101356 | SR101356
Q490 | NY | SOL-10411 | 45396.5 | NA |  |  | 56275.36 | -10878.86 | -19.33% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1. SR093326
Q620 | NY | SOL-10867 | 68002 | 69136.85 | -1134.85 | -1.641% | 80133.62 | -12131.62 | -15.14% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
QMOA | NY | SOL-10415 | 5822 | NA |  |  | 6997.682 | -1175.682 | -16.8% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
X024 | NY | SOL-10419 | 25287.875 | 26148.77 | -860.895 | -3.292% | 30453 | -5165.125 | -16.96% | 1. On 02/05, the technician onsite found a faulty optimizer while troubleshooting the central unit of Inverter 2. Technician noted that the optimizer would need to be replaced and initiated an RMA on the same day. The optimizer still needs to be replaced during the next onsite visit. | 1. SR096294
X026 | NY | SOL-10420 | 22873.4 | 20965 | 1908.4 | 9.103% | 39656.197 | -16782.797 | -42.32% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1.SR095662
X090 | NY | SOL-10925 | 19383.25 | 17377.444 | 2005.806 | 11.54% | 23401.742 | -4018.492 | -17.17% | 1. Site production was low on 05/03 to 05/05, 05/07, 05/09, 05/13, 05/14, 05/22 due to rain.
X117 | NY | SOL-10422 | 15725.9 | 18001.473 | -2275.573 | -12.64% | 21263.503 | -5537.603 | -26.04% | 1. Site was offline from 8:15 to 9:45 on 05/08 due to technician was onsite for preventive maintenance work. | 1. PM8103
X125 | NY | SOL-10423 | 30249.75 | 31532.214 | -1282.464 | -4.067% | 36059.164 | -5809.414 | -16.11% | 1. Site was offline from 8:15 to 9:15 on 05/12 due to technician was onsite for preventive maintenance work. | 1. PM8003
X134 | NY | SOL-10424 | 29069.219 | 30539.796 | -1470.577 | -4.815% | 36309.354 | -7240.135 | -19.94% | 1. Site production was low on 05/03 to 05/05, 05/07, 05/09, 05/13, 05/14, 05/22 due to rain.
X135 | NY | SOL-10425 | 23534.406 | 22643.746 | 890.66 | 3.933% | 28985.517 | -5451.111 | -18.81% | 1. Site production was low on 05/03 to 05/05, 05/07, 05/09, 05/13, 05/14, 05/22 due to rain.
X139 JHS 222 | NY | SOL-10426 | 36602.392 | 39736.466 | -3134.074 | -7.887% | 45112.114 | -8509.722 | -18.86% | 1. Site production was low on 05/03 to 05/05, 05/07, 05/09, 05/13, 05/14, 05/22 due to rain.
X140 | NY | SOL-10926 | 20987.125 | 17423.44 | 3563.685 | 20.45% | 24233 | -3245.875 | -13.39% | 1. Site production was low on 05/03 to 05/05, 05/07, 05/09, 05/13, 05/14, 05/22 due to rain.
X166 | NY | SOL-10427 | 21361 | 21039.116 | 321.884 | 1.53% | 26944.807 | -5583.807 | -20.72% | 1. Site was offline from 9:11 to 9:31 on 05/05 due to technician was onsite for preventive maintenance work. | 1. PM2150
Murphy | MN | SOL-10094 | 910700 | 1021693 | -110993 | -10.86% | 942079.6 | -31379.6 | -3.331% | 1.Inverter 4 was offline on 05/24 reporting "Modules emergency fault" and was back online at 09:45CDT on 05/25,it was again tripped off at 17:45CDT on 05/25. Technician checked in and stated that it has a bad AC capacitor on Module 3 which is not safe to run so it was disabled but 1 and 2 are producing in that inverter and inverter is back online at 10:45 CDT on 05/27. 2. Inverter A was offline at 15:15 CDT on 05/12,on 05/14 technician checked in found an ground fault on detector after resetting the alarms and powercycled inverter it was back online at 13:15CDT on 05/22.It was again tripped offline on 05/23 and was back online on 05/27. 3.Inverter A was derating by 130 kW from 4/21/25. After technician checked in on 05/05 he discovered in the first cabinet the 3 main breakers were not closing and he performed reset after which inverter started producing normally. | 1.SR101910 2.SR101354 3.SR100141 | SR101354 | SR100141
Terning | MN | SOL-10093 | 1038972 | 1072323 | -33351 | -3.11% | 943772.2 | 95199.8 | 10.09%
Boas Road 04 | NY | SOL-10908 | 0 | 285541.91 | -285541.91 | -100% | 380347.01 | -380347.01 | -100% | 1. Inverter 1 didn't start for production on 05/17 and reporting "SE VBUS NEG DERIVATIVE FAULT ". On 05/19 echnician found that three strings were damaged and required additional troubleshooting. 2. Meter stopped communicating from 14:05 on 03/16 till date. | 1.SR101620 2. SR098641 | SR098641
Kelly Bridge Farm | NY | SOL-10911 | 0 | 312509.3 | -312509.3 | -100% | 378396.52 | -378396.52 | -100% | 1. Inverter 26 was derated by 39kW down on 05/08 and from 05/13 to 05/19. 2. Numerous inverters are experiencing multiple trippings from 05/01 to 05/12. 3. Site was de-energised by technician on 05/07 from 08:35am to 10:35am to troubleshoot meter. Meter is not communicating from 03/16. Technician removed meter and shorted CTs. Meter was tested by Measulogic and no issues found. IP address may be the issue. | 1. SR101641 2. SR100447 3. SR098640 | SR100447 | SR098640
Pool Brook Road | NY | SOL-10909 | 265159 | 270156.58 | -4997.58 | -1.85% | 374337.91 | -109178.91 | -29.17% | 1. Site production was low 05/02 to 05/07, 05/09, 05/17, 05/22 to 05/24 due to rain.
Sackett Lake | NY | SOL-10910 | 142347 | 302419.78 | -160072.78 | -52.93% | 375323.01 | -232976.01 | -62.07% | 1. Inverter 2 was offline for whole month and inverter being RMA'd. | 1. SR100623, SR099149, SR101482 | SR099149 | SR101482
Burritt Road | NY | SOL-10913 | 329840 | 351436.43 | -21596.43 | -6.145% | 387566.99 | -57726.99 | -14.89% | 1. Technician took inverter 7 offline on 05/08 from 11:10am to 12:05pm. | 1. PM7532
Villa Roma 1 | NY | SOL-10914 | 274928 | 146.62 | 274781.38 | 187411% | 361531.61 | -86603.61 | -23.95% | 1.Expected energy values are reporting very low. Created a case #66639 with GPM, As per GPM the BOM has been frozen from 02/27. | 1. SR099403
Villa Roma 2 | NY | SOL-10915 | 272744 | 276952.67 | -4208.67 | -1.52% | 350695.51 | -77951.51 | -22.23% | 1. Site production was low on 05/04, 05/05, 05/09, 05/10, 05/22 and 05/31 due to rain.
Washington 1 | NY | SOL-10912 | 343030 | 352474.11 | -9444.11 | -2.679% | 383203.8 | -40173.8 | -10.48% | 1. Site production was low on 05/03, 05/07, 05/08, 05/21 to 05/24, 05/28 due to rain.
Washington 3 | NY | SOL-10828 | 385488 | 0 | 385488 |  | 469462.09 | -83974.09 | -17.89% | 1. Inverter 2 was tripped offline on 04/30 due to bad inductor fan and Inverter was back online on 05/07 at 09:45 am after technician replaced inductor. 2. Combiner Box #7 requires additional troubleshooting. 3. POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1. SR100629 2. SR100190 3. SR093024 | SR100190 | SR093024
Washington 4 | NY | SOL-10829 | 328690.8 | 422376.6 | -93685.8 | -0.22181 | 470453.1 | -141762.3 | -30.13% | 1. The site was offline from 11:35 AM on 05/15 to 3:35 PM on 05/16 while technicians were onsite working on the combiner boxes. CB 4 will remain offline until the DC switch is replaced in Inverter 1. On 05/28, a technician was onsite and took the site offline to work on the inverters. They replaced the DC switch on Inverter 2, but after troubleshooting, both inverters were left offline and require further investigation. | 1. SR100200, SR098198 | SR098198
Big Tree | NY | SOL-10966 | 334799 | NA |  |  | 396020 | -61221 | -15.46% | 1.Combiner box 7,string 1 is underperforming since 03/21.Needs further investigation. | 1.SR098866
Canoga | NY | SOL-10965 | 0 | NA |  |  | 0 | 0 |  | 1.Site was offline since 09:55 on 03/27 due to utility work at substation. NYSEG is replacing Circuit Switcher with A Vacuum Circuit Breaker estimated time is six weeks. On 05/12 an update was given stating Substation Seneca Falls will be returned to service possibly on 6/15. | 1.SR098998
County Route 84 | NY | SOL-10967 | 766800 | NA |  |  | 954472.22 | -187672.22 | -19.66% | 1.Site tripped offline and meter voltages were dropped to zero at 23:15. On 05/25 site came back online at 00:55 on 05/26. | 1.SR101929
Donati | NY | SOL-10968 | 355625 | NA |  |  | 496637.33 | -141012.33 | -28.39% | 1.Weather station Reporting 0 value from 05/31/24. POA sensors need to be replaced. 2. All trackers have been struck from various dates. Followed up with Soltec and they are working on it. Soltec will be conducting a site visit. | 1.SR092964 2.SR098877,SR095253 | SR098877 | SR095253
Henrietta | NY | SOL-10972 | 649490 | NA |  |  | 1054030.12 | -404540.12 | -38.38% | 1.Site tripped offline at 15:20 on 05/17 and meter voltages were also dropped to zero. Technician checked into site on 05/19 and and closed MV Disconnect switch, site was back online 05/19. 2.Inverters 1 and 2 tripped offline on 05/05. Inverter 1 showed no fault code, while Inverter 2 reported 'Vac out of range. On 05/06, a technician checked in and stated that both inverters would remain offline until Transformer 1 was tested and repaired. After the transformer was repaired, both inverters were brought back online at 12:40. On 05/15, Inverter 3 tripped offline at 12:40 due to being in stop mode. It was brought back online at 13:15 on 05/16 after the technician changed its operating mode and restarted it. | 1.SR101625 2.SR101020 | SR101020
NY 70 | NY | SOL-10970 | 886000 | NA |  |  | 1183305.28 | -297305.28 | -25.12% | 1. Inverters 3 and 4 tripped offline at 20:05 on 04/30. On 05/01, the technician confirmed the inverters were producing power but had no communication. A faulty NPort-3 was found, and as instructed by GPM tech support, an RMA was initiated. On 05/19, the technician replaced the RMA’d part with a new one, restoring inverter and meter communication at 15:45. 2. Inverter 1 was offline since 04/28. On 05/05 technician replaced exterior and interior filters brought inverter back online at 14:00. | 1. SR100387, SR100721 & PM7743 2. SR100387 | SR100721 | SR100387
Reid | NY | SOL-10991 | 616581.1317 | 583641.8 | 32939.3317 | 5.644% | 970735 | -354153.8683 | -36.48% | 1. Inverter 9 came back online at 10:30 on 05/02 after the breakers were reset. It tripped offline again at 13:00 on 05/10 and was brought back online at 09:00 on 05/13 by resetting the breakers. It tripped again at 14:15 the same day due to "Inverter/Irradiance Check" and "Grid Line Voltage Out of Range," and came back online at 11:45 on 05/21 after the technician reset the breaker. It tripped once more at 10:30 on 05/27 and was brought back online at 08:15 on 05/30 after the technician closed the AC breaker. 2. Inverter 30 tripped offline at 12:25 on 05/10, reporting "Grid Line Voltage Out of Range," and came back online at 09:15 on 05/13 after resetting the breaker. It tripped again at 13:15 on 05/16 and was back online at 11:15 on 05/21 after resetting the breaker. It tripped once more at 12:15 on 05/26 and came back online at 08:15 on 05/30 after the technician closed the AC breaker. 3. Inverter 28 tripped offline at 12:55 on 05/10, reporting "Grid Line Voltage Out of Range," and was back online at 09:15 on 05/13 after resetting the breakers. It tripped again at 13:45 on 05/16 and came back online at 11:15 on 05/21 by resetting the breaker. It tripped once more at 14:00 on 05/26 and was brought back online at 08:15 on 05/30 after the technician closed the AC breaker. 4. Inverter 5 tripped offline at 15:45 on 05/11, reporting "Grid Line Voltage Out of Range," and came back online at 09:00 on 05/13 by resetting the breaker. It tripped again at 13:00 on 05/27 and was brought back online at 08:15 on 05/30 after the technician closed the AC breaker. 5. Inverter 6 tripped offline at 13:45 on 05/24, displaying the alarm "Bus Imbalance - Protect0070." On 05/30, the technician inspected the unit, initiated an RMA, and the inverter remained offline for the rest of the month. 6. Inverter 32 tripped offline at 12:45 on 05/27 and was brought back online at 08:15 on 05/30 after the technician closed the AC breaker. | 1. SR100811, SR101403 & SR101938 2. SR101263, SR101594 & SR101938 3. SR101263, SR101594 & SR101938 4. SR101263 & SR101938 5. SR101912 6. SR101938 | SR101403 | SR101938 | SR101263 | SR101594 | SR101938 | SR101263 | SR101594 | SR101938 | SR101263 | SR101938 | SR101912 | SR101938
Sangolqui | NY | SOL-10975 | 354940 | NA |  |  | 486092.87 | -131152.87 | -26.98% | 1. Site production was low on 05/03, 05/04, 05/21 to 05/23 due to rain.
State Highway 17B | NY | SOL-10988 | 683720 | NA |  |  | 753209.85 | -69489.85 | -9.226%
State Route 14A | NY | SOL-10997 | 190293 | NA |  |  | 966912.78 | -776619.78 | -80.32% | 1. Site was offline since 04/03. On 05/14 USNE replaced the SEL relay and CAT5 cable brought site back online at 12:55. It went offline again on 05/22. On 05/23, the technician re-energized the site, but it was shut down after Transformer 2 showed signs of internal arcing. Further MV troubleshooting is required, and the site will remain offline for safety. | 1. SR099347, SR101820 | SR101820
West Creek | NY | SOL-10995 | 565640 | NA |  |  | 985279.61 | -419639.61 | -42.59% | 1. Site was offline from 14:00 on 05/08 and back online at 15:20 on 05/12 after utility power restored. 2. Site tripped offline at 16:25 on 05/13. On 05/16/25, the technician found the utility recloser in the open state. After inspecting the site, the technician contacted NYSEG. According to NYSEG, a crew was working on the utility line. Power was restored, and the site came back online at 16:25 the same day and site was again offline from 14:00 on 05/19, back online at 8:30 on 05/20/25 after technician power cycled the DAS. | 1. SR101160 2. SR101416 | SR101416
Wildflower | NY | SOL-10982 | 637034 | NA |  |  | 991234.8 | -354200.8 | -35.73% | 1.Inverter 2 tripped offlline at 15:30 on 05/04 with an "AL_CODE3_AC_CONTACTOR" fault. On 05/09, the technician swapped its AC contactor and reset both inverters from 50Hz to 60Hz. After replacing the K2 relay, inverter 2 restarted at 16:00; inverter 1 remains off due to a faulty breaker. 2. Inverter 1 tripped at 10:25 on 05/07 with an "SE PERSISTENT ERROR" and returned online at 15:30 the same day as the issue self-resolved. It stayed offline after swapping the K2 relay with inverter 2 on 05/09. On 05/16, the technician replaced the K2 relay with a new RMA part, and inverter 1 was back online at 11:15. | 1. SR100997 2. SR100997, SR101109 | SR100997 | SR101109
Glen Mary 1 | NY | SOL-10993 | 564170 | NA |  |  | 1014571.98 | -450401.98 | -44.39% | 1. Site was offline from 15:25 to 19:05 on 05/06 due to a brife outage. 2. Site was offline from 14:10 on 05/19/25 and restored at 14:35 on 05/21 after the technician power cycled the DAS. It went offline again on 05/22 due to utility line damage and came back online at 14:25 after utility power was restored. | 1. SR101078 2. SR101078, SR101652 | SR101078 | SR101652
Glen Mary 2 | NY | SOL-10994 | 248380 | NA |  |  | 432204.17 | -183824.17 | -42.53% | 1. Site was offline from 15:25 to 19:20 on 05/06 due to a brife outage. 2. Site was offline from 15:10 on 05/22 due to an line damage at utility end and came back online at 14:25 on 05/28 after utility power restores. | 1. SR101079 2. SR101079 | SR101079
Telegraph 1 | NY | SOL-11003 | 609457 | NA |  |  | 722853.26 | -113396.26 | -15.69% | 1. Site production was low on 05/03, 05/04, 05.13, 05/21 to 05/23 due to rain.
Telegraph 2 | NY | SOL-11004 | 322890 | NA |  |  | 376205.85 | -53315.85 | -14.17% | 1. Site production was low on 05/03, 05/04, 05/13, 05/21 to 05/23 due to rain.
Cafferty Hill | NY | SOL-10996 | 699070 | NA |  |  | 925815.16 | -226745.16 | -24.49% | 1. Site production was low on 05/03, 05/04, 05/09, 05/21 to 05/23, 05/28 due to rain.
Dunkleman | NY | SOL-11008 | 931420 | NA |  |  | 1222284.26 | -290864.26 | -23.8% | 1. Currently, the following trackers are stuck Group 1: 57 & 119 Group 2: 24, 27, 32, 36, 39, 43, 54, 59, 61, 97, 114, & 124. A total of 14 tracker control units are struck. | 1. SR095109
Route 19 1 | NY | SOL-11001 | 384140 | NA |  |  | 492648.27 | -108508.27 | -22.03% | 1. Site production was low on 05/03, 05/13, 05/21 to 05/24, 05/28 due to rain.
Route 19 2 | NY | SOL-11002 | 926520 | NA |  |  | 1226350.14 | -299830.14 | -24.45% | 1. Site production was low on 05/03, 05/13, 05/21 to 05/24, 05/28 due to rain.
Yellow Mills 1 | NY | SOL-11006 | 309410 | NA |  |  | 416192.42 | -106782.42 | -25.66% | 1. Site was offline from 05:05 to 16:05 on 05/18 due to a brief outage. 2. Site was taken offline from 11:00 to 12:40 on 05/20 to work on Preventative maintenance. | 1. SR101632 2. PM7738
Yellow Mills 2 | NY | SOL-11005 | 325193 | NA |  |  | 429297.84 | -104104.84 | -24.25% | 1. Site was offline from 05:05 to 16:05 on 05/18 due to a brief outage. 2. Site was taken offline from 12:40 to 14:15 on 05/20 to work on Preventative maintenance. | 1. SR101091 2. PM8086
Yellow Mills 3 | NY | SOL-11007 | 319142 | NA |  |  | 411178.38 | -92036.38 | -22.38% | 1. Site was offline from 05:05 to 16:05 on 05/18 due to a brief outage. | 1. SR101633
Catskill | NY | SOL-11021 | 575300 | NA |  |  | 720288.86 | -144988.86 | -20.13% | 1. Site production was low on 05/03, 05/05, 05/09, 05/21 to 05/24, 05/28 due to rain.
Eddy Ridge | NY | SOL-11054 | 466429 | NA |  |  | 589040 | -122611 | -20.82% | 1. Site was taken offline from 12:20 to 14:15 on 05/06, the technician replaced the PT board in the inverter. 2. Inverter is exceeding its curtailment at 2338kW from 5/10/25. | 1. SR099360 2. SR101282 | SR101282
Ridgeway #1 | NY | SOL-11018 | 1046948 | NA |  |  | 1246214.38 | -199266.38 | -15.99% | 1. All trakers are operating normal from 05/13/25. 2. Site was offline from 08:50 to 12:00 on 05/12 due to EV solar was onsite to replace inverter PT boards. | 1. SR100044 2. SR099140 | SR099140
Rivard 1 | NY | SOL-11011 | 867771.6857 | 0 | 867771.6857 |  | 898187.05 | -30415.3643 | -3.386% | 1. The site lost communication at 9:15 AM on 04/12; however, meter production data remained available. On 04/24, the technician found that Pad 1 DAS had a blown 4A fuse. They removed a fuse from Pad 2, but it failed upon re-energization. The technician will need to return with additional fuses. | 1.SR099726
Rivard 2 | NY | SOL-11012 | 825788.245 | 821072.9 | 4715.345 | 0.5743% | 1008005 | -182216.755 | -18.08% | 1. Tracker control 33 - 90, 129 - 136, 148 , 20-32, 123-128, 172-183 are not communicating & tracker 156 , 121 is stuck and production dropped (approxmately ) 25 KW down. | 1.SR095073
Ridgeway #2 | NY | SOL-11027 | 529391 | NA |  |  | 632557 | -103166 | -16.31% | 1. Tracker 53 was stuck at -20° on 04/16 at 12:10 and stopped communicating from 04/17 at 06:30. Additionally, trackers 49, 90, and 96 were stuck from 04/28. All trackers returned to normal on 05/30 after being reset by a technician. | 1. SR100042
Spencer | NY | SOL-11017 | 862283 | NA |  |  | 1213900 | -351617 | -28.97% | 1. Trackers 1 and 170 returned to normal on 05/01 at 16:35. Tracker 1 got stuck again at 54° from 05/03/25. Additionally, Tracker 170 got stuck again at 18:30 on 05/15 and returned to normal on 05/19. From 05/20, Trackers 98 and 10 were stuck at around 14°. Trackers 1, 170, 98, and 10 returned to normal on 05/21 at 16:45. Tracker 1 got stuck again at 54° on 05/26. | 1. SR101152
Reisender | NY | SOL-10886 | 302280 | 302943.39 | -663.39 | -0.219% | 387404 | -85124 | -21.97% | 1.Low production /generation on 05/09,05/14 and 05/22 due to rain
Finney | NY | SOL-10999 | 870110 | NA |  |  | 1165223 | -295113 | -25.33% | 1.Low production /generation on 05/04,05/05 and 05/09 due to rain
Davis Solar | NY | SOL-10958 | 224681 | 326104.5 | -101423.5 | -31.1% | 450157 | -225476 | -50.09% | 1.Inverter 1 tripped offline at 13:45 on 05/04 and was online at 17:00 after a remote reset. 2.Inverter 1 tripped offline at 12:00 on 05/12 due to an insulation failure and came back online at 16:45 on 05/22 after technicians cleared the ground fault .Technicians isolated two strings on Channel 2, CB 12and mentioned it requires additional troubleshooting.On 05/30 ,technician replaced 8 fuses on combiner box CB12 and all the strings of CB 12 are online since then. | 1.SR100032 2.SR101327, SR101956 | SR101327 | SR101956
Genesee | NY | SOL-10951 | 0 | 0 | 0 |  | 942025 | -942025 | -100% | 1.Site remained offline throughout the month.The recloser is opened due to the circuit being out of normal configuration.Dispacth was scheduled in the month of june | 1.SR100101
Landau I | NY | SOL-10891 | 336380 | NA |  |  | 409363 | -72983 | -17.83% | 1.Low production /generation on 05/05, 05/09 and 05/22 due to rain.
Landau II | NY | SOL-10895 | 343090 | NA |  |  | 889569 | -546479 | -61.43% | 1. The site was offline from 07:05 to 09:40 on 05/01 due to a technician being on-site to work on the solar system. 2. Inverter 2 tripped offline at 14:50 on 05/04, reporting that the AC contactor was in the 'OPEN' state. After a remote reset, the inverter came back online at 11:20 on 05/05 but tripped offline again at 12:00 on the same day, reporting an 'Insulation Resistance Failure.' A remote reset was initiated but was unsuccessful, as the inverter continued to fault with the same error even after resetting. Since then, the inverter has been intermittently tripping on and off multiple times throughout the month. 3. Inverter 1 tripped offline at 06:25 on 05/09, reporting an undervoltage fault. A technician inspected the site on 05/12, performed a hard reset, and closed the operator switch on the inverter. The inverter came back online at 13:15 on 05/12. However, it tripped offline again at 07:05 on 05/13, reporting a 'Grid Undervoltage Fast' fault. After a remote reset, the inverter came back online at 09:55 on 05/13.Since then, the inverter has been intermittently tripping on and off multiple times throughout the month. 4. The site went offline at 16:10 on 05/09. A technician visited the site on 05/10, closed the relay, and the site came back online at 11:25 on 05/10. | 1. SR100509 2. SR100448, SR101460, SR101476,SR101572, SR101848 3. SR101225,SR102056 4. SR101237 | SR100448 | SR101460 | SR101476 | SR101572 | SR101848 | SR101225
New Beginnings | NY | SOL-10890 | 247740 | 331745.41 | -84005.41 | -25.32% | 401712 | -153972 | -38.33% | 1. The inverter tripped offline at 19:10 on 05/24. After arriving on site, the technician identified a ground fault that will require two technicians for further troubleshooting. It was also noted that contacting SMA will be necessary for additional support. | 1. SR101915
Bullitt Farm Solar, LLC | NY | SOL-10998 | 772282 | 739504.407 | 32777.593 | 4.432% | 1157050 | -384768 | -33.25% | 1. Site production was low on 05/03,05/07, 05/11, 05/13, 05/14, 05/21 to 05/24 due to rain.
Brodhead Solar, LLC | NY | SOL-10899 | 380716 | 391433.119 | -10717.119 | -2.738% | 506277 | -125561 | -24.8% | 1. NCU 2 tracker 1 stuck since 11/19 and tracker 35 stuck at 11:45 since 01/31 2. NCU 1 tracker 10 stuck at 09:15 since 02/23. Additionally NCU 1 tracker 38 stuck at 21:00 since 05/09. | 1. SR095624 2. SR097725 | SR097725
Svenski | NY | SOL-10894 | 278263 | NA |  |  | 431419 | -153156 | -35.5% | 1. Inverter 1 tripped offline at 14:20 on 05/05, with the AC breaker in the open state and reporting 'STOP: PARAMETER INVOPMOD.' After a successful remote reset, the inverter came back online at 15:40 on 05/05. Additionally, Inverter 1 tripped offline again at 13:15 on 05/08 with the same AC breaker status and error message. It was successfully reset remotely and came back online at 13:40 on 05/08. and again tripped offline at 13:15 on 05/12, and after another successful remote reset, it returned online at 16:05 on 05/12. Inverter is tripping on and off through out the month. | 1. SR101028, SR101305, SR101878 | SR101305 | SR101878
Bantam | NY | SOL-10986 | 108270 | NA |  |  | 1155000 | -1046730 | -90.63% | 1.All trackers are stuck between -56.48 degrees and -60.81 degrees. On 05/08 technician , reset the trackers and then all the trackers started tracking 2.All trackers stuck in snow stow from 05/12. On 05/13 Technician changed the system to auto and the trackers resumed. He also followed up with Nextracker but did not receive a response. Currently, NCU 4 device 1035 is stuck again due to a weak motor and is pending further troubleshooting with the motor rotation tool 3. Inverter 2 tripped offline at 13:10 on 05/18 and displayed an "Insulation Alarm." The AC breaker switch was in the open position. On 05/20, a technician troubleshot the issue, and the inverter came back online at 17:05. However, Inverter 2 tripped offline again at 11:30 on 05/23, reporting "AC breaker switch open." On the same day, a technician performed troubleshooting, and Inverter 2 is now back online. However, five combiner boxes (CB 2-1, CB 2-2, CB 2-6, CB 2-8, and CB 2-10) are currently offline. 4. Inverter 1 tripped offline at 16:40 at 05/26 and is in AC breaker switch in open state. On 05/28 technician found a water intrusion and condensation inside inverter 1 and the DC compartment. No internal damage was found at the inverter. 4 combiner boxes also had intrusions and have been isolated. For safety reasons, the inverter remains offline and further troubleshooting is needed 5. Weather station (POA2,GHI,rPOA ) stopped communicating at 18:10 on 05/27. Will investigate next time onsite | 1. SR101011 2.SR101314 3.SR101647 4. SR101947 5.SR102015 | SR101314 | SR101647 | SR101947 | SR102015
Bogart | NY | SOL-10887 | 315310 | 313452.8 | 1857.2 | 0.5925% | 393903 | -78593 | -19.95% | 1.Combiner boxes 1.12 and 1.13 have been underperforming since 01/27, with an approximate loss of 79 kW. Will investigate during the next onsite visit. | 1.SR096006
Dubois | NY | SOL-10892 |  | NA | [5 empty] | 1.Inverter tripped offline from 12:00 to 15:30 on 05/05 2.Site offline on 05/06 due to utility outage . On 05/07 site back online at 15:24 3. Inverter is offline on 05/18 Freporting F27: modules start fault. F32: Error Mod Self-diagnosis. 9 Logic Status Fault. On 05/19 inverters back online at 17:30 4.Inverter 1.4 module tripped offline on 05/20. On 05/21 technician has reseated the connections between the fans and control board and module 4 began producing normally. 5.Inverters tripped offline from 05/22 due to AC breaker open. On 05/23 technician reenergized the inverters and came back online at 13:00 | 1.SR101022 , SR101023 2. SR101048 3. SR101642 4. SR101845 5.SR101845 | SR101023 | SR101048 | SR101642 | SR101845 | SR101845 |  | SR101942 | SR101997 | SR092209 | SR101998 | SR092751 | SR092255 | SR092095
Salt Point | NY | SOL-10888 | 338230 | NA |  |  | 482241 | -144011 | -29.86% | 1. Trackers – NCU 1 SPC 103 through 115 were stuck starting from 03/18. On 03/19, a technician checked the site and found that the TCU breaker had tripped. A broken panel was also found and needs replacement. A ticket was created, and further troubleshooting is required. On 05/07, the technician repaired the wire and conduit. Additional time is needed on-site to replace more damaged wires and an SPC box that contained a mouse nest. | 1.SR098692
Wheatland 2A | NY | SOL-10971 | 681340 | NA |  |  | 1053225 | -371885 | -35.31% | 1. .14 trackers are currently stuck from 01/06 NCU 1 SPC 111, 112, 118, 205, 305, 307, 310, & 311 & NCU 2 SPC 125, 126, 136, 242, 338, & 341. On 04/15 Technician worked on the trackers, multiple trackers are still not reporting and require further troubleshooting with NexTracker. 2.Technician after replacing two HVPS on 04/28. Currently multiple trackers are still struck and requires additional troubleshooting along with NEXTracker's assistance 3. Inverter 1 tripped offline at 10:45 to 20.:10 on 05/24 and AC Breaker reporting "Open State" 4. Inverter 1 offline from 05/26 due to AC contractor in open position. On 05/28 technician reached out of to SMA for additional troubleshooting. Inverter 1 will remain offline. | 1. SR099686 2. SR094820 3. SR101909 4. SR101931 | SR094820 | SR101909 | SR101931
Wheatland 2B | NY | SOL-10961 | 812620 | NA |  |  | 1046530 | -233910 | -22.35% | 1. 15 trackers are currently stuck from 03/21 NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 | 1. SR098860
Brickchurch | NY | SOL-10889 | 350550 | 335777.97 | 14772.03 | 4.399% | 499952 | -149402 | -29.88% | 1.All NCU 2 trackers have lost communication, while NCU 1 trackers 115-127 remain stuck from 03/27. Previous stuck trackers included 18 on 03/24 and specific units on 03/17 and alos NCU 2 SPC 220, 253, 329, & 338 are stuck from from 05/12 | 1. SR09745 ,SR099118 | SR099118
McCarthy Solar | NY | SOL-10992 | 333660 | NA |  |  | 404377 | -70717 | -17.49% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/14, 05/22, 05/28 due to rain.
Costanza | NY | SOL-10907 | 281340 | NA |  |  | 411426 | -130086 | -31.62% | 1. The site went offline at 12:30 on 05/05 because the customer recloser was open. On 05/06, a technician closed the relay, and the site came back online at 08:50 on 05/06 2.Site tripped offline from 09:35 to 11:39 on 05/08 due to utility outage 3.The site went offline at 12:48 on 05/17. On 05/21, a technician re-energized the site, and it came back online at 14:16. 4.Site was offline from 05/31 due to utility outage | 1.SR101005 2.SR101164 3. SR101616 4. SR102212 | SR101164 | SR101616 | SR102212
Lockenhurst Pond | NY | SOL-11000 | 343913.7164 | 369550 | -25636.2836 | -6.937% | 473503 | -129589.2836 | -27.37% | 1.The site tripped offline from 10:40 to 10:45 on05/30 and SEL opened, meter and relay voltages available. | 1. SR102178
Drinkwater | NY | SOL-10896 | 322920 | NA |  |  | 423973 | -101053 | -23.83% | 1. Site production was low on 05/04, 05/05, 05/09, 05/22, 05/23, 05/24 due to rain.
Altamont | NY | SOL-11085 | 668025 | 683749.6 | -15724.6 | -2.3% | 709911 | -41886 | -5.9% | 1. Site production was low on 05/04, 05/05, 05/09, 05/22, 05/23, 05/24 due to rain.
Krumkill North | NY | SOL-11086 | 624527 | 670096.3 | -45569.3 | -6.8% | 776930 | -152403 | -19.62% | 1. Site production was low on 05/04, 05/05, 05/09, 05/22, 05/23, 05/24 due to rain.
Krumkill South | NY | SOL-11087 | 515330 | 532603.6 | -17273.6 | -3.243% | 609090 | -93760 | -15.39% | 1. Site production was low on 05/04, 05/05, 05/09, 05/22, 05/23, 05/24 due to rain.
X092 | NY | SOL-11189 | 17684.4 | 18009.21 | -324.81 | -1.804% | 22323 | -4638.6 | -20.78% | 1. Site production was low on 05/04, 05/09, 05/21 to 05/23 due to rain.
X093 | NY | SOL-10932 | 1862.1802 | 12441.15 | -10578.9698 | -85.03% | 15637 | -13774.8198 | -88.09% | 1. The site went offline at 13:15 on 03/18 and later self-resolved and back online on 08:00 AM on 04/15 and again tripped offline at 12:00 PM on 04/17 and offline throughout the month, awaiting for EPC to address. On 05/27 Site was back online at 08:45 on 05/27 2. Many optimizers on SE are offline and later back online on 04/15. Additionally 1 optimizer on SE is offline , EPC to complete. | 1. SR098724 2.SR095945 | SR095945
X095 | NY | SOL-10929 | 17538.3477 | NA |  |  | 21123 | -3584.6523 | -16.97% | 1.Currently, the following optimizers are offline or severely underproducing | 1. SR095946
X181 | NY | SOL-10428 | 32339.2838 | NA |  |  | 39535 | -7195.7162 | -18.2% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/14, 05/22, 05/28 due to rain.
X415 | NY | SOL-10429 | 20586.1641 | NA |  | 0% | 23011 | -2424.8359 | -10.54% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/14, 05/22, 05/28 due to rain.
K198 | NY | SOL-10930 | 15353.9688 | 14993.88 | 360.0888 | 2.402% | 17463 | -2109.0312 | -12.08% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/14, 05/22, 05/28 due to rain.
K203 | NY | SOL-11190 | 19346.2 | 17609.03 | 1737.17 | 9.865% | 23537 | -4190.8 | -17.81% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/14, 05/22, 05/28 due to rain. | [7 empty] | SR102056 | SR101237
K213 | NY | SOL-11191 | 19297.6 | 23171.24 | -3873.64 | -16.72% | 24815 | -5517.4 | -22.23% | 1. Inverter 3 tripped offline at 08:05 on 04/17. After the technician checked into the site, he found that the breaker was faulty and its connection to the busbar had overheated. The breaker is currently being replaced, and the inverter is offline throughout the month. | 1. SR099930
K217 | NY | SOL-10933 | 10659.7266 | 0 | 10659.7266 |  | 13842 | -3182.2734 | -22.99% | 1. Inverter 1 left unit tripped offline on 05/10 at 10:15 and reporting "03x9B". On 05/16 Technician found a failed optimizer, troubleshoot the optimizer. Inverter is back online | 1.SR101266
K307 | NY | SOL-10876 | 24381.5 | NA |  |  | 28916 | -4534.5 | -15.68% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/14, 05/22, 05/28 due to rain.
K610 | NY | SOL-11158 | 29119.2 | 28022.01 | 1097.19 | 3.915% | 33621 | -4501.8 | -13.39% | 1. Site was offline at 12:45 from 05/31. | 1. SR102229
M025 | NY | SOL-10392 | 12201.2461 | 25807.5 | -13606.2539 | -52.72% | 28833 | -16631.7539 | -57.68% | 1. Multiple optimizers are offline and pending EPC. 2. Inverter 1 tripped offline at 14:45 on 04/17, reporting '3 Phase Possible Arc Detection,' and came back online at 08:00 on 05/21. The inverter tripped offline again at 14:45 on 05/26. 3. Inverter 1 right unit tripped offline at 15:00 on 04/14, reporting a "3 Phase Possible Arc Detection" fault. Additionally, the middle unit tripped offline at 15:00 on 04/15, and the issue is being addressed under EPC. All units were brought back online at 09:00 on 05/21.Additionally, Inverter 1's right unit tripped offline at 11:00 on 05/24. 4. Inverter 2 middle unit tripped offline at 12:00 on 04/13, reporting a "3 Phase Possible Arc Detection" fault. The issue is being addressed under EPC. It was later brought back online at 09:00 on 05/21. However, Inverter 2 left unit tripped offline again at 15:00 on 05/25. 5. Inverter 3 middle unit tripped offline at 13:00 on 04/13 and reporting "3 Phase Possible Arc Detection" fault, Additionally left unit has tripped offline at 16:00 on 04/15 and adressing this issue under EPC.It was later brought back online at 09:00 on 05/21. However, Inverter 3 middle unit tripped offline again at 16:00 on 05/24. | 1. SR095956 2. SR099791 3. SR099791 4. SR099792 5. SR099793 | SR099791 | SR099791 | SR099792 | SR099793
M028 | NY | SOL-10381 | 19068.1172 | 18609.49 | 458.6272 | 2.464% | 22886 | -3817.8828 | -16.68% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q030 | NY | SOL-10878 | 23733.2422 | NA |  |  | 27337 | -3603.7578 | -13.18% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q130 | NY | SOL-10877 | 13589.5363 | NA |  |  | 15497 | -1907.4637 | -12.31% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q196 | NY | SOL-10879 | 17875.9383 | NA |  |  | 20173 | -2297.0617 | -11.39% | 1. Site production was low on 05/05, 05/06, 05/09 due to rain.
Q220 | NY | SOL-10873 | 20956.7969 | NA |  |  | 23174 | -2217.2031 | -9.568% | 1. Weather station stopped communication at 17:00 on 02/22 and adressing this issue under EPC and back online at 09:15 on 05/01. | 1. SR100524
Q205 | NY | SOL-10922 | 24385.0469 | 28274.8 | -3889.7531 | -13.76% | 28124 | -3738.9531 | -13.29% | 1. Inverter 1 right unit and Inverter 2 middle unit tripped offline at 12:00 on 05/11, reporting 'AC Voltage Too High.' Both units came back online at 17:30 on the same day. Additionally, Inverter 1 experienced frequent and intermittent trips over several days during the month. 2. Inverter 2 middle unit tripped offline at 09:45 on 05/25, reporting 'Grid Voltage Unbalance.' Inverter 3 middle unit also tripped offline at 07:00 on 05/25, reporting 'Error On,' and later self-resolved and back online at 18:00 on the same day. 3. Inverter 1 right unit tripped offline, reporting 'Grid Voltage Irregularity,' and later self-resolved but tripped offline again around midday. The inverter finally came back online at 17:00 on 05/26. | 1. SR100036 2. SR101922 3. SR101940 | SR101922 | SR101940
Q400 | NY | SOL-10871 | 26544.5859 | NA |  |  | 45134 | -18589.4141 | -41.19% | 1. A few strings are offline. EPC to complete. 2. Inverter 3 has tripped offline at 13:45 on 05/26 and reporting "Fault". 3. Inverter 1 left unit tripped offline at 12:00 PM on 04/17. Additionally, the right unit of Inverter 1 tripped offline at 06:00 AM on 05/12. The issue is being addressed under EPC, and both units self-resolved at 08:00 AM on 05/20. 4. Inverter 3 middle unit offline at 07:00 on 04/14 and adressing this issue under EPC. later self resolved and back online at 11:00 on 05/07. 5. Inverter 2 middle unit tripped offline at 15:15 on 04/28 and later self resolved and back online at 13:00 on 05/23.. Multiple inverter units experienced intermittent tripping throughout the month. | 1. SR095941 2. SR098490 3. SR099138 4. SR099857 5. SR100587 | SR098490 | SR099138 | SR099857 | SR100587
R003 | NY | SOL-10416 | 35329.2731 | NA |  |  | 40507 | -5177.7269 | -12.78% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/22, 05/28 due to rain.
R007 | NY | SOL-10417 | 37098.3672 | 37305.19 | -206.8228 | -0.5544% | 45612 | -8513.6328 | -18.67% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/22, 05/28 due to rain.
BK16 | NY | SOL-11093 | 39286.9688 | NA |  |  | 43901 | -4614.0312 | -10.51% | 1. Site production was low on 05/04, 05/05, 05/09, 05/13, 05/22, 05/28 due to rain.
Trenton - Trenton East | IL | SOL-11060 | 401135 | 427249 | -26114 | -6.112% | 488196 | -87061 | -17.83% | 1. Inverter 1 underperforming by 100 kW Inverter 2 underperforming by 5 kW Inverter 7 underperforming by 15 kW Inverter 8 underperforming by 37 kW Trackers have not communicated since 04/23 due to storm damage; EPC is working on partial energization, with trackers in stow and inverters expected to be derated. | 1. SR100220
Trenton - Trenton West | IL | SOL-11061 | 154211 | 253964.7 | -99753.7 | -39.28% | 486768 | -332557 | -68.32% | 1. Site was offline at 10:15 on 05/27 and remained offline throughout the month. | 1. SR102012
Dakota - Dakota Solar 1 | IL | SOL-11113 | 504703 | 600136 | -95433 | -15.9% | 0 | 504703 |  | 1. All trackers were stuck at 0 degrees as of 10:15 on 05/16. A technician visited the site on 05/20 and power-cycled all the trackers. then all trackers came back online and resumed tracking. 2. The site was taken offline at 10:15 on 05/21/25 due to a planned utility outage for work on the 34 kV line. It was brought back online at 13:15 on 05/22. | 1. SR098315 2. SR101778, SR101328 | SR101778 | SR101328
X018 | NY | SOL-10418 | 13614.8196 | 11268.16 | 2346.6596 | 20.83% | 22512 | -8897.1804 | -39.52% | 1. Inverter 2 underperforming compared to its peers and reporting a device communication fault since 01/22. 2. Inverter 1 had been underperforming by 13 kW compared to its peers since 03/26. A technician visited the site on 05/24, checked with SE, and found that the center and right units were offline, displaying Error 3x9B (RSd fault). The technician replaced the covers, toggled the switches, and turned the DC disconnect switches to the ON position. The pairing process was initiated and completed successfully. The inverter came back online on 05/24. | 1. SR096257 2. SR099018, SR099951 | SR099018 | SR099951
Janiak Solar | NY | SOL-10898 | 318017 | 333604 | -15587 | -4.672% | 412625 | -94608 | -22.93% | 1. The site went offline from 12:18 to 12:26 on 05/16 due to a relay opening. A brief outage occurred later, which self-resolved and relay closed. | 1. SR101588
County Route 11B | NY | SOL-10983 | 556820 | NA |  |  | NA |  |  | 1. Trackers 76 and 142 have been stuck since 04/25. Additionally, 13 trackers - 3, 13, 16, 54, 67, 76, 82, 83, 99, 109, 142, 148, and 183 have been stuck since 05/05. 2. Inverter 1 has been offline since 04/16. A technician visited the site on 05/22 and identified an issue with the SCADA system. Inverter 1 remained offline throughout the month. 3. The site tripped offline at 11:15 on 05/18. USNE inspected the site and, after examining the transformer, determined that additional troubleshooting is required. | 1. SR101645 2. SR097816 3. SR099947 | SR097816 | SR099947
Barone | NY | SOL-11034 | 549573 | NA |  |  | 684560 | -134987 | -19.72% | 1. The site tripped offline at 21:20 on 05/08 due to a utility outage caused by a fallen tree. A technician checked in at the site and found the recloser in the open position. The technician then closed the relay. The crew is currently working on repairs, and the site was back online at 09:40 on 05/10. 2. Trackers 11, 73, and 84 were stuck starting from 04/27, and Tracker 5 stopped tracking on 05/05. Additionally, all trackers were stuck on 05/06 but later self-resolved, and most trackers were back online by 05/07, except for Trackers 5, 73, and 84. Tracker 5 resumed tracking on 05/13, and Tracker 84 resumed on 05/27. | 1. SR101206 2. SR100609 | SR100609
Cedarville | IL | SOL-11069 | 428027 | 423775.7 | 4251.3 | 1.003% | 525848 | -97821 | -18.6% | 1. Inverters 9, 10, 11, 12, 13, 14, 15, and 16 tripped at 13:15, followed by Inverter 8 at 13:30 on 05/19, due to EPC work being carried out on-site. All inverters were back online at 17:00 on 05/19. 2. All trackers have been stuck at 0.99 degrees since 05/07. | 1. SR101685 2. SR101228 | SR101228
O'Brien Hill #1 | NY | SOL-11098 |  | NA | [5 empty] | 1.Site was offline from 03/07. The utility was contacted again to close the recloser, but the closure was not successful. Further troubleshooting is needed. | 1.SR098278, SR098670 | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 710692 | NA |  |  | N/A |  |  | 1. Inverter 1 tripped offline at 16:50 to 18:30 on 05/21 and reporting the overall work status as 'STOP'. It later self-resolved. 2. CB2 had been tripping on and off since 05/12. EV Solar checked on-site on 05/22, and after completing their work, CB2 was brought back online. | 1. SR101801 2. SR101819 | SR101819
Trinity - Freeport | IL | SOL-11057 | 479568 | 471609 | 7959 | 1.688% | 522288 | -42720 | -8.179% | 1. TCU 3, 33 through 66 are stuck from 4/24/25 at 13:00CDT. 2. Inverter 2 has been derating by approximately 5 kW to 20 kW in the afternoons since 03/28. The issue is currently under EPC. | 1.SR098066 2.SR099545 | SR099545
Ransom | NY | SOL-11157 | 743877.8 | NA |  |  | NA |  |  | 1. The site was offline from 07:05 to 09:55 on 05/01 due to EV Solar being on-site to replace the CT on Pad 1. 2. The site tripped offline at 07:00 on 05/28 due to a utility outage. Repairs were carried out, and the site was back online by 10:30. 3. Tracker W-050 and trackers W-159 and W-166 were stuck at 45° and 0°, respectively. Additionally, trackers E-82, E-83, E-167, E-168, and E-169 have been deviating between 12:00 PM and 5:00 PM since 04/07. All stuck trackers were back online as of 05/21; however, 4–5 trackers have continued to show deviations this month. | 1. SR100701 2. SR102028 3. SR099473 | SR102028 | SR099473
Horseheads - Wedge | NY | SOL-11160 | 523669 | NA |  |  | NA |  |  | 1.Trackers 101–114 were not tracking. This large group of trackers was the last to come online and may have been misconfigured. The GC is looking for the tracker layout plans for the site. After EV solar checked in and a new Cradlepoint was installed, these trackers came back online. | 1.SR099014,SR100026 | SR100026
Otisville - Shoddy Hollow | NY | SOL-11185 | 758134.8 | NA |  |  | NA |  |  | 1. All the trackers have been stuck mode since 05/14. 2. Inverter 1 is underproducing 1200kW due to module 1-2 is tripped offline at 14:40 on 04/29. | 1. SR098693 2. SR100729 | SR100729
Wellsville - Chenunda Creek | NY | SOL-11187 | 395137 | NA |  |  | NA |  |  | 1. The inverter has been experiencing a recurring trip event daily between 16:00 - 18:00 since 04/28. The issue later self-resolved, and the tripping appears to have stopped on 05/15. 2. The site was offline from 09:40 to 11:45 on 05/19 and later self-resolved. 3. Tracker 39 is stuck since 05/20. | 1. SR100662 2. SR101669 3. SR101745 | SR101669 | SR101745
DC: Washington - Essex Condominium | DC | SOL-10036 | 3982 | 5103.537 | -1121.537 | -21.98% | 4750.212 | -768.212 | -16.17% | 1. Site production was low on 05/04, 05/09, 05/13, 05/14, 05/21, 05/22, 05/27, 05/28 due to rain.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 9634 | 13220.9 | -3586.9 | -27.13% | 13467.537 | -3833.537 | -28.47% | 1. Meter voltages dropped to zero on 05/06 at 19:45 due to wiring issues. After onsite troubleshooting, meter voltages returned to normal on 05/07. Meter voltages dropped to zero again at 11:30 on 05/27, but production was confirmed at the inverters and voltages returned to normal at 18:30 on 05/28. 2. Inverter 2 has been offline since 03/28, reporting a fault current. 3. The site tripped offline at 23:00 on 05/01 and was back online at 08:15 on 05/02. It tripped again at 07:45 on 05/03 and was back online at 11:00 the same day. The site tripped again at 20:00 on 05/05 and was back online at 11:45 on 05/06. Another trip occurred at 15:30 on 05/10 and it was back online at 17:30. The final trip happened at 11:30 on 05/27 and the site was back online at 18:30 on the same day — this instance was self-resolved. | 1.SR100771 2.SR100622,SR095581 3.SR099162
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 14874 | 11763.123 | 3110.877 | 26.45% | 13460.33 | 1413.67 | 10.5%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Jun
Generate Capital |  |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  |  | 42369822.4118 | 17317666.147 | 25052156.2648 | 144.7% | 49787445.05 | -7417622.6382 | -14.9%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 19970.625 | 37270.35 | -17299.725 | -46.42% | 38094.4 | -18123.775 | -47.58% | 1. Inverter 1 went offline at 12:00 from 06/24.Will need to be investigated. 2. All inverters tripped offline at 14:15 on 06/25, reporting a 'Grid Voltage Fault,' and later self-resolved at 18:50 on 06/25. 3. Inverter 2 middle unit is tripping on and offline since 05/30 and issue self-resolved from 06/12. | 1. SR103460 2. SR103558 3. SR102435 | SR103558 | SR102435
K041 | NY | SOL-10357 | 26654.7812 | 30754.17 | -4099.3887 | -13.33% | 31695 | -5040.2188 | -15.9% | 1. Inverter module 1.0.71 went offline since 11/15/24, reporting 'No communication with Power Optimizer.' After replacing the optimizer, the module came back online on 06/01. 2.Inverters are tripping on and offline on 06/13 due to a technician being on-site for preventive maintenance. | 1. SR093289 2.PM8345
K043 | NY | SOL-10358 | 30931 | 33675 | -2744 | -8.148% | 6951 | 23980 | 345% | 1. Inverter 1 middle unit dropped production 13 kW down at 12:00 on 06/04. Inverter fan is under replacement. 2.Estimated values are low in AE we have also verified the file which was given by GC | 1. SR102473
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 28924 | -28924 | -100% | 1.Site was offline from 02/21 due to Phase C fuse was blown and parts were needed. | 1. SR097569
K115 | NY | SOL-10361 | 5326.6406 | 13256.49 | -7929.8494 | -59.82% | 18308.64 | -12981.9994 | -70.91% | 1. 96 optimizers are down for site construction. | 1. SR093291
K152 | NY | SOL-10362 | 9851.25 | 10260.33 | -409.08 | -3.987% | 10940 | -1088.75 | -9.952%
K166 | NY | SOL-10363 | 36140 | 39102.92 | -2962.92 | -7.577% | 40314.5 | -4174.5 | -10.35% | 1. Optimizers Modules 2.0.160, 2.0211,3.0.17 and 3.0.33 are offline from 06/04. | 1. SR095666
K206 | NY | SOL-10927 | 21537.6719 | 20572.7 | 964.9719 | 4.691% | 23702 | -2164.3281 | -9.131%
K251 | NY | SOL-10365 | 13051.4375 | 0 | 13051.4375 |  | 25462.41 | -12410.9725 | -48.74% | 1. Inverter 1 tripped offline at 13:00 on 06/12 and remained offline through out the month. 2. Inverter module 1.0.153 12D31EC2-C5 is offline since 11/15/25 will troubleshoting the issue during PM visit. 3. Weather station stopped communicating at 07:00 on 11/22/24 . | 1. SR102970 2. SR093292 3. SR093633 | SR093292 | SR093633
K269 | NY | SOL-10366 | 21627.8125 | 25278.65 | -3650.8375 | -14.44% | 25051.98 | -3424.1675 | -13.67% | 1.Inverters producing as expected and expected value and forecasted energy values diffrence.
K273 | NY | SOL-10367 | 20960.1875 | 0 | 20960.1875 |  | 30934 | -9973.8125 | -32.24% | 1. 26 optimizers are down for roof repair. 2. Weather station stopped communicating since 06/14/24. | 1. SR093294
K287 | NY | SOL-10919 | 18763.9688 | 16103.01 | 2660.9587 | 16.52% | 21718 | -2954.0312 | -13.6% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
K298 | NY | SOL-10368 | 20591.3438 | 21440.24 | -848.8963 | -3.959% | 25175 | -4583.6562 | -18.21% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
K335 | NY | SOL-10370 | 20569.9375 | 24021.24 | -3451.3025 | -14.37% | 25592 | -5022.0625 | -19.62% | 1. Both inverters tripped offline at 12:15 on 06/25 and reporting "3phase Sunspec" fault. later self resolved and back online at 18:00 on 06/26. | 1. SR103533
K345 | NY | SOL-10920 | 24507.2812 | 14335.24 | 10172.0413 | 70.96% | 29326 | -4818.7188 | -16.43% | 1. Inverter 3 is underproducing due to unit(7E9C82CA) underproducing from 13:30 on 06/20 and reporting "external fan" fault. | 1. SR103259
K445 | NY | SOL-10373 | 20602.4062 | 22293.98 | -1691.5737 | -7.588% | 23683.37 | -3080.9637 | -13.01% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
K495 | NY | SOL-10374 | 84354 | 83864.09 | 489.91 | 0.5842% | 97327.32 | -12973.32 | -13.33% | 1.Inverter 11 (left unit) was offline since 04/18, reporting a "DC Isolation Fault." During troubleshooting, it was discovered that following a firmware update, the inverter no longer displayed fault codes and continued to fail to produce power. SolarEdge technical support was contacted, and a callback was received. Case number 5713468 was created. | 1. SR101786
M020 | NY | SOL-10380 | 22387.4375 | 23071 | -683.5625 | -2.963% | 27263 | -4875.5625 | -17.88% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
M092 | NY | SOL-10383 | 22328.875 | 23813.76 | -1484.885 | -6.235% | 26112.96 | -3784.085 | -14.49% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
M143 | NY | SOL-10384 | 24011.4375 | 29585.28 | -5573.8425 | -18.84% | 28779.79 | -4768.3525 | -16.57% | 1. Inverter 3 left unit is having multiple trippings since 06/08 on high irradiance day. | 1. SR102672
M144 | NY | SOL-10385 | 36137.0625 | 39456.57 | -3319.5075 | -8.413% | 47489.14 | -11352.0775 | -23.9% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
M167 | NY | SOL-10386 | 28733.2812 | 20908.97 | 7824.3112 | 37.42% | 35467.9 | -6734.6188 | -18.99% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
M188 | NY | SOL-10387 | 19170.2188 | 19623.05 | -452.8312 | -2.308% | 23732.02 | -4561.8013 | -19.22% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
EMHC | NY | SOL-10351 | 7915.9609 | 6589.297 | 1326.6639 | 20.13% | 12239.52 | -4323.5591 | -35.32% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 35176 | -35176 | -100% | 1.Site stopped communicating from 03/25. On 03/27 Technician stated that main breaker tripped and malfunctioning. Site was remained offline till date. As per GenC, EPC has been responsive on the warranty claim. They are sourcing the breaker and should perform repairs in June. | 1. SR102532
Q018 | NY | SOL-10398 | 19132.875 | 20700.88 | -1568.005 | -7.575% | 19976.3 | -843.425 | -4.222% | 1.Inverters 1,2 are offline from 08:30 to 15:45 on 06/23 | 1. SR103286
Q021 | NY | SOL-10399 | 15640.0625 | 15031.53 | 608.5325 | 4.048% | 16758.83 | -1118.7675 | -6.676%
Q025 | NY | SOL-10400 | 27194.3125 | 26758.96 | 435.3525 | 1.627% | 15102 | 12092.3125 | 80.07%
Q074 | NY | SOL-10402 | 17398.375 | 17593.24 | -194.865 | -1.108% | 18971.07 | -1572.695 | -8.29%
Q115 | NY | SOL-10872 | 22855.1875 | 24405.24 | -1550.0525 | -6.351% | 25038.25 | -2183.0625 | -8.719%
Q139 | NY | SOL-10403 | 13673.4688 | 15136.32 | -1462.8512 | -9.665% | 16017 | -2343.5312 | -14.63% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
Q157 | NY | SOL-10404 | 24393.5625 | 25953.17 | -1559.6075 | -6.009% | 27305.78 | -2912.2175 | -10.67% | 1.Inverter 4 started late for production at 15:00 on 06/18 | 1. SR103116
Q192 | NY | SOL-10406 | 37709.75 | 41865.54 | -4155.79 | -9.927% | 4113.07 | 33596.68 | 816.8% | Based on the site’s weather station data, the plant is performing as expected. The forecasted (theoretical) values appear lower because they are derived from long-term average weather data, typically spanning 10–15 years. In contrast, actual versus expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance. There may be a data glitch affecting the expected values.
Q210 | NY | SOL-10407 | 29576.625 | 31213.15 | -1636.525 | -5.243% | 34306 | -4729.375 | -13.79% | 1.Inverter 1, unit 1.1 tripped offline on 06/24 at 15:00 reporting "Residual Current Device". Self resolved on 06/25 | 1.SR103569
Q229 | NY | SOL-10408 | 13318.3438 | 15154.58 | -1836.2362 | -12.12% | 14832.6 | -1514.2563 | -10.21% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1.SR088813
Q231 | NY | SOL-10870 | 50798 | 52427.44 | -1629.44 | -3.108% | 58879 | -8081 | -13.72% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
Q405 | NY | SOL-10409 | 56298.75 | 62728.45 | -6429.7 | -10.25% | 61347.86 | -5049.11 | -8.23% | 1. 4 Inverter modules are offline. Will investigate next time on site. Module 1.0.64 Module 4.0.39 , 3.0.20 ,1.0.64 | 1.SR093324
Q435 | NY | SOL-10923 | 60990.4375 | 61208.12 | -217.6825 | -0.3556% | 83541 | -22550.5625 | -26.99% | 1.Inverter 01 discovered offline.Opened AC combiner panel and found breaker tripped at 13:15 on 06/04 in both AE and SE. Inveter 1 came back online on 06/09 | 1.SR102499
Q485 | NY | SOL-10869 | 68410.75 | 53323.04 | 15087.71 | 28.29% | 79147.91 | -10737.16 | -13.57% | 1.Inverter 4 middle unit tripped offline at 09:00 on 06/12. On 06/17 technician tested and replaced the failed optimizers for inverter 4 came back online and producing as expected | 1.SR102920
Q490 | NY | SOL-10411 | 48688.9863 | N/A |  |  | 53116.12 | -4427.1337 | -8.335% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1.SR093326
Q620 | NY | SOL-10867 | 74928.25 | 75703.92 | -775.67 | -1.025% | 83113.84 | -8185.59 | -9.849%
QMOA | NY | SOL-10415 | 6248.8 | N/A |  |  | 7429.65 | -1180.85 | -15.89% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
X024 | NY | SOL-10419 | 27652.5312 | 28471.48 | -818.9487 | -2.876% | 28806 | -1153.4688 | -4.004% | 1. On 02/05, the technician onsite found a faulty optimizer while troubleshooting the central unit of Inverter 2. Technician noted that the optimizer would need to be replaced and initiated an RMA on the same day. The optimizer still needs to be replaced during the next onsite visit. | 1. SR096294
X026 | NY | SOL-10420 | 25041 | 22800 | 2241 | 9.829% | 38026 | -12985 | -34.15% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1.SR095662
X090 | NY | SOL-10925 | 19835 | 18734 | 1101 | 5.877% | 23966 | -4131 | -17.24% | 1.- Inverter 1 (Unit 1.2) is offline on 06/25 | 1.SR103568
X117 | NY | SOL-10422 | 17607 | 19618 | -2011 | -10.25% | 20473 | -2866 | -14% | 1. Inverter 1 right unit is tripping on and offline since 06/01. Self resolved on 06/12 | 1.SR102436
X125 | NY | SOL-10423 | 32830 | 33471 | -641 | -1.915% | 36856.22 | -4026.22 | -10.92% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
X134 | NY | SOL-10424 | 31871 | 32985 | -1114 | -3.377% | 37077 | -5206 | -14.04% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
X135 | NY | SOL-10425 | 26049 | 30015 | -3966 | -13.21% | 29467 | -3418 | -11.6% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
X139 JHS 222 | NY | SOL-10426 | 39810 | 42093 | -2283 | -5.424% | 46791 | -6981 | -14.92% | 1.- Inverter 1 right unit is tripping on and offline since 05/30 | 1.SR102437
X140 | NY | SOL-10926 | 22680.7812 | 18924.19 | 3756.5913 | 19.85% | 25042 | -2361.2188 | -9.429%
X166 | NY | SOL-10427 | 23196 | 22514 | 682 | 3.029% | 27533 | -4337 | -15.75% | 1.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Murphy | MN | SOL-10094 | 787760 | 843351.2 | -55591.2 | -6.592% | 943113.3 | -155353.3 | -16.47% | 1. Inverter 1 tripped offline at 07:00 on 06/07 due to the main AC circuit breaker being open and came back online at 09:45 on 06/09. Additionally, Inverter 1 has been derating by 200 kW since 06/10 due to a faulty control board and IGBTs in Module 1 that need replacement. On 06/18, the inverter was taken offline from 07:00 to 10:30 for troubleshooting. 2. Inverter 5 tripped offline at 07:15 on 06/08, reporting 'Inverter Fault at 50s.' After a remote reset, the inverter came back online at 08:30 on 06/09 and again inverter 5 offline on 06/29 and came back online at 10:15 on 06/30 | 1. SR101354 2. SR102217 | SR102217
Terning | MN | SOL-10093 | 846214 | 880245.1 | -34031.1 | -3.866% | 962294.1 | -116080.1 | -12.06% | 1. Inverter 3 derated at about 860kW on 06/04 later self resolved. | 1. SR102507
Boas Road 04 | NY | SOL-10908 | - | 399796 |  |  | 381322 |  |  | 1. Meter stopped communicating from 14:05 on 03/16 till date. 2. Inverter 1 did not start production on 05/17 and reported 'SE VBUS NEG DERIVATIVE FAULT.' As a result, three strings were damaged and required additional troubleshooting. On 06/16, the three strings were replaced, but the inverter still required further troubleshooting. 3. The site was taken offline at 06:55 on 06/16 and brought back online at 11:15 on 06/18 for Inverter 1 troubleshooting. | 1. SR098641 2. SR101620, SR103015, SR103150 3. SR101620 | SR101620 | SR103015 | SR103150 | SR101620
Kelly Bridge Farm | NY | SOL-10911 | 66233 | 336303 | -270070 | -80.31% | 373520 | -307287 | -82.27% | 1. The site was taken offline from 08:20 to 12:20 on 06/03 due to NYSEG being on-site for transformer testing. 2. Inverters 26 and 27 are derating by 20kW down each compared to its peers since 06/04 later inverter 27 resolved on 06/06. 3. Inverters 18 through 22 tripped offline at 11:15 on 06/11 and were brought back online at 09:30 on 06/12 after a breaker reset. They tripped offline again at 10:45 on 06/12 and were restored at 09:20 on 06/13 after resetting the breaker. The inverters tripped offline once more at 10:40 on 06/19 and were brought back online at 12:25 on 06/23 after resetting breaker. 4. The site was taken offline from 08:25 to 12:40 on 06/23 due to a technician being on-site performing inverter troubleshooting. Later, Inverters 28 to 33 went offline due to a damaged breaker. | 1. SR102364 2. SR102506 3. SR102821, SR102951, SR103185 4. SR103185 | SR102506 | SR102821 | SR102951 | SR103185 | SR103185
Pool Brook Road | NY | SOL-10909 | 207378 | 242450 | -35072 | -14.47% | 361532 | -154154 | -42.64% | 1. The site was taken offline at 12:30 on 06/04 and brought back online at 12:10 on 06/12 due to a planned outage. | 1. SR102460
Sackett Lake | NY | SOL-10910 | 265315 | 341765 | -76450 | -22.37% | 364487 | -99172 | -27.21% | 1. Inverter 2 was offline since 03/30 and being RMA'd and later back online at 15:35 0n 06/10. 2. Inverter 1 went offline at 07:00 on 05/31, reporting 'SE GRID POWER CONSUMPTION (60).' After replacing the TFAM board, the inverter is back online at 13:10 on 06/02. It tripped offline again at 09:00 on 06/09 and back online at 13:40 on the same day after replacing the strings. The inverter tripped offline once more from 15:00 to 15:35 on 06/10. | 1. SR100623, SR099149, SR101482 2. SR102219 | SR099149 | SR101482 | SR102219
Burritt Road | NY | SOL-10913 | 390310 | 421201 | -30891 | -7.334% | 413053 | -22743 | -5.506%
Villa Roma 1 | NY | SOL-10914 | 298826 | 2112 | 296714 | 14049% | 347740 | -48914 | -14.07% | 1.Expected energy values are reporting very low. Created a case #66639 with GPM, As per GPM the BOM has been frozen from 02/27. | 1. SR099403
Villa Roma 2 | NY | SOL-10915 | 295810 | 310718 | -14908 | -4.798% | 336904 | -41094 | -12.2%
Washington 1 | NY | SOL-10912 | 396720 | 415588 | -18868 | -4.54% | 408816 | -12096 | -2.959% | 1. Inverter 2 is tripped offline at 05:50 on 06/08 and reporting "SE PHASE R BLOWER FAIL (98)" and back online at 14:35 on 06/08. | 1. SR102665
Washington 3 | NY | SOL-10828 | 433898 | 675268 | -241370 | -35.74% | 499324 | -65426 | -13.1% | 1. Combiner Box 4 is offline due to a broken DC switch inside Inverter 1. A new DC switch needs to be installed 2. POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1. SR102427 2.SR093024 | SR093024
Washington 4 | NY | SOL-10829 | 411504 | 495599 | -84095 | -16.97% | 500452 | -88948 | -17.77% | 1.The site remained offline from 06/01 to 14:30 on 06/06, as technicians had left the inverters offline for further troubleshooting. | 1.SR098198,SR100200 | SR100200
Big Tree | NY | SOL-10966 | 404899 | N/A |  |  | 429682 | -24783 | -5.768% | 1.Site was offline from 12:40 to 16:10 on 06/09 as USNE techicians were onsite. 2.Combiner box 7,string 1 is underperforming since 03/21.Needs further investigation. | 1.SR100625 2.SR098866 | SR098866
Canoga | NY | SOL-10965 | - | N/A | [5 empty] | 1.Site was offline throughout the month due to utility work at substation | 1.SR098998
County Route 84 | NY | SOL-10967 | 887510 | N/A |  |  | 972096 | -84586 | -8.701% | 1.Site was offline from 10:55 to 14:50 on 06/04 to work on transformer issue 2. Inverter 4 inductor fan was being RMA'd from 06/27. | 1.SR100373 2.SR103651 | SR103651
Donati | NY | SOL-10968 | 476881 | N/A |  |  | 550490 | -73609 | -13.37% | 1.Weather station Reporting 0 value from 05/31/24. POA sensors need to be replaced. 2.Stuck trackers: A01, A05 through A07, A10, F19, F21 through 22, F27, F33, G14.Further troubleshoting is required. | 1.SR092964 2.SR095253,SR098877 | SR095253 | SR098877
Henrietta | NY | SOL-10972 | 1065880 | N/A |  |  | 1172239 | -106359 | -9.073% | 1.Site was offline from 08:50 on 06/08 to 02:05 on 06/09. | 1.SR102662
NY 70 | NY | SOL-10970 | 1143230 | N/A |  |  | 1263015 | -119785 | -9.484%
Reid | NY | SOL-10991 | 599906.1041 | 636437.8 | -36531.6959 | -5.74% | 917075 | -317168.8959 | -34.58% | 1.Inverter 6 was being RMA'd from 05/30 and it was replaced and producing as expected from 06/17 2.Inverter 9 was offline on multiple days of the month. 3.Inverters 28 was frequently trippping on and off.Inverter 28 was completly offline from 06/20 to rest of the month. 4. InverterS from 1 to 20 tripped offline at 07:30 on 06/15 and AC voltages dropped to 0V. Possibly Pad 1 breaker trip.Inverters were online at 10:45 on 06/17. 5. Inverter 20 tripped offline at 12:15 on 06/21 and remained offline throughout the month due to "Grid voltage out of range" and "Power Module Protection - Protect0120" respectively. 6.Inverter 30 was offline on multiple days of the month. 7.Site was offline from 03:00 on 06/22 to 15:00 on 06/27. 8. Inverter 28 again tripped offline at 15:00 from 06/28 "Grid Phase Voltage Out of Range - GridV.OutL". 9.Inverter 14 offline from 06/28 and reporting "Power Module Protection". 10. Inverters 14 , 5, 29 and 32 have also tripped offline at 13:40 from 06/30 producing fault "" Grid voltage out of range". | 1.SR101912 2.SR102335,SR102682 3.SR102682,SR103181 4.SR102996 5.SR103257 6.SR103260 7.SR103266 8.SR103181 9.SR103257 10.SR103260 | SR102335 | SR102682 | SR102682 | SR103181 | SR102996 | SR103257 | SR103260 | SR103266 | SR103181 | SR103257 | SR103260
Sangolqui | NY | SOL-10975 | 437080 | N/A |  |  | 538488 | -101408 | -18.83% | 1.Inverter 2 was offline from 10:50 on 06/02 to 13:00 on 06/05 due to "SE AUXILIARY SUPPLY FAIL (135)". | 1.SR102298
State Highway 17B | NY | SOL-10988 | 719330 | N/A | [5 empty] | 1.Site was offline from 07:50 on 06/21 to 02:00 on 06/22 due to utility outage 2.Inverter 3 tripped offline at 11:25 from 06/23 and reporting "OVERTEMP PHASE 1". inverter came back online on 06/26. 3.Inverter 2 was offline from 06/27 and came back online at 15:10 on 06/30. 4.Inverters 1 tripped offline at 13:30 on 06/26 and came back online on 06/27. Inverter once again tripped offline at 14:25 from 06/30 | 1.SR103256 2.SR103314 3.SR103671 4.SR103671 | SR103314 | SR103671 | SR103671
State Route 14A | NY | SOL-10997 | - | N/A |  |  | 967648 |  |  | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required, and the site will remain offline for safety. | 1. SR101820, SR099347 | SR099347
West Creek | NY | SOL-10995 | 836200 | N/A |  |  | 960614 | -124414 | -12.95% | 1. CB 25 String 1 has been offline since 06/03 due to a possible ground fault. 2. The site tripped offline from 10:05 to 14:00 on 06/13 | 1. SR102360 2. SR102937 | SR102937
Wildflower | NY | SOL-10982 | 777681 | N/A |  |  | 972382.4 | -194701.4 | -20.02% | 1. Inverter 2 did not start producing on 06/07 but later began production at 11:40 on the same day. It tripped offline again at 17:55 on 06/19 due to a 'Fatal Error' and 'AC Contactor Fault,' and came back online at 11:05 on 06/22. | 1. SR102637
Glen Mary 1 | NY | SOL-10993 | 883350 | N/A |  |  | 1006679 | -123329 | -12.25% | 1.Inverter 2 started production late at 11:35 on 06/07. It went offline again on 06/20, reporting 'Fatal Error' and 'AC Contactor Fault.' Inverter 2 came back online at 11:00 on 06/22 | 1. SR103167
Glen Mary 2 | NY | SOL-10994 | 396430 | N/A |  |  | 429189 | -32759 | -7.633%
Telegraph 1 | NY | SOL-11003 | 724888 | N/A |  |  | 758222 | -33334 | -4.396%
Telegraph 2 | NY | SOL-11004 | 383510 | N/A |  |  | 395820 | -12310 | -3.11%
Cafferty Hill | NY | SOL-10996 | 887090 | N/A |  |  | 945865 | -58775 | -6.214%
Dunkleman | NY | SOL-11008 | 1191520 | N/A |  |  | 1303096 | -111576 | -8.562% | 1.Currently, the following trackers are stuck Group 1: 57 & 119 Group 2: 24, 27, 32, 36, 39, 43, 54, 59, 61, 97, 114, & 124. A total of 14 tracker control units are struck from 06/11 | 1.SR095109
Route 19 1 | NY | SOL-11001 | 485730 | N/A |  |  | 540517 | -54787 | -10.14% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
Route 19 2 | NY | SOL-11002 | 1170370 | N/A |  |  | 1328891 | -158521 | -11.93% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
Yellow Mills 1 | NY | SOL-11006 | 271062 | N/A |  |  | 404357 | -133295 | -32.96% | 1.Site tripped offline at 09:20 on 06/03 due to switching operation and was back online at 17:40 at 06/05. 2.Inverter tripped offline at 15:25 on 06/15, reporting a 'Sampling Fault.' After power cycling, it came back online at 08:55 on 06/16. 3.Inverter tripped offline at 14:15 on 06/17 reporting " Sampling fault".Inverter was back online at 10:50 on 06/18 after power cycled by Sungrow.Inverter again tripped offline at 08:20 on 06/20 reporting "sampling fault",Inverter was back online at 16:35 on 06/24 after restoring the power by Sungrow. | 1.SR102378 2.SR102995 3.SR103080 | SR102995 | SR103080
Yellow Mills 2 | NY | SOL-11005 | 368106 | N/A |  |  | 418478 | -50372 | -12.04% | 1.Site tripped offline at 09:10 on 06/03 due to switching operation and was back online at 17:40 on 06/05. 2.Meter power & voltages reporting zero from 18:05 on 06/16 and production can be confirmed at inverter level. Self resolved on 06/20 | 1.SR102379
Yellow Mills 3 | NY | SOL-11007 | 351235 | N/A |  |  | 398512 | -47277 | -11.86% | 1.Site tripped offline at 09:20 on 06/03 due to switching operation at site and was back online at 17:40 on 06/05 | 1.SR102380
Catskill | NY | SOL-11021 | 676307 | N/A |  |  | 722557 | -46250 | -6.401% | 1.Site tripped offline at 01:35 on 06/15,meter voltages were dropped to 0 and 09:35pm relay closed and voltages were available. Closed MV switch using SEL relay and set relay to remote mode after which site was back online at 16:45 on 06/16. | SR102984
Eddy Ridge | NY | SOL-11054 | 615336 | N/A |  |  | 626850 | -11514 | -1.837% | 1.The inverter is exceeding its curtailment at 2338KW since 8am on 05/10 . | 1.SR101282
Ridgeway #1 | NY | SOL-11018 | 1316830 | N/A |  |  | 1266592.7 | 50237.3 | 3.966%
Rivard 1 | NY | SOL-11011 | 1088066.8957 | 0 | 1088066.8957 |  | 138294.8 | 949772.0957 | 686.8% | 1. The site lost communication at 9:15 on 04/12; however, meter production data remained available. On 04/24, the technician found that Pad 1 DAS had a blown 4A fuse. They removed a fuse from Pad 2, but it failed upon re-energization. The technician will need to return with additional fuses. 2.Weather station lost communication from 03/29 | 1. SR099726
Rivard 2 | NY | SOL-11012 | 1057218.755 | 1026533 | 30685.755 | 2.989% | 1086602 | -29383.245 | -2.704% | 1. Tracker control 33 - 90, 129 - 136, 148 , 20-32, 123-128, 172-183 are not communicating & tracker 156 , 121 is stuck and production dropped (approxmately ) 25 kW down. 2. Site was offline from 14:44 to 15:40 on 06/10 to perform Preventive Maintenance Inspection. 3. Inverter 1 offline from 13:15 to 13:58 on 06/23 to perform Preventive Maintenance Inspection. | 1. SR095073, PM7888 2. PM7888, SR103366 3. PM7888, SR103366 | SR103366 | SR103366
Ridgeway #2 | NY | SOL-11027 | 659346 | N/A |  |  | 645978 | 13368 | 2.069%
Spencer | NY | SOL-11017 | 1160891 | N/A |  |  | 1233800 | -72909 | -5.909% | 1.Tracker 170 stuck at 54.93 deg on 06/18 | 1.SR101152
Reisender | NY | SOL-10886 | 331750 | 333637 | -1887 | -0.5656% | 383449 | -51699 | -13.48% | 1.Site tripped offline at 09:45 from 06/30 | 1.SR103760
Finney | NY | SOL-10999 | 1023680 | N/A |  |  | 1241407 | -217727 | -17.54% | 1.Site tripped offline from 10:59 to 16:05 on 06/19. Site came back online by remote reset and started producing at 16:05. 2.Inverter 1 is currently offline on 06/23 and reporting "AC Switch breaker open". Inverter 1 came back online at 14:24 on 06/24 3. Inverter 1 offline on 06/25 and reporting" AC Breaker Switch Open". Inverter voltages are available. inverter 1 came back online on 06/26 4. Site tripped offline at 00:33 on 06/26. Site came back online at 07:00 on 06/27 | 1.SR103174 2. SR103321 3. SR103538 4. SR103570 | SR103321 | SR103538 | SR103570
Davis Solar | NY | SOL-10958 | 292865 | 374601.7 | -81736.7 | -21.82% | 452578 | -159713 | -35.29% | 1. The inverter tripped offline at 09:00 on 06/06 and later came back online at 11:30 on the same day via remote reset. 2. The inverter tripped offline at 12:45 on 06/12 and came back online at 13:30 on the same day via remote reset. It tripped offline again at 17:15 on 06/12 and was brought back online at 17:45 via remote reset. | 1. SR102601 2. SR102895 | SR102895
Genesee | NY | SOL-10951 | 706865 | N/A |  |  | 958340 | -251475 | -26.24% | 1. The site was offline from 04/21 and came back online at 15:40 on 06/02. 2. Trackers 23, 24, 33, 37, and 72 through 151 have been stuck since 06/02. 3. The site tripped offline at 09:05 on 06/12 due to a utility outage and later came back online at 11:10 on 06/16. | 1. SR100101 2. SR102328 3. SR102889 | SR102328 | SR102889
Landau I | NY | SOL-10891 | 378150 | N/A |  |  | 415759 | -37609 | -9.046%
Landau II | NY | SOL-10895 | 22460 | N/A | [5 empty] | 1. Inverter 2 tripped offline at 14:45 on 05/31 due to the AC breaker switch being open. It was found that the AC breaker needs to be replaced. Inverter 2 will remain offline until the new AC breaker is installed. | 1. SR101082, SR101848, SR103374 | SR101848 | SR103374
New Beginnings | NY | SOL-10890 | 63410 | 371839 | -308429 | -82.95% | 402875 | -339465 | -84.26% | 1. The inverter tripped offline at 19:10 on 05/24 and later came back online at 15:10 on 06/25 after the DC shunt was replaced. | 1. SR101915
Bullitt Farm Solar, LLC | NY | SOL-10998 | 1089099 | 1103979 | -14880 | -1.348% | 1188892 | -99793 | -8.394%
Brodhead Solar, LLC | NY | SOL-10899 | 370257 | 453079 | -82822 | -18.28% | 517267 | -147010 | -28.42% | 1. NCU 2 Tracker 1 has been stuck since 11/19, and Tracker 35 was stuck at 11:45 on 01/31 but later resumed tracking at 11:00 on 06/26 after the trackers were power cycled. 2. NCU 1 Tracker 10 has been stuck at 09:15 since 02/23. Additionally, NCU 1 Tracker 38 was stuck at 21:00 since 05/09 and later resumed tracking at 11:00 on 06/26 after the trackers were power cycled. | 1. SR095624 2. SR097725 | SR097725
Svenski | NY | SOL-10894 | 365745 | N/A |  |  | 437648 | -71903 | -16.43% | 1. The site went offline at 16:00 on 06/06 due to a utility outage and came back online at 10:35 on 06/07 via remote reset. | 1. SR102628
Bantam | NY | SOL-10986 | 94580 | N/A |  |  | 1178744 | -1084164 | -91.98% | 1. All trackers were stuck in snow stow mode from 05/12 and later resumed tracking after the snow sensor was disabled on 06/11. 2. Inverter 1 tripped offline at 16:40 on 05/26 and is currently in an open AC breaker switch state. Water intrusion and condensation were found inside Inverter 1 and its DC compartment, but no internal damage was observed. Additionally, four combiner boxes also had water intrusion and have been isolated. For safety reasons, the inverter remains offline, and further troubleshooting is required. 3. The weather station (POA2, GHI, rPOA) has stopped communicating since 18:10 on 05/27. | 1. SR101314 2. SR101947 3. SR102015 | SR101947 | SR102015
Bogart | NY | SOL-10887 | 319950 | 372889 | -52939 | -14.2% | 395717 | -75767 | -19.15% | 1. The inverter went offline on 06/28 because the AC breaker switch was in the "Open" state and has remained offline since then. | 1. SR103685
Dubois | NY | SOL-10892 | 275800 | N/A | [5 empty] | 1. The site tripped offline at 09:00 on 06/08 due to a utility outage and came back online at 08:51 on 06/10. 2. The site tripped offline at 08:12 on 06/16 due to a utility outage and came back online at 13:54 on the same day. Additional troubleshooting is needed as the strobe was temporarily removed. 3. The weather station has been reporting 0 since 13:14 on 06/21. 4. The site tripped offline at 10:01 on 06/27 due to a utility outage and came back online at 07:53 on 06/30. | 1. SR102664 2. SR103019 3. SR103279 4. SR103668 | SR103019 | SR103279 | SR103668
Salt Point | NY | SOL-10888 | 385040 | N/A |  |  | 482846 | -97806 | -20.26% | 1. Trackers – NCU 1 SPC 103 through 115 were stuck starting from 03/18 due to a tripped TCU breaker and a broken panel that requires replacement. Additional time is needed on-site to replace damaged wires and an SPC box that contained a mouse nest. 2. The site tripped offline at 17:25 on 06/06 and later came back online at 10:45 on 06/07 via remote reclose. | 1. SR098692 2. SR102638 | SR102638
Wheatland 2A | NY | SOL-10971 | 864380 | N/A |  |  | 1095784 | -231404 | -21.12% | 1. 14 trackers are currently stuck from 01/06 NCU 1 SPC 111, 112, 118, 205, 305, 307, 310, & 311 & NCU 2 SPC 125, 126, 136, 242, 338, & 341. On 04/15 Technician worked on the trackers, multiple trackers are still not reporting and require further troubleshooting with NexTracker. 2.Technician after replacing two HVPS on 04/28. Currently multiple trackers are still struck and requires additional troubleshooting along with NEXTracker's assistance 3. Inverter 1 was offline from 10:45 on 05/24 due to the AC contactor being in the open position and came back online at 16:00 on 06/09. 4. Inverter 1 CB1 has had an active ground fault on STR 14 since 05/24. | 1. SR099686 2. SR094820 3. SR101931 4. SR102747 | SR094820 | SR101931 | SR102747
Wheatland 2B | NY | SOL-10961 | 1027920 | N/A |  |  | 1088223 | -60303 | -5.541% | 1. 15 trackers are currently stuck from 03/21 NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 | 1. SR098860
Brickchurch | NY | SOL-10889 | 459310 | 459002 | 308 | 0.0671% | 502386 | -43076 | -8.574% | 1.All NCU 2 trackers have lost communication, while NCU 1 trackers 115-127 remain stuck from 03/27. Previous stuck trackers included 18 on 03/24 and specific units on 03/17 and alos NCU 2 SPC 220, 253, 329, & 338 are stuck from from 05/12 | 1. SR097454, SR099118 | SR099118
McCarthy Solar | NY | SOL-10992 | 283530 | N/A |  |  | 418645 | -135115 | -32.27% | 1. The site tripped offline at 07:10 on 06/24 and has been offline since then. | 1. SR103367
Costanza | NY | SOL-10907 | 364360 | N/A |  |  | 414587 | -50227 | -12.11% | 1. The site was offline on 05/31 due to a utility outage and came back online at 08:17 on 06/01. 2. The site was offline from 10:20 on 06/07 and came back online at 11:12 on 06/08. 3. The site was offline from 07:27 on 06/26 to 12:09 on 06/27 due to a planned outage by the utility and later came back online at 11:39 on 06/29. | 1. SR102212 2. SR102640 3. SR103552 | SR102640 | SR103552
Lockenhurst Pond | NY | SOL-11000 | 416911.2836 | 444563.9 | -27652.6164 | -6.22% | 498681 | -81769.7164 | -16.4% | 1.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Drinkwater | NY | SOL-10896 | 392340 | N/A |  |  | 416568 | -24228 | -5.816%
Altamont | NY | SOL-11085 | 691328 | 694252.9 | -2924.9 | -0.4213% | 722079.4 | -30751.4 | -4.259%
Krumkill North | NY | SOL-11086 | 713039 | 821994.6 | -108955.6 | -13.26% | 819211.9 | -106172.9 | -12.96% | 1. The site was offline from 21:30 on 06/24 due to a utility outage and came back online at 13:45 on 06/28. | 1. SR103476
Krumkill South | NY | SOL-11087 | 590962 | 652801.5 | -61839.5 | -9.473% | 642237.6 | -51275.6 | -7.984% | 1. The site was offline from 21:30 on 06/24 due to a utility outage and came back online at 13:30 on 06/28. | 1. SR103477
X092 | NY | SOL-11189 | 19330.2 | 19496.43 | -166.23 | -0.8526% | 22556 | -3225.8 | -14.3%
X093 | NY | SOL-10932 | 12912.2643 | 13336.82 | -424.5557 | -3.183% | 16028 | -3115.7357 | -19.44% | 1. Many optimizers on SE are offline and later back online on 04/15. Additionally 1 optimizer on SE is offline , EPC to complete. 2. Inverter 1 has been offline since 12:00 on 06/24. | 1. SR095945 2. SR103457 | SR103457
X095 | NY | SOL-10929 | 19363.9609 | N/A |  |  | 21772 | -2408.0391 | -11.06% | 1. Currently, the following optimizers are offline or severely underproducing Panel 1.0.7 124BD3FC-2C Panel 1.0.65 124CF1D2-21 Panel 1.0.84 124BDFF4-30 Panel 3.0.28 124A7869-3D Panel 3.0.31 124CF59F-F2 | 1. SR095946
X181 | NY | SOL-10428 | 31533.8438 | N/A |  |  | 40286 | -8752.1562 | -21.73% | 1. The inverters have been offline since 12:00 on 06/24. | 1. SR103482
X415 | NY | SOL-10429 | 22569.3984 | N/A |  |  | 23788 | -1218.6016 | -5.123%
K198 | NY | SOL-10930 | 16595.4766 | 15968.67 | 626.8066 | 3.925% | 18100 | -1504.5234 | -8.312%
K203 | NY | SOL-11190 | 21003.6 | 18798.59 | 2205.01 | 11.73% | 24585 | -3581.4 | -14.57% | 1.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
K213 | NY | SOL-11191 | 23157.2 | 24726.14 | -1568.94 | -6.345% | 25727 | -2569.8 | -9.989% | 1. The site was offline from 12:00 to 13:30 on 06/04 due to EPC being onsite. | 1. SR099930
K217 | NY | SOL-10933 | 13048.0547 | 0 | 13048.0547 |  | 14344 | -1295.9453 | -9.035%
K307 | NY | SOL-10876 | 26644.9922 | N/A |  |  | 29938 | -3293.0078 | -11%
K610 | NY | SOL-11158 | 26998.1 | 29381.58 | -2383.48 | -8.112% | 34545 | -7546.9 | -21.85% | 1. Inverter 2 (as per SE Inverter 1) — Units 1.1 and 1.2 tripped offline at 12:00, and Unit 1.3 tripped offline at 16:15 on 06/18. The inverter has remained offline since then. | 1. SR103141
M025 | NY | SOL-10392 | 14378.1797 | 27168.34 | -12790.1603 | -47.08% | 29661 | -15282.8203 | -51.52% | 1. Inverter 1 tripped offline at 14:45 on 05/26 and came back online at 08:15 on 06/13. It tripped offline again at 14:15 on 06/18 and came back online at 10:30 on 06/20. It tripped once more at 13:45 on 06/20 and came back online at 10:15 on 06/26. 2. Inverter 2, Unit 2.2 tripped offline at 14:30 on 05/25 and came back online at 09:45 on 06/20. It tripped offline again at 12:30 on 06/20 and came back online at 10:15 on 06/21. It tripped once more at 15:45 on 06/21, came back online at 10:15 on 06/26, and again tripped offline at 15:30 on 06/29 due to '3 Phase Possible Arc Detection'. 3.Inverter 3, Unit 3.3 tripped offline at 16:00 on 05/24 and came back online at 09:45 on 06/20. It tripped offline again at 14:00 on 06/20 and later came back online at 10:15 on 06/26. Unit 3.1 tripped offline at 13:00 on 05/30 and came back online at 09:45 on 06/20. 4. Inverter 1 tripped offline at 14:15 on 06/30. | 1. SR099791 2. SR099792, SR103096 3. SR099793 4. SR103710 | SR099792 | SR103096 | SR099793 | SR103710
M028 | NY | SOL-10381 | 21351.7988 | 20259.09 | 1092.7088 | 5.394% | 23402 | -2050.2012 | -8.761%
Q030 | NY | SOL-10878 | 25762.8359 | N/A |  |  | 27991 | -2228.1641 | -7.96%
Q130 | NY | SOL-10877 | 14657.909 | N/A |  |  | 16011.71 | -1353.801 | -8.455%
Q196 | NY | SOL-10879 | 19067.674 | N/A |  |  | 20705 | -1637.326 | -7.908%
Q220 | NY | SOL-10873 | 22339.375 | N/A |  |  | 24264 | -1924.625 | -7.932% | 1. The inverters are experiencing minor shading. | 1. SR103361
Q205 | NY | SOL-10922 | 26836.7812 | 31288.28 | -4451.4987 | -14.23% | 28490 | -1653.2188 | -5.803% | 1. Inverter 1, Unit 1.1 tripped offline at 09:00 on 06/01 and came back online at 19:00 on the same day. | 1. SR101940
Q400 | NY | SOL-10871 | 34967.6406 | N/A |  |  | 47087 | -12119.3594 | -25.74% | 1. Inverter 2, Unit 2.2 tripped offline at 10:30 on 06/08 and came back online at 11:45 on 06/16. Unit 2.1 tripped offline at 13:00 on 06/02, came back online at 11:45 on 06/16, tripped offline again at 17:00 on 06/16, and came back online at 11:45 on 06/23. 2. Inverter 1, Unit 1.2 was offline from 06/12 and came back online at 12:45 on 06/16. It went offline again at 17:15 on 06/19, came back online at 12:00 on 06/23, then went offline again at 05:15 on 06/25 and came back online at 13:45 on 06/27. 3. Inverter 3, Unit 3.1 tripped offline at 08:15 on 06/24 and came back online at 14:00 on 06/27. It tripped offline again at 13:45 on 06/29 and has been offline since then. 4. Inverter 2, Unit 2.1 did not start production on 06/30. | 1. SR100587, SR103188 2. SR102888 3. SR103641 4. SR103805 | SR103188 | SR102888 | SR103641 | SR103805
R003 | NY | SOL-10416 | 35472.3363 | 31288 | 4184.3363 | 13.37% | 42621 | -7148.6637 | -16.77% | 1. Inverter 2, Unit 2.1 tripped offline at 11:45 on 06/19 and has been offline since then. The unit is being RMA’d. | 1. SR103246
R007 | NY | SOL-10417 | 40259.1406 | 39836.05 | 423.0906 | 1.062% | 45310.59 | -5051.4494 | -11.15%
BK16 | NY | SOL-11093 | 40757.8125 | N/A |  |  | 45236 | -4478.1875 | -9.9% | 1. Inverter 4 went offline at 13:00 on 06/25 and came back online at 09:15 on 06/27, and again went offline at 13:30 on 06/29. | 1. SR103557
Trenton - Trenton East | IL | SOL-11060 | 404610 | 424129.5 | -19519.5 | -4.602% | 529693 | -125083 | -23.61% | 1. Inverter 1 underperforming by 100 kW Inverter 2 underperforming by 5 kW Inverter 7 underperforming by 15 kW Inverter 8 underperforming by 37 kW Trackers have not communicated since 04/23 due to storm damage; EPC is working on partial energization, with trackers in stow and inverters expected to be derated. | 1. SR100220
Trenton - Trenton West | IL | SOL-11061 | 190756.0524 | 284524.2 | -93768.1476 | -32.96% | 528624 | -337867.9476 | -63.91% | 1. The site was offline from 10:15 on 05/27 and came back online at 12:15 on 06/05. | 1. SR102012
Dakota - Dakota Solar 1 | IL | SOL-11113 | 532897 | 637314.1 | -104417.1 | -16.38% | 0 | 532897
X018 | NY | SOL-10418 | 15981.2804 | 12217.07 | 3764.2104 | 30.81% | 22996 | -7014.7196 | -30.5%
Janiak Solar | NY | SOL-10898 | 361767 | 384116.3 | -22349.3 | -5.818% | 426374 | -64607 | -15.15% | 1. The site tripped offline at 13:15 on 06/17 due to fluctuations in recloser voltages and came back online at 13:30 on 06/18. | 1. SR103076
County Route 11B | NY | SOL-10983 | 108145 | N/A |  |  | NA |  |  | 1. Trackers 76 and 142 have been stuck since 04/25. Additionally, 13 trackers - 3, 13, 16, 54, 67, 76, 82, 83, 99, 109, 142, 148, and 183 have been stuck since 05/05. 2. The site tripped offline at 11:15 on 05/18. USNE inspected the site and, after examining the transformer, determined that additional troubleshooting was required. The transformer was later re-energized on 06/03, and the site came back online at 10:55 on 06/03. | 1. SR097816 2. SR101645 | SR101645
Barone | NY | SOL-11034 | 116276 | N/A |  |  | 233057 | -116781 | -50.11% | 1. Trackers 11 and 73 were stuck from 04/27 and resumed tracking on 06/11. Tracker 86 was stuck from 06/13, and Tracker 84 was stuck from 06/16, both resumed tracking on 06/24. Tracker 108 was stuck from 06/24 and resumed tracking on 06/25. Tracker 103 has been stuck from 06/25 and resumed tracking on 06/27. 2. The site tripped offline at 16:00 on 06/06 and came back online at 11:35 on 06/07. 3. The site was offline from 13:25 to 15:00 on 06/20 as EV Solar was onsite to work on the TCU and inspect the inverter. | 1. SR100609 2. SR102630 3. SR103214 | SR102630 | SR103214
Cedarville | IL | SOL-11069 | 442351 | 418595.1 | 23755.9 | 5.675% | 542601.1 | -100250.1 | -18.48% | 1. All trackers have been stuck at 0.99 degrees since 05/07. | 1. SR101228
O'Brien Hill #1 | NY | SOL-11098 | 0 | N/A |  |  | N/A |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 140669 | N/A |  |  | 288848 | -148179 | -51.3% | 1. Tracker T02.D.37 was stuck at 0 degrees on 06/09. Further troubleshooting is required. 2. The site tripped offline at 14:25 on 06/25 due to a utility outage and came back online at 11:50 on 06/26. 3.Combiner Box 13 tripped offline at 19:10 on 06/25 and came back online at 14:45 on 06/26. | 1. SR102684 2. SR103541 3. SR103547 | SR103541 | SR103547
Trinity - Freeport | IL | SOL-11057 | 481318 | 411109.6 | 70208.4 | 17.08% | 544048 | -62730 | -11.53% | 1. TCU 3, 33 through 66 are stuck from 4/24/25 at 13:00CDT. 2. Inverter 2 has been derating by approximately 5 kW to 20 kW in the afternoons since 03/28. The issue is currently under EPC. 3. The site tripped offline at 23:45 on 06/26 and came back online at 15:15 on 06/27. | 1. SR098066 2. SR099545 3. SR103643 | SR099545 | SR103643
Ransom | NY | SOL-11157 | 156931 | N/A |  |  | 326042 | -169111 | -51.87% | 1. Tracker W-050 and trackers W-159 and W-166 were stuck at 45° and 0°, respectively. Additionally, trackers E-82, E-83, E-167, E-168, and E-169 have been deviating between 12:00 PM and 5:00 PM since 04/07. However, 4–5 trackers continue to show deviations. Trackers W-050 and W-160 have been stuck since 06/04, and tracker W-166 has been tracking incorrectly since 06/16. 2. The site was de-energized from 09:00 to 13:45 on 06/11 as Spartan Alternative Energy was onsite for transformer work. 3. The site was offline from 07:40 to 09:20 on 06/20 as EV Solar was onsite to work on the meter CT of Inverter 1. 4. The site tripped offline at 11:10 on 06/22 and came back online at 09:15 on 06/23. 5. Inverter 2 tripped offline at 14:45 on 06/28 and came back online at 06:45 on 06/30. | 1. SR099473 2. SR102805 3. SR103193 4. SR103271 5. SR103687 | SR102805 | SR103193 | SR103271 | SR103687
Horseheads - Wedge | NY | SOL-11160 | 165061 | N/A |  |  | 344639 | -179578 | -52.11% | 1. Site production was low on 06/25 due to technician was on site for preventive maintenance work. 2. The site went offline at 15:45 on 06/28 due to the circuit breaker being in the open position and later came back online at 09:45 on 06/30. | 1. PM13634 2. SR103689
Otisville - Shoddy Hollow | NY | SOL-11185 | 173192 | N/A |  |  | 363236 | -190044 | -52.32% | 1. All the trackers have been stuck mode since 05/14. 2. Combiner boxes 10, 14, 17, and 23 were taken offline on 06/23 as EV Solar was onsite for module replacement. They were re-energized after the work was completed. 3. Inverter 2 tripped offline at 18:40 on 06/23 due to "Overall Work State Stop" and came back online at 05:20 on 06/24. 4. The site tripped offline at 17:40 on 06/25 and came back online at 05:30 on 06/26. 5. Site production was low on 06/11 due to technician was on site for preventive maintenance work. 6. Site was taken offline by EV Solar on 06/10 from 14:20 to 15:25 to pictures of the CT's in the transformer. | 1. SR098693 2. SR103313 3. SR103353 4. SR103559 5. PM13738 6. SR102779 | SR103313 | SR103353 | SR103559 | SR102779
Wellsville - Chenunda Creek | NY | SOL-11187 | 181323 | N/A |  |  | 381833 | -200510 | -52.51% | 1. The site was offline from 09:25 to 11:15 on 06/30 as EV Solar was on site to work on CT#2. | 1. SR103737
DC: Washington - Essex Condominium | DC | SOL-10036 | 4453 | 5876.931 | -1423.931 | -24.23% | 5419.412 | -966.412 | -17.83% | 1. Low production/generation due to low irradiance on 06/09,06/14 ,06/15 ,06/16 & 06/17
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 6506 | 11997 | -5491 | -45.77% | 13161 | -6655 | -50.57% | 1.Inverter 2 has been offline since 03/28, reporting a fault current. 2. Meter power dropped to zero at 09:30 on 06/14 due to wiring issues but production was confirmed at meter level and were back to normal at 11:00 ,again tripped off at 10:00 on 06/17 and were back online at 19:30 on 06/19,tripped off at 09:45 on 06/20 and back online at 12:00 on 06/22,again tripped off at 11:30 and were back online at 19:00 on 06/26. | 1.SR100622,SR095581 2.SR100771
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 13229 | 10354 | 2875 | 27.77% | 13154 | 75 | 0.5702%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Jul
Generate Capital |  |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  |  | 53197393.8953 | 18342180.644 | 34855213.2513 | 190% | 50545171.8178 | 2652222.0775 | 5.247% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 22080.75 | 42520.39 | -20439.64 | -48.07% | 37634.39 | -15553.64 | -41.33% | 1. Inverter 1 is missing communications and offline as per the meter production and came back online on 07/11 | 1.SR103460
K041 | NY | SOL-10357 | 30806.7812 | 35182.89 | -4376.1087 | -12.44% | 32538 | -1731.2188 | -5.321% | 1.Low production/generation due to low irradiance on 07/14 ,07/14
K043 | NY | SOL-10358 | 35140.5 | 39838.042 | -4697.542 | -11.79% | 7003.033 | 28137.467 | 401.8% | 1. Inverter 1 middle unit dropped production 13 kW down at 12:00 on 06/04. Inverter fan is under replacement. 2.Inverter 3 middle unit(unit 3.2) is derating by 14kW since 06/11 and reporting "External fan fault" since 6/4 3.Estimated values are low in AE we have also verified the file which was given by GC | 1. SR102473 2.SR103360 | SR103360
K058 | NY | SOL-10360 | 0 | 0 | 0 |  | 28709 | -28709 | -100% | 1.Site was offline from 02/21 due to Phase C fuse was blown and parts were needed. | 1. SR097569 ,SR102535 | SR102535
K115 | NY | SOL-10361 | 5994.9688 | 15981.37 | -9986.4013 | -62.49% | 18780.49 | -12785.5213 | -68.08% | 1. 96 optimizers are down for site construction. 2.Inverter 1 tripped offline on 07/22 from 07:23 to 13:00 and producing "irradiance check " fault and again offline from 09:07 to 10:00 on 07/23 | 1.SR093291 2.SR104754 | SR104754
K152 | NY | SOL-10362 | 11235.5 | 11639.54 | -404.04 | -3.471% | 10840 | 395.5 | 3.649%
K166 | NY | SOL-10363 | 42074.5 | 45470.58 | -3396.08 | -7.469% | 39952.56 | 2121.94 | 5.311%
K206 | NY | SOL-10927 | 25801.2188 | 24180.51 | 1620.7088 | 6.703% | 24570 | 1231.2188 | 5.011%
K251 | NY | SOL-10365 | 20454.375 | 0 | 20454.375 |  | 25324.63 | -4870.255 | -19.23% | 1.Inverter 1 tripped offline at 13:00 on 06/12 and came back online on 07/10 2. Inverter module 1.0.153 12D31EC2-C5 is offline, reporting no comms with power optimizer. 3.Weather station stopped communicating on 11/22 at 07:00. | 1.SR102970 2. SR093292 3.SR093633 | SR093292 | SR093633
K269 | NY | SOL-10366 | 24601.3125 | 28866.1 | -4264.7875 | -14.77% | 25783.66 | -1182.3475 | -4.586% | 1.Inverters producing as expected and expected value and forecasted energy values diffrence.
K273 | NY | SOL-10367 | 19989.1875 | 0 | 19989.1875 |  | 30662 | -10672.8125 | -34.81% | 1. 26 optimizers are down for roof repair. 2. Weather station stopped communicating since 06/14/24. 3. Inverter 2 middle unit (unit 2.1) was offline on multiple days and reporting low voltage | 1. SR093294 2.SR104856 | SR104856
K287 | NY | SOL-10919 | 21277.7188 | 18223.17 | 3054.5488 | 16.76% | 22153 | -875.2812 | -3.951%
K298 | NY | SOL-10368 | 23346.625 | 24604.5 | -1257.875 | -5.112% | 26042 | -2695.375 | -10.35% | 1.Inverter 2 tripped offline at 12:00 and back online at 17:30 on 07/22, reporting a low irradiance check | 1.SR099824
K335 | NY | SOL-10370 | 23818.1875 | 27510.19 | -3692.0025 | -13.42% | 6708.597 | 17109.5905 | 255% | 1.Both inverters tripped offline on 07/05 at 08:00 and reporting "Grid Voltage" and came back online on 07/06 2. The estimated values in AlsoEnergy appeared lower, and there was a discrepancy between the values shown in the Configuration and Analysis sections. | 1.SR104039
K345 | NY | SOL-10920 | 28493.5938 | 16426.56 | 12067.0337 | 73.46% | 29496 | -1002.4062 | -3.398% | 1. Inverter 3 is underproducing due to unit(7E9C82CA) underproducing from 13:30 on 06/20 and reporting "external fan" fault. | 1.SR103259
K445 | NY | SOL-10373 | 23873.9062 | 25868.68 | -1994.7738 | -7.711% | 24192.71 | -318.8037 | -1.318%
K495 | NY | SOL-10374 | 101785.4705 | 100102.3 | 1683.1705 | 1.681% | 100968.4 | 817.0705 | 0.8092% | 1.Inverter 11 (left unit) was offline since 04/18, reporting a "DC Isolation Fault." During troubleshooting, it was discovered that following a firmware update, the inverter no longer displayed fault codes and continued to fail to produce power. SolarEdge technical support was contacted, and a callback was received. Case number 5713468 was created. | 1. SR101786
M020 | NY | SOL-10380 | 26263.7188 | 26808.87 | -545.1512 | -2.033% | 27263 | -999.2812 | -3.665%
M092 | NY | SOL-10383 | 25513.3125 | 27052.52 | -1539.2075 | -5.69% | 26962.78 | -1449.4675 | -5.376%
M143 | NY | SOL-10384 | 26932.8125 | 33267.06 | -6334.2475 | -19.04% | 28941.11 | -2008.2975 | -6.939% | 1. Inverter 3 left unit is having multiple trippings since 06/08 on high irradiance day. | 1. SR102672
M144 | NY | SOL-10385 | 41808.0625 | 45206.86 | -3398.7975 | -7.518% | 48675.37 | -6867.3075 | -14.11% | 1. Low production/generation due to low irradiance on 07/14 & 07/31
M167 | NY | SOL-10386 | 32401.5 | 23815.59 | 8585.91 | 36.05% | 35855.98 | -3454.48 | -9.634%
M188 | NY | SOL-10387 | 22118.3125 | 22518.45 | -400.1375 | -1.777% | 24672.09 | -2553.7775 | -10.35% | 1.Low production/generation due to low irradiance on 07/31
EMHC | NY | SOL-10351 | 8553.8281 | 7417.912 | 1135.9161 | 15.31% | 12191.91 | -3638.0819 | -29.84% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline | 1.SR093236
Q008 | NY | SOL-10397 | 0 | 0 | 0 |  | 36312 | -36312 | -100% | 1.Site stopped communicating from 03/25. On 03/27 Technician stated that main breaker tripped and malfunctioning. Site was remained offline till date. As per GenC, EPC has been responsive on the warranty claim. | 1.SR102532 , SR102533 | SR102533
Q018 | NY | SOL-10398 | 22422.5625 | 24285.08 | -1862.5175 | -7.669% | 19671.97 | 2750.5925 | 13.98%
Q021 | NY | SOL-10399 | 17811.25 | 17422.69 | 388.56 | 2.23% | 16686.18 | 1125.07 | 6.743%
Q025 | NY | SOL-10400 | 30847.0625 | 30210.9 | 636.1625 | 2.106% | 15399 | 15448.0625 | 100.3%
Q074 | NY | SOL-10402 | 20091.25 | 20099.01 | -7.76 | -0.03861% | 18770.07 | 1321.18 | 7.039%
Q115 | NY | SOL-10872 | 25668.5625 | 27335.48 | -1666.9175 | -6.098% | 24925.88 | 742.6825 | 2.98%
Q139 | NY | SOL-10403 | 15708.0625 | 17354.15 | -1646.0875 | -9.485% | 15860 | -151.9375 | -0.958% | 1.Some optimizers with production issues 1264FFBB-30 - Half production ,12639DA9-BB - Half production | 1. SR088282
Q157 | NY | SOL-10404 | 27253.8125 | 30897.83 | -3644.0175 | -11.79% | 27966.37 | -712.5575 | -2.548% | 1.Inverter 2 is underperforming 8kW compared to its peers since 07/06. Failed negative string connector repaired, inv 2 is producing normally on 07/16 | 1.SR104430
Q192 | NY | SOL-10406 | 42644.875 | 46844.32 | -4199.445 | -8.965% | 478.6818 | 42166.1932 | 8809% | Based on the site’s weather station data, the plant is performing as expected. The forecasted (theoretical) values appear lower because they are derived from long-term average weather data, typically spanning 10–15 years. In contrast, actual versus expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance. There may be a data glitch affecting the expected values.
Q210 | NY | SOL-10407 | 30659.75 | 35721.36 | -5061.61 | -14.17% | 33897 | -3237.25 | -9.55% | 1. Inverter 1, unit 1.1 tripped offline on 06/24 at 15:00 reporting "Residual Current Device" . Replaced DC relay board and re-energized the inverter. Issue resolved on 07/24 | 1. SR103569
Q229 | NY | SOL-10408 | 15332.0792 | 17350.71 | -2018.6308 | -11.63% | 14637.41 | 694.6692 | 4.746% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1. SR088813
Q231 | NY | SOL-10870 | 57414 | 60749 | -3335 | -5.49% | 61540 | -4126 | -6.705% | 1. Inverter 1, Unit 1.1 tripped offline at 12:30 on 07/11. Replaced defective optimizer from stock, inverter is producing normally on 07/14 | 1. SR104342
Q405 | NY | SOL-10409 | 65372.75 | 71921.91 | -6549.16 | -9.106% | 60634.29 | 4738.46 | 7.815% | 1.4 Inverter modules are offline. Will investigate next time on site. Module 1.0.64 Module 4.0.39 , 3.0.20 ,1.0.64 | 1. SR093324
Q435 | NY | SOL-10923 | 64450.375 | 67828.89 | -3378.515 | -4.981% | 84298 | -19847.625 | -23.54% | 1.Low production/generation due to low irradiance 07/31
Q485 | NY | SOL-10869 | 77438.625 | 61581.27 | 15857.355 | 25.75% | 80201.91 | -2763.285 | -3.445% | 1. Inverter 3 right unit tripped offline at 12:00 on 07/01 and reporting "Fault" in AE. Inverter faulted RSD, inspected array and inverter. Power cycled unit, inverter 3 producing as expected from 07/11 | 1. SR103857
Q490 | NY | SOL-10411 | 54376.1387 | N/A |  |  | 52505.61 | 1870.5287 | 3.563% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1.SR093326
Q620 | NY | SOL-10867 | 83649 | 85365.47 | -1716.47 | -2.011% | 84122.95 | -473.95 | -0.5634% | 1.Inverter modules 3.0.144 and 5.0.100 are offline | 1. SR093327
QMOA | NY | SOL-10415 | 7003.7 | N/A |  |  | 7555.046 | -551.346 | -7.298%
X024 | NY | SOL-10419 | 31410.5 | 32184.54 | -774.04 | -2.405% | 28524 | 2886.5 | 10.12% | 1.Inverter 2 offline from 12:20 to 12:41 on 07/24 due to technician was on site | 1.SR096294
X026 | NY | SOL-10420 | 28396.4 | 25893.72 | 2502.68 | 9.665% | 37688.65 | -9292.25 | -24.66% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1.SR095662
X090 | NY | SOL-10925 | 20376.1875 | 21371.14 | -994.9525 | -4.656% | 24800 | -4423.8125 | -17.84% | 1.Inverter 1 right unit is back online on 07/02 at 13:15 2. Inverter 1 right unit tripped offline at 07:00 on 07/18 and reporting "AC Freq Too High (Line 3)" | 1.SR103568 2.SR105209 | SR105209
X117 | NY | SOL-10422 | 20442.5 | 21974.4 | -1531.9 | -6.971% | 20331.66 | 110.84 | 0.5452%
X125 | NY | SOL-10423 | 37847.9375 | 38359.23 | -511.2925 | -1.333% | 37253.94 | 593.9975 | 1.594%
X134 | NY | SOL-10424 | 36328.625 | 26292.3 | 10036.325 | 38.17% | 37970 | -1641.375 | -4.323%
X135 | NY | SOL-10425 | 27094.9375 | 34359.57 | -7264.6325 | -21.14% | 30069 | -2974.0625 | -9.891% | 1. Inverter 1 unit 1.2 is derating by 30kW since 07/15. | 1.SR104744
X139 JHS 222 | NY | SOL-10426 | 45256.6235 | 47698.11 | -2441.4865 | -5.119% | 48383 | -3126.3765 | -6.462%
X140 | NY | SOL-10926 | 25634.0312 | 21347.36 | 4286.6712 | 20.08% | 25647 | -12.9688 | -0.05057%
X166 | NY | SOL-10427 | 26409.4 | 25666.1 | 743.3 | 2.896% | 28572 | -2162.6 | -7.569%
Murphy | MN | SOL-10094 | 1027570 | 1128104 | -100534 | -8.912% | 1079999 | -52429 | -4.855% | 1. Inverter 4 tripped offline at 12:45 on 07/01 and back online at 08:45 on 07/07, while tech on site inverter 5 is offline from 09:00 to 12:30. 2. Inverter 1 tripped offline at 10:45 on 07/08 and back online at 15:00 on 07/09 but inverter 1 is producing at its half production through out the month 3. Inverter 3 was offline from 08:00 to 10:30 on 07/11 while technician on site 4.Inverter 5 tripped offline at 10:30 and later PE was able to reset at 17:30 on 07/16 5. Inverter 2 tripped offline at 12:15 on 07/23 and back online at 08:00 on 07/24 | 1.SR101910 2.SR101354 3.PM7993 4.SR104543 5.SR104886 | SR101354 | SR104543 | SR104886
Terning | MN | SOL-10093 | 1103539.3317 | 1177067 | -73527.6683 | -6.247% | 1077330 | 26209.3317 | 2.433% | 1.Inverter 5 tripped offline at 11:00 on 07/14 and back online at 09:15 on 07/17 | 1.SR104398
Boas Road 04 | NY | SOL-10908 | 0 | 418297.2 | -418297.2 | -1 | 421307.46 | -421307.46 | -100% | 1. Meter stopped communicating from 14:05 on 03/16 till date. 2. Inverter 1 is back online at 07:15 on 07/11 3. Site lost communication on 07/07 at 23:40 and later back online at 07:10 on 07/11 but inverter 2 is offline and back online at 09:55 on 07/17 | 1.SR098641 2.SR103150 3.SR104128 | SR103150 | SR104128
Kelly Bridge Farm | NY | SOL-10911 | 356939 | 395735.4 | -38796.4 | -9.804% | 409604.48 | -52665.48 | -12.86% | 1. Inverters 26 are derating by 20kW down each compared to its peers since 06/04. 2. Inverters 28 to 33 are tripped offline at 13:25 on 06/23 due to damaged breaker. After install the new breaker inverters are back online at 09:40 on 07/09. 3. inverters 18 to 22 tripped offline from 08:55 to 11:35 on 07/07. due tech onsite and replceing the CB's. 4. Site was taken offline from 07:25 to 09:40 on 07/09 due to technision was on site and install the new breaker. 5. Inverter 10 went offline at 06:30 on 07/27, reporting 'standby mode'. It later self-resolved and came back online at 06:30 on 07/28. | 1. SR102506 2. SR103185 3. SR102919 4. SR103185 5. SR105115 | SR103185 | SR102919 | SR103185 | SR105115
Pool Brook Road | NY | SOL-10909 | 304116 | 391072.41 | -86956.41 | -22.24% | 388129.3 | -84013.3 | -21.65% | 1. Inverter 8 tripped offline at 13:05 on 07/20 due to B-phase has blown fuse. 2. Inverters 1 to 16 and 20 to 33 tripped offline at 16:05 on 07/24 and came back online at 06:00 on 07/25. They tripped offline again at 18:00 on 07/28. | 1. SR104724 2. SR105002 | SR105002
Sackett Lake | NY | SOL-10910 | 372255 | 182350.26 | 189904.74 | 104.1% | 401920.7 | -29665.7 | -7.381% | 1. Inverter 1 tripped offline at 16:45 on 07/03 reporting "Isolation resistance values out of limits". later seif resolved and back online at 06:00 on 07/04 | 1. SR104001
Burritt Road | NY | SOL-10913 | 439000 | 460347.77 | -21347.77 | -4.637% | 411700.36 | 27299.64 | 6.631%
Villa Roma 1 | NY | SOL-10914 | 338515 | 3881.75 | 334633.25 | 8621% | 360546.51 | -22031.51 | -6.111% | 1.Expected energy values are reporting very low. Created a case #66639 with GPM, As per GPM the BOM has been frozen from 02/27. | 1. SR099403
Villa Roma 2 | NY | SOL-10915 | 327962 | 355213.51 | -27251.51 | -7.672% | 349710.41 | -21748.41 | -6.219%
Washington 1 | NY | SOL-10912 | 414100 | 455057.17 | -40957.17 | -9% | 406846.2 | 7253.8 | 1.783% | 1. Inverter 2 tripped offline at 06:00 on 07/22, reporting a 'PH. R blower' fault, and came back online at 09:55 on 07/23. | 1. SR102665
Washington 3 | NY | SOL-10828 | 468035 | 1177020.71 | -708985.71 | -60.24% | 497085.28 | -29050.28 | -5.844% | 1. Inverter 1 experienced multiple trip events starting from 07/17. A technician later cleared a ground fault, and the inverter returned to normal operation on 07/23. 2. POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1. SR104609 2. SR093024 | SR093024
Washington 4 | NY | SOL-10829 | 512454 | 540275.93 | -27821.93 | -5.15% | 498240.8 | 14213.2 | 2.853%
Big Tree | NY | SOL-10966 | 436120 | 435290 | 830 | 0.1907% | 416811.05 | 19308.95 | 4.633% | 1. Combiner box 7,string 1 is underperforming since 03/21.Needs further investigation. | 1. SR098866
Canoga | NY | SOL-10965 | 564710 | N/A |  |  | 0 | 564710 |  | 1.The site went offline at 09:55 on 03/27 due to utility work at the substation. On 07/16, a technician re-energized the inverters, and the site came back online at 09:35 on 07/16. 2. Site was offline at 04:30 on 07/21 and later tecnician Power cycled the DAS and site is back online at 02:05 on 07/22. | 1. SR098998 2. SR104684 | SR104684
County Route 84 | NY | SOL-10967 | 935320 | 914380 | 20940 | 2.29% | 1051868.43 | -116548.43 | -11.08% | 1. Inverter 4 tripped offline at 13:15 on 06/27. The inductor fan was sent for RMA on 06/27. Later, a technician replaced the inductor fan, and the inverter was back online at 14:10 on 07/07. 2. The site tripped offline at 18:55 on 07/13 and back online at 03:25 on 07/14. It tripped offline again at 11:50 on 07/20 due to technician working on site, and was back online at 13:40 on 07/21 | 1. SR103651 2. SR104374 | SR104374
Donati | NY | SOL-10968 | 547550 | N/A |  |  | 545503.25 | 2046.75 | 0.3752% | 1.Weather station Reporting 0 value from 05/31/24. POA sensors need to be replaced. 2.Stuck trackers: A01, A05 through A07, A10, F19, F21 through 22, F27, F33, G14.Further troubleshoting is required. | 1.SR092964 2.SR095253,SR098877 | SR095253 | SR098877
Henrietta | NY | SOL-10972 | 1155000 | 1113180 | 41820 | 3.757% | 1152537.6 | 2462.4 | 0.2137%
NY 70 | NY | SOL-10970 | 1218390 | 1215880 | 2510 | 0.2064% | 1269880.53 | -51490.53 | -4.055% | 1. The site was taken offline from 08:15 to 11:30 and again from 14:55 to 16:05 on 07/29, as the utility performed emergent work at the site. | 1. SR105211
Reid | NY | SOL-10991 | 827385.8259 | 889116.1 | -61730.2741 | -6.943% | 94887 | 732498.8259 | 772% | 1. Inverters 14 , 5, 29 and 32 have also tripped offline at 13:40 from 06/30 producing fault "" Grid voltage out of range".and except inveretr 14 is RMA'd remaining inverters back online at 14:30 on 07/07. 2.Inverter 9 was offline on multiple days of the month. 3.Inverters 28 was frequently trippping on and off.Inverter 28 was completly offline from 06/20 and later back online at 14:45 on 07/07. and again tripped offline at 12:30 on 07/10 and inveretr is under RMA'd 4. Inverter 20 tripped offline at 12:15 on 06/21 and remained offline throughout the month due to "Grid voltage out of range" and "Power Module Protection - Protect0120" respectively. 5. Inverter 30 was offline on multiple days of the month. 6. Inverter 23 tripped offline at 15:00 on 07/13 and reporting "Grid Phase Voltage Out of Range - GridV.OutLim". and later back online at 08:30 on 07/16. 7. Inverter 1 is derating by 25kW at 12:30 on 07/13 compared to peers and reporting "External Fan Err - ExtFanerr". after replacening the fan inverters is back to normal operation on 07/16. 8. Pad 1(1-20) inverters tripped offline at 19:20 on 07/17 and back online at 10:45 on 07/18. 9. Inverter 5 tripped offline at 14:00 on 07/21 and reporting Grid Line Voltage Out of Range - GridV.OutLim. 10 . Inverter 32 tripped offline at 12:00 on 07/23 and reporting "Grid Phase Voltage Out of Range - GridV.OutLim" and later closeing bracker inverter is back online at 09:00 on 07/28. 11. Inverter 33 tripped offline and reporting "Grid Phase Voltage Out of Range - GridV.OutLim" and later closeing bracker inverter is back online at 09:00 on 07/28. 12. Inverters 3,9,28 & 30 have tripped offline at 11:45 on 07/28 and reporting Grid Line Voltage Out of Range - GridV.OutLim and offline throughout the month. | 1. SR103260, SR103257 2. SR102335, SR102682, SR104557 3. SR102682,SR103181 SR104208 4. SR103257 5. SR103260, SR104208 6. SR104370 7. SR104371 8. SR104594 9. SR104741 10. SR104887 11. SR104998 12. SR105204 | SR103257 | SR102335 | SR102682 | SR104557 | SR102682 | SR103181 | SR104208 | SR103257 | SR103260 | SR104208 | SR104370 | SR104371 | SR104594 | SR104741 | SR104887 | SR104998 | SR105204
Sangolqui | NY | SOL-10975 | 556270 | 555700 | 570 | 0.1026% | 534834.66 | 21435.34 | 4.008%
State Highway 17B | NY | SOL-10988 | 844420 | 841370 | 3050 | 0.3625% | NA |  |  | 1. Inverters 1 tripped offline at 14:25 on 06/30 after replaceing the DC motor, Inverter is back online at 14:15 on 07/03. 2. Site was taken offline from 09:20 to 10:20 on 07/15 due to technician was on site and Cleaned transformer. | 1. SR103671 2. SR103452, PM7683 | SR103452
State Route 14A | NY | SOL-10997 | 0 | N/A |  |  | 1023871.6 | -1023871.6 | -100% | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required. On 07/02 technician was after pulling event files from the SEL for analysis. The site remains offline. | 1. SR101820, SR099347, SR103655 | SR099347 | SR103655
West Creek | NY | SOL-10995 | 952660 | 905450 | 47210 | 5.214% | 1056166.02 | -103506.02 | -9.8% | 1.Site offline at 14:35 on 07/03 and site came back online at 07:50 on 07/07 due to utility outage | 1. SR103990
Wildflower | NY | SOL-10982 | 892850 | 890492 | 2358 | 0.2648% | 992227.03 | -99377.03 | -10.02% | 1. Combiner box 33 is being isolated from 07/18 due to hotspot found during the PM to prevent any further thermal damage. On 07/29 technician has re-energized the combiner box 33. Additional Troubleshooting is required to re-energize the combiner 11 and filter replacement 2.Inverters tripping on and offline from 10:55 to 14:10 due to technician was on site to perform preventive maintanance | 1.SR104624 2.PM1903
Glen Mary 1 | NY | SOL-10993 | 1034840 | 1030810 | 4030 | 0.391% | 998812.44 | 36027.56 | 3.607% | 1.Site tripped offline from 07:30 to 20:15 on 07/25 due to utility outage 2.Site tripped offline at 15:35 on 07/26 and came back online at 12:45 on 07/27 | 1. SR105048 2.SR105120 | SR105120
Glen Mary 2 | NY | SOL-10994 | 461130 | 216810 | 244320 | 112.7% | 425618.76 | 35511.24 | 8.343% | 1.Site tripped offline due to utility outage at 07:35 on 07/25 and came back online at 06:15 on 07/26 2.Weather station stopped communicating from 07/04 and regained on 07/20 | 1. SR105049
Telegraph 1 | NY | SOL-11003 | 758150 | N/A |  |  | 748051.86 | 10098.14 | 1.35% | 1.Site tripped offline from 08:15 to 10:30 and 14:55 to 16:05 on 07/209 due to utility outage | 1.SR105225
Telegraph 2 | NY | SOL-11004 | 399640 | N/A |  |  | 390141.68 | 9498.32 | 2.435% | 1.Site tripped offline from 08:!5 to 09:25 and 14:55 to 16:05 on 07/29 due to utility outage | 1.SR105226
Cafferty Hill | NY | SOL-10996 | 1070170 | 1096662.81 | -26492.81 | -2.416% | 1010963.44 | 59206.56 | 5.856% | 1.Site tripped offline from 16:15 to 17:10 on 07/20 | 1.SR104664
Dunkleman | NY | SOL-11008 | 1328630 | 1325930 | 2700 | 0.2036% | 1303096.45 | 25533.55 | 1.959% | 1.Currently, the following trackers are stuck Group 1: 57 & 119 Group 2: 24, 27, 32, 36, 39, 43, 54, 59, 61, 97, 114, & 124. A total of 14 tracker control units are struck from 06/11 | 1. SR095109
Route 19 1 | NY | SOL-11001 | 526400 | 524990 | 1410 | 0.2686% | 527552.5 | -1152.5 | -0.2185% | 1.Site tripped offline from 14:55 to 16:05 on 07/29 | 1.SR105216
Route 19 2 | NY | SOL-11002 | 1275880 | 1272140 | 3740 | 0.294% | 1305988.63 | -30108.63 | -2.305% | 1.Site tripped offline from 08:20 to 11:35 and 15:00 to 16:05 on 07/29 | 1. SR105218
Yellow Mills 1 | NY | SOL-11006 | 457718 | 455797 | 1921 | 0.4215% | 434537.61 | 23180.39 | 5.334%
Yellow Mills 2 | NY | SOL-11005 | 452895 | N/A |  |  | 450519.38 | 2375.62 | 0.5273%
Yellow Mills 3 | NY | SOL-11007 | 431452 | 429805 | 1647 | 0.3832% | 428647.82 | 2804.18 | 0.6542%
Catskill | NY | SOL-11021 | 359700 | 358236 | 1464 | 0.4087% | 783825.25 | -424125.25 | -54.11% | 1.Site was offline from 07/14. On 07/25 Technician has replaced the CTs on the inverter 2 but inverter remained offline. Upon further troubleshooting technician found LVRT board and communication board need replaced on the inverters. Technician has followed up with Sungrow for the replacement. Currently, both inverters will remain offline until parts being replace | 1.SR104383
Eddy Ridge | NY | SOL-11054 | 648019 | 646353 | 1666 | 0.2578% | 648740 | -721 | -0.1111% | 1.The inverter is exceeding its curtailment at 2338KW since 8am on 05/10 . 2.Site tripped offline at 08:50 to 14:45 on 07/26 3. Trackers 1 through 49 are currently stuck. | 1.SR101282 2.SR105110 3. SR105180 | SR105110 | SR105180
Ridgeway #1 | NY | SOL-11018 | 1451284 | 1447271 | 4013 | 0.2773% | 1342085.15 | 109198.85 | 8.137% | 1.Site was offline from 11:00 - 15:15 on 07/08 2. Inverter 2 tripped offline from 7:55 to 08:35 on 07/20 due to Overall Work state as "STOP". | 1.SR104142 2.SR104657 | SR104657
Rivard 1 | NY | SOL-11011 | 1028409.2893 | 1098061 | -69651.7107 | -6.343% | 1115777 | -87367.7107 | -7.83% | 1.Inverter 1 tripped offline again soon after the previous site visit on 7/11, reporting "Error error". On 07/16 Inverter 1 has been re-energized came back online at 10:00 2.Weather station lost communication from 03/29. | 1. SR104455
Rivard 2 | NY | SOL-11012 | 1175701.791 | 1148796 | 26905.791 | 2.342% | 1076280 | 99421.791 | 9.238% | 1.Tracker control 33 - 90, 129 - 136, 148 , 20-32, 123-128, 172-183 are not communicating & tracker 156 , 121 is stuck and production dropped (approxmately ) 25 kW down. On 07/24 after re-energized the tracker motor, all trackers are currently tracking | 1.SR095073
Ridgeway #2 | NY | SOL-11027
Spencer | NY | SOL-11017 | 1365998 | 1361782 | 4216 | 0.3096% | 1303450 | 62548 | 4.799% | 1.Tracker 169 is stuck from 07/17 | 1. SR101152
Reisender | NY | SOL-10886 | 383420 | 391343 | -7923 | -2.025% | 415133.27 | -31713.27 | -7.639% | 1.Site tripped offline at 09:45 from 06/30 and it came back online at 09:30 on 07/01 | 1.SR103760
Finney | NY | SOL-10999 | 996120 | 994390 | 1730 | 0.174% | 1313701.15 | -317581.15 | -24.17% | 1.Inverter 1 went offline on 07/01 and came back online at 15:47 on 07/02. It tripped offline again on 07/07 and returned online on 07/10. Once more, Inverter 1 went offline on 07/15 and came back online at 10:48 on 07/25. 2.Site was offline from 07/09 and it came back online on 07/10 | 1.SR103538 2.SR103538 3.SR104184 | SR103538 | SR104184
Davis Solar | NY | SOL-10958 | 392668 | 443281.7 | -50613.7 | -11.42% | 479574 | -86906 | -18.12% | 1.Inverter started for production at 13:45 on 07/04 2.Inverter tripped offline from 10:00 to 15:15 on 07/07 and again inverter tripped offline from 10:15 to 12:45 on 07/09 3.Inverter tripped offline 10:10 to 12:00 and 13:36 to 14:40 on 07/18 due to SMA technician was on site. 4.Inverter tripped offline from 06:00 to 09:25 on 07/21 and again inverter tripped offline from 10:09 to 10:36 and 14:00 to 14:42 on 07/29 | 1.SR104018 2.SR104092 3.SR104283 4.SR104691 5. SR104691 | SR104092 | SR104283 | SR104691 | SR104691
Genesee | NY | SOL-10951 | 1001760.5 | 1000080.71 | 1679.79 | 0.168% | 1013360.34 | -11599.84 | -1.145% | 1.Trackers 23, 24, 33, 37, and 72 through 151 have been stuck since 06/02 | 1. SR102328
Landau I | NY | SOL-10891 | 429340 | N/A |  |  | 448929.38 | -19589.38 | -4.364%
Landau II | NY | SOL-10895 | 374100 | N/A |  |  | NA |  |  | 1. Inverter 2 tripped offline at 14:45 on 05/31 due to the AC breaker switch being open.After replacing AC breaker inverter 2 came back online at 17:55 on 07/07 2.Inverter 2 tripped offline at 11:45 on 07/08. It came back online at 12:45 on 07/12 and again inverter 2 tripped offline at 08:05 it came back online on 07/14 again inverter tripped offline 2 from 12:00 to 15:50 3.Site tripped offline from 09:40 to 12:55 on 07/15 4.Inverter 2 tripped offline from 08:50 to 13:35 on 07/20 5.Site tripped offline at 11:!5 on 07/21 and came back online at 15:05 on 07/22 and also inverter 2 offline on 07/23 and again site tripped offline at 17:00 on 07/24 it came back online at 09:45 on 07/25 6.Inverter 2 tripped offline from 08:55 to 14:15 on 07/26 and again inverter 2tripped offline at 11:55 07/27 and came back online on 07/28 at 08:45 and again offline from 12:!5 to 15:25 on same day 7.Inverter 2 tripped offline from 10:05 to 14:10 on 07/29 | 1.SR104727 2.SR104138 3.SR104422 4.SR104601 5. SR104708 6.SR105105 7.SR105276 | SR104138 | SR104422 | SR104601 | SR104708 | SR105105 | SR105276
New Beginnings | NY | SOL-10890 | 420830 | 435980.89 |  |  | 430014.12 | -9184.12 | -2.136%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 1262399 | 1316479 | -54080 | -4.108% | 1265415 | -3016 | -0.2383% | 1.Site tripped offline from 08:30 to 11:15 on 07/26 | 1.SR105107
Brodhead Solar, LLC | NY | SOL-10899 | 450232 | 464945.2 | -14713.2 | -3.165% | 543814.2 | -93582.2 | -17.21% | 1.NCU 1 tracker 10 which is RMAd. Tracker 9,38 and 35 are tracking at site but not communicating properly in AE as per technician. | 1. SR104075
Svenski | NY | SOL-10894 | 406997 | N/A |  |  | 455483.42 | -48486.42 | -10.65% | 1. Inverter 1 has tripped offline at 18:20 and AC Breaker is in Open State and reporting "STOP: PARAMETER INVOPMOD". After remote reset inverter came back online at 07:40. Inverterr again tripped offline from 06:00 to 12:50 on 07/04 and again inverter tripped offline at 06:00 to 09:35 on 07/08 and again inverter tripped offline from 06:00 to 09:10 on 07/11 and again inverter trippped offline 10:45 to 14:20 on 07/14 2.Inverter tripped offline from 11:25 to 11:50 on 07/28 | 1.SR103943 2. SR105161 | SR105161
Bantam | NY | SOL-10986 | 109500 | 418980 | -309480 | -73.87% | 1295680.06 | -1186180.06 | -91.55% | 1.Inverter 1 tripped offline at 16:40 on 05/26 and is currently in an open AC breaker switch state. Water intrusion and condensation were found inside Inverter 1 and its DC compartment, but no internal damage was observed. Additionally, four combiner boxes also had water intrusion and have been isolated. For safety reasons, the inverter remains offline, and further troubleshooting is required. 2.The weather station (POA2, GHI, rPOA) has stopped communicating since 18:10 on 05/27. 3.Site tripped offline from 07:20 to 11:45 on 07/26 | 1. SR101947 2.SR102015 3. SR105108 | SR102015 | SR105108
Bogart | NY | SOL-10887 | 0 | 398556.16 | -398556.16 | -100% | 419353.86 | -419353.86 | -100% | 1. The inverter went offline on 06/28 because the AC breaker switch was in the "Open" state and has remained offline since then. | 1. SR103685
Dubois | NY | SOL-10892 | 386460 | 386385.12 | 74.88 | 0.01938% | NA |  |  | 1. Inverter tripped offline at 18:20 on 07/07 and reporting "F6:LOW VAC" and it came back online at 15:05 on 07/08 | 1.SR104120
Salt Point | NY | SOL-10888 | 416220 | 416220 | 0 | 0% | 514904.5 | -98684.5 | -19.17% | 1.Site tripped offline at 17:45 on 07/04 and site ccame back online at 19:30 on 07/05 2.Site offline at 19:00 on 07/09 and came back online at 09:30 on 07/10 3.Inverters tripped offline from 20:50 on 07/10 and it came back online at 08:30 on 07/11 4. Inverter tripped offline at 18:10 on 07/11 and it came back online at 07:20 on 07/12 5.Inverter offline from 12:50 to 14:05 on 07/17 due to technician was on site. 6. Site tripped offline from 19:00 to 20:00 on 07/25 | 1.SR104019 2.SR104175 3. SR104235 4.SR104341 5. SR104445 6.SR104920 | SR104175 | SR104235 | SR104341 | SR104445 | SR104920
Wheatland 2A | NY | SOL-10971 | 1082680 | 1080840 | 1840 | 0.1702% | 1177354.56 | -94674.56 | -8.041% | 1.Inverter 1 tripped offline at 14:45 and came back online at 09:30 on 07/14 2.Site tripped offline from 13:30 to 14:20 on 07/16 | 1. SR104335 2. SR104540 | SR104540
Wheatland 2B | NY | SOL-10961 | 1133400 | 1131560 | 1840 | 0.1626% | 1168051.71 | -34651.71 | -2.967% | 1. 15 trackers are currently stuck from 03/21 NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 2.Site tripped offline from 13:30 to 14:25 on 07/16 due to fluctuations in utility voltages | 1.SR098860 2. SR104541 | SR104541
Brickchurch | NY | SOL-10889 | 0 | 519962.55 | -519962.55 | -100% | 532046.63 | -532046.63 | -100% | 1.Inverter 1 offline from 07/01 is reporting the AC breaker state as OPEN. Inverter 1 to be RMA'ed and remain offline through out the month. | 1. SR103824
McCarthy Solar | NY | SOL-10992 | 211620 | N/A |  |  | 448453.17 | -236833.17 | -52.81% | 1. Site tripped offline at 7:10 at 07:10 since 06/24 and Site re-energized on 07/04 at 11:30 2. Site tripped offline at 17:35 from 07/18 | 1. SR103367 2. SR104633 | SR104633
Costanza | NY | SOL-10907 | 404580 | 404631.91 | -51.91 | -0.01283% | 449076.09 | -44496.09 | -9.908% | 1.Inverter 1 tripped offline at 14:25 on 07/01 and reporting "AC breaker Switch Open".After Closed in SEL. Site came back online on 07/02 at 08:15 2.Inverter tripped offline at 06:00 on 07/08 and came back online on 07/09 at 14:13 3. Inverter tripped offline at 07:00 on 07/13 and reporting "AC Breaker State Open and came back online on 07/14 at 08:25 4.Inverter offline from 06:00 to 11:24 on 07/18 5.Inverter offline from 06:00 to 11:!0 on 07/23 | 1.SR103852 2.SR104141 3. SR104367 4. SR104600 5. SR104850 | SR104141 | SR104367 | SR104600 | SR104850
Lockenhurst Pond | NY | SOL-11000 | 484585 | 522005.2 | -37420.2 | -7.169% | 531355 | -46770 | -8.802%
Drinkwater | NY | SOL-10896 | 466130 | 454000 | 12130 | 2.672% | 460623.61 | 5506.39 | 1.195%
Altamont | NY | SOL-11085 | 877117 | 899395.7 | -22278.7 | -2.477% | 754982.6 | 122134.4 | 16.18%
Krumkill North | NY | SOL-11086 | 836577 | 922798.5 | -86221.5 | -9.343% | 844821.9 | -8244.9 | -0.9759%
Krumkill South | NY | SOL-11087 | 695464 | 735498 | -40034 | -5.443% | 662314.2 | 33149.8 | 5.005%
X092 | NY | SOL-11189 | 21888 | 22130.17 | -242.17 | -1.094% | 23075 | -1187 | -5.144%
X093 | NY | SOL-10932 | 11283.9199 | 15307.49 | -4023.5701 | -26.28% | 16257 | -4973.0801 | -30.59% | 1. Inverter 1 has been offline since 12:00 on 06/24.Inverter came back online on 07/21 | 1.SR103457
X095 | NY | SOL-10929 | 21468.9141 | 19545.91 | 1923.0041 | 9.838% | 22228 | -759.0859 | -3.415%
X181 | NY | SOL-10428 | 40966.7344 | 34560.46 | 6406.2744 | 18.54% | 41522 | -555.2656 | -1.337% | 1. The inverters have been offline since 12:00 on 06/24. On 07/02 inverters cam eback online at 11:45 | 1. SR103482
X415 | NY | SOL-10429 | 25868.9766 | 22259.89 | 3609.0866 | 16.21% | 24392 | 1476.9766 | 6.055%
K198 | NY | SOL-10930 | 18358.1641 | 18103.17 | 254.9941 | 1.409% | 18689 | -330.8359 | -1.77% | 1. Inverter 2 unit 2.3 offline from 07/26 | 1. SR105122
K203 | NY | SOL-11190 | 24407.1 | 21909.75 | 2497.35 | 11.4% | 25198 | -790.9 | -3.139% | 1.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
K213 | NY | SOL-11191 | 27870.1 | 29258.25 | -1388.15 | -4.744% | 26555 | 1315.1 | 4.952%
K217 | NY | SOL-10933 | 14644.6484 | 13647.47 | 997.1784 | 7.307% | 14632 | 12.6484 | 0.08644%
K307 | NY | SOL-10876 | 30193.3281 | 28697.91 | 1495.4181 | 5.211% | 30546 | -352.6719 | -1.155%
K610 | NY | SOL-11158 | 25973.6 | 33773.86 | -7800.26 | -23.1% | 35413 | -9439.4 | -26.66% | 1. Inverter 2 (as per SE Inverter 1) — Units 1.1 and 1.2 tripped offline at 12:00, and Unit 1.3 tripped offline at 16:15 on 06/18. The inverter has remained offline and SolarEdge has rmad the center unit. | 1. SR103141
M025 | NY | SOL-10392 | 17221.1328 | 31789.36 | -14568.2272 | -45.83% | 31160 | -13938.8672 | -44.73% | 1.Inverter 2 left unit tripped offline at 15:30 on 06/29 due to '3 Phase Possible Arc Detection'. On 7/10 technician Inspected array, no issues found. Reset inverter, online and producing. 2. Inverter 1 tripped offline at 14:15 from 06/30. parts being RMAD 3.Inverter 3 left unit tripped offline at 15:00 on 06/30. On 07/11 technician investigated inverters 1, 2 and 3. Inverter 1 has been RMA'd. Inverters 2 and 3 were restored to full capacity after performing system checks. 4. Inverter center unit many intermittent tripping events | 1. SR103096 2. SR103710 3.SR103871 4. SR104959 | SR103710 | SR103871 | SR104959
M028 | NY | SOL-10381 | 24044.498 | 22765.21 | 1279.288 | 5.619% | 24106 | -61.502 | -0.2551%
Q030 | NY | SOL-10878 | 28858.4609 | 28301.79 | 556.6709 | 1.967% | 28977 | -118.5391 | -0.4091%
Q130 | NY | SOL-10877 | 16564.2891 | 15232.4 | 1331.8891 | 8.744% | 16423.27 | 141.0191 | 0.8587%
Q196 | NY | SOL-10879 | 21595.4588 | 21688.12 | -92.6612 | -0.4272% | 21304 | 291.4588 | 1.368%
Q220 | NY | SOL-10873 | 25706.3906 | 28923 | -3216.6094 | -11.12% | 24647 | 1059.3906 | 4.298% | 1. The inverters are experiencing minor shading. | 1. SR103361
Q205 | NY | SOL-10922 | 29880.3438 | 35274.04 | -5393.6963 | -15.29% | 29435 | 445.3438 | 1.513%
Q400 | NY | SOL-10871 | 28683.4375 | N/A |  |  | 48524 | -19840.5625 | -40.89% | 1. Inverter 3 and unit 3.1 tripped offline at 13:45 on 06/29 and has been offline since then. 2.Inverter 2, Unit 2.1 offline from 06/30. 07/15 technician 2 optimizers replaced, inverter is operating normally. | 1. SR103641 2. SR103805 | SR103805
R003 | NY | SOL-10416 | 38385.1094 | 44378.38 | -5993.2706 | -13.5% | 43732 | -5346.8906 | -12.23% | 1. Inverter 2, Unit 2.1 tripped offline at 11:45 on 06/19 and has been offline since then. The unit is being RMA’d. | 1.SR103246
R007 | NY | SOL-10417 | 47890.6875 | 47595.02 | 295.6675 | 0.6212% | 47903.21 | -12.5225 | -0.02614%
BK16 | NY | SOL-11093 | 47968.9844 | 47268.57 | 700.4144 | 1.482% | 46590 | 1378.9844 | 2.96%
Trenton - Trenton East | IL | SOL-11060 | 408839 | 466838 | -57999 | -12.42% | 551866 | -143027 | -25.92% | 1. Inverter 1 underperforming by 100 kW Inverter 2 underperforming by 5 kW Inverter 7 underperforming by 15 kW Inverter 8 underperforming by 37 kW Trackers have not communicated since 04/23 due to storm damage; EPC is working on partial energization, with trackers in stow and inverters expected to be derated. 2. The site tripped offline at 07:00 on 07/19 and later came back online at 16:00 on 07/21. | 1. SR100220 2. SR104636 | SR104636
Trenton - Trenton West | IL | SOL-11061 | 279491 | 396472.3 | -116981.3 | -29.51% | 552240 | -272749 | -49.39% | 1. Inverter 1 was offline from 05:45 on 07/14 due to an 'Isolation fault' and came back online at 15:15 on 07/14. The inverter started production late on 07/15 and 07/16. It went offline again at 14:45 on 07/17 and later came back online at 11:15 on 07/18. 2. The site tripped offline at 06:00 on 07/19 and came back online at 07:30 on the same day. | 1. SR104413 2. SR104637 | SR104637
Dakota - Dakota Solar 1 | IL | SOL-11113 | 498126 | 522565.8 | -24439.8 | -4.677% | 396944 | 101182 | 25.49% | 1. The site was offline from 05:15 to 12:00 on 07/10 due to a planned outage by the utility. 2. The site tripped offline at 12:15 on 07/16 and later came back online at 15:15 on the same day. The site tripped offline again at 10:30 on 07/19 and came back online at 14:00 on the same day. | 1. SR104168 2. SR104538 | SR104538
X018 | NY | SOL-10418 | 21239.7391 | 14102.8 | 7136.9391 | 50.61% | 23493 | -2253.2609 | -9.591% | 1. Inverter 1 has been underperforming by 13 kW due to a 'Fault' since 07/11. | 1. SR104292
Janiak Solar | NY | SOL-10898 | 398017 | 428103.8 | -30086.8 | -7.028% | 457863 | -59846 | -13.07% | 1. The site went offline at 17:15 on 07/03 due to a utility outage and later came back online at 07:30 on 07/05. | 1. SR104007
County Route 11B | NY | SOL-10983 | 1436404 | 1431678 | 4726 | 0.3301% | NA |  |  | 1. Trackers 76 and 142 have been stuck since 04/25. Additionally, 13 trackers (3, 13, 16, 54, 67, 76, 82, 83, 99, 109, 142, 148, and 183) have been stuck since 05/05, and tracker 190 has been stuck since 07/10. | 1. SR97816
Barone | NY | SOL-11034 | 670991 | 667986 | 3005 | 0.4499% | 757195 | -86204 | -11.38% | 1. The inverter tripped offline at 05:55 on 07/02 and later came back online at 10:15 on 07/02. 2. The site tripped offline at 15:10 on 07/03 due to a utility outage and later came back online at 12:15 on 07/05. 2. The site tripped offline at 11:40 on 07/26 due to a utility outage and later came back online at 10:25 on 07/27. | 1. SR103880 2. SR104002 3. SR105114 | SR104002 | SR105114
Cedarville | IL | SOL-11069 | 412476 | 392183 | 20293 | 5.174% | 559363.6 | -146887.6 | -26.26% | 1. All trackers have been stuck at 0.99 degrees since 05/07. | 1. SR101228
O'Brien Hill #1 | NY | SOL-11098 | 0 | N/A |  |  | NA |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 1037428 | 1037322 | 106 | 0.01022% | NA |  |  | 1. Tracker T02.E.37 has been stuck since 06/30 and T01.A.03 has been stuck since 07/14. Both trackers later resumed regular operation on 07/28. 2. The site tripped offline at 14:20 on 07/04 due to a utility outage and later came back online at 10:40 on 07/07. | 1. SR102684 2. SR104020 | SR104020
Trinity - Freeport | IL | SOL-11057 | 442554 | 500503.4 | -57949.4 | -11.58% | 569424 | -126870 | -22.28% | 1.Inverter 2 has been derating by approximately 5 kW to 20 kW in the afternoons since 03/28. The issue is currently under EPC. 2.Site tripped offline from 05:15 to 09:55 on 07/30 | 1.SR099545 2.SR105330 | SR105330
Ransom | NY | SOL-11157 | 864708 | 861300 | 3408 | 0.3957% | NA |  |  | 1. The site tripped offline at 15:05 on 07/03 due to a utility outage and later came back online at 13:30 on 07/07. 2. The site tripped offline at 15:45 on 07/10 and later came back online at 09:25 on 07/11. It tripped offline again at 16:50 on 07/12 and came back online on 07/14. | 1. SR103988 2. SR104286 | SR104286
Horseheads - Wedge | NY | SOL-11160 | 730633 | 728031 | 2602 | 0.3574% | NA
Otisville - Shoddy Hollow | NY | SOL-11185 | 1135818 | 1131387 | 4431 | 0.3916% | NA |  |  | 1. All the trackers have been stuck mode since 05/14. 2. The site tripped offline at 17:40 on 07/03 due to the recloser being opened and later came back online at 08:20 on 07/05 after the recloser was closed. | 1. SR098693 2. SR104015 | SR104015
Wellsville - Chenunda Creek | NY | SOL-11187 | 621490 | 619787 | 1703 | 0.2748% | NA |  |  | 1. Tracker 27 has been stuck since 07/17, tracker 45 was deviating from 07/17 and was resolved on 07/23, and tracker 41 has been stuck since 07/23. | 1. SR104558
DC: Washington - Essex Condominium | DC | SOL-10036 | 4372 | 5739 | -1367 | -23.82% | 5314 | -942 | -17.73% | 1.Low production/generation due to low irradiance 07/10 , 07/31
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 10048 | 13191 | -3143 | -23.83% | 13677 | -3629 | -26.53% | 1.Inverter 2 has been offline since 03/28, reporting a fault current. 2.The meter power dropped to zero and also lost communication multiple times throughout the month. | 1. SR100622 2.SR100117
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 14836 | 11476 | 3360 | 29.28% | 13669 | 1167 | 8.538%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149
IL: Viola - Goldenrod - (PW) | IL | SOL-11132
IL: Marengo - Grant - (PW) | IL | SOL-11147
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Aug
Generate Capital |  |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  |  | 54974715.6033 | 27424163.826 | 27550551.7773 | 100.5% | 49799707.165 | 5175008.4383 | 10.39% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 25387.875 | 41100.46 | -15712.585 | -38.23% | 38297.31 | -12909.435 | -33.71% | 1.Meter B phase currents dropped to Zero whole month. Need to replace CT | 1.SR102152
K041 | NY | SOL-10357 | 29664.6562 | 33369.58 | -3704.9238 | -11.1% | 28973 | 691.6562 | 2.387%
K043 | NY | SOL-10358 | 37015 | 36588.2 | 426.8 | 1.166% | 6290.855 | 30724.145 | 488.4% | 1. Inverter 3 middle unit(unit 3.2) is producing as expected from 08/01 2.Estimated values are low in AE we have also verified the file which was given by GC | 1. SR103360
K058 | NY | SOL-10360 | 25689.9375 | 26459.76 | -769.8225 | -2.909% | 28466.52 | -2776.5825 | -9.754% | 1.Site was offline from 02/21 due to Phase C fuse was blown and parts were needed | 1. SR097569 ,SR102535 | SR102535
K115 | NY | SOL-10361 | 5371.6562 | 15184.17 | -9812.5138 | -64.62% | 16381.54 | -11009.8838 | -67.21% | 1. 96 optimizers are down for site construction. GenC says EPC is remapping, completion estimated by next week | 1.SR093291
K152 | NY | SOL-10362 | 10972.875 | 11315.42 | -342.545 | -3.027% | 11000 | -27.125 | -0.2466%
K166 | NY | SOL-10363 | 39443.125 | 42852.99 | -3409.865 | -7.957% | 40444.54 | -1001.415 | -2.476%
K206 | NY | SOL-10927 | 23900.0156 | 22143.95 | 1756.0656 | 7.93% | 21657 | 2243.0156 | 10.36%
K251 | NY | SOL-10365 | 25397.0625 | N/A |  |  | 25716.15 | -319.0875 | -1.241% | 1. Weather station stopped communicating on 11/22 at 07:00. 2. Inverter module 1.0.153 12D31EC2-C5 is offline, reporting no comms with power optimizer. | 1.SR093633 2. SR093292 | SR093292
K269 | NY | SOL-10366 | 23964.625 | 27883.37 | -3918.745 | -14.05% | 23034.2 | 930.425 | 4.039% | 1.Inverters producing as expected and expected value and forecasted energy values diffrence.
K273 | NY | SOL-10367 | 15821.375 | N/A |  |  | 31080 | -15258.625 | -49.09% | 1. 26 optimizers are down for roof repair. 2. Weather station stopped communicating since 06/14/24. 3. Inverter 2 middle unit (unit 2.1) was offline on multiple days and reporting low voltage 4. Meter was reading inaccurate Valuses for whole month likely bad CT. | 1. SR093294 2. SR086842 3. SR104856 4. SR103245 | SR086842 | SR104856 | SR103245
K287 | NY | SOL-10919 | 20571.75 | 17766.42 | 2805.33 | 15.79% | 19892 | 679.75 | 3.417% | 1. Actual vs expected delta is showing 16% due to expected energy recording low possibly due to data glitch (similar event observe last years).
K298 | NY | SOL-10368 | 22554.125 | 23679.06 | -1124.935 | -4.751% | 22900 | -345.875 | -1.51%
K335 | NY | SOL-10370 | 23670.5625 | 26153.44 | -2482.8775 | -9.494% | 25730 | -2059.4375 | -8.004% | 1. The estimated values in AlsoEnergy appeared lower, and there was a discrepancy between the values shown in the Configuration and Analysis sections.
K345 | NY | SOL-10920 | 27708.4062 | 16063.37 | 11645.0362 | 72.49% | 26340 | 1368.4062 | 5.195% | 1. Inverter 3 is underproducing due to unit(7E9C82CA) underproducing from 13:30 on 06/20 and reporting "external fan" fault. 2. Actual vs expected delta is showing 72% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1.SR103259
K445 | NY | SOL-10373 | 22595.3437 | 24700.37 | -2105.0263 | -8.522% | 21831.14 | 764.2037 | 3.501%
K495 | NY | SOL-10374 | 92612.7795 | 95773.44 | -3160.6605 | -3.3% | 96093.38 | -3480.6005 | -3.622% | 1.Inverter 11 (left unit) was offline since 04/18, reporting a "DC Isolation Fault." During troubleshooting, it was discovered that following a firmware update, the inverter no longer displayed fault codes and continued to fail to produce power. SolarEdge technical support was contacted, and a callback was received. Case number 5713468 was created. | 1.SR101786 , SR102902 | SR102902
M020 | NY | SOL-10380 | 24930.8438 | 25352.02 | -421.1763 | -1.661% | 25211 | -280.1562 | -1.111%
M092 | NY | SOL-10383 | 24807.1875 | 26333.54 | -1526.3525 | -5.796% | 23750.38 | 1056.8075 | 4.45%
M143 | NY | SOL-10384 | 26852.375 | 32610.05 | -5757.675 | -17.66% | 25919.28 | 933.095 | 3.6% | 1. Inverter 3 left unit is having multiple trippings since 06/08 on high irradiance day. | 1. SR102672
M144 | NY | SOL-10385 | 40468.5625 | 44100.43 | -3631.8675 | -8.235% | 43639.62 | -3171.0575 | -7.266%
M167 | NY | SOL-10386 | 29635.5938 | 22915.6 | 6719.9938 | 29.32% | 31794.96 | -2159.3662 | -6.792% | 1. Actual vs expected delta is showing 29% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
M188 | NY | SOL-10387 | 20889.4062 | 21532.78 | -643.3737 | -2.988% | 22453.19 | -1563.7837 | -6.965%
EMHC | NY | SOL-10351 | 9480.9922 | 6968.195 | 2512.7972 | 36.06% | 10404.48 | -923.4878 | -8.876% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline 2. Actual vs expected delta is showing 36% due to expected energy recording low possibly due to data glitch (similar event observe last years). | 1. SR093236
Q008 | NY | SOL-10397 | 4112.8746 | 4516.582 | -403.7074 | -8.938% | 31495 | -27382.1254 | -86.94% | 1.Site stopped communicating from 03/25. On 03/27 Technician stated that main breaker tripped and malfunctioning. Site was back online on 08/28 at 16:00 | 1.SR102532 , SR102532 | SR102532
Q018 | NY | SOL-10398 | 21744.125 | 23671.38 | -1927.255 | -8.142% | 20045.95 | 1698.175 | 8.471%
Q021 | NY | SOL-10399 | 17483.25 | 17280.21 | 203.04 | 1.175% | 16869.41 | 613.84 | 3.639%
Q025 | NY | SOL-10400 | 29830.5625 | 29222.12 | 608.4425 | 2.082% | 14697 | 15133.5625 | 103% | 1. Actual vs Forcasted delta is showing 103% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Q074 | NY | SOL-10402 | 19681.4375 | 19392.61 | 288.8275 | 1.489% | 19027.01 | 654.4275 | 3.439%
Q115 | NY | SOL-10872 | 25297.8125 | 27092.84 | -1795.0275 | -6.625% | 25304.7 | -6.8875 | -0.02722%
Q139 | NY | SOL-10403 | 15065.7812 | 16401.54 | -1335.7588 | -8.144% | 15998 | -932.2188 | -5.827% | 1.Some optimizers with production issues 1264FFBB-30 - Half production ,12639DA9-BB - Half production | 1. SR088282
Q157 | NY | SOL-10404 | 23352.1875 | 30752.33 | -7400.1425 | -24.06% | 28355.47 | -5003.2825 | -17.64% | 1.Inverter 1 started late for production since 08/01. On 08/11 Technician with SolarEdge support troubleshot inverter 1 but it remained offline. Inverter is now being RMA'd | 1.SR105502
Q192 | NY | SOL-10406 | 41920.25 | 46029.85 | -4109.6 | -8.928% | 41191.2 | 729.05 | 1.77%
Q210 | NY | SOL-10407 | 33990.125 | 34065.25 | -75.125 | -0.2205% | 34388 | -397.875 | -1.157%
Q229 | NY | SOL-10408 | 14682.6083 | 16629.88 | -1947.2717 | -11.71% | 14688.96 | -6.3517 | -0.04324% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1. SR088813
Q231 | NY | SOL-10870 | 52444.25 | 58605.91 | -6161.66 | -10.51% | 53954 | -1509.75 | -2.798% | 1.Inverter 2, Unit 2.2 tripped offline on 08/01 at 15:30 EDT reporting low voltage and error status in SE. On 08/20 technician after swapping and pairing optimizer inverter 2 is producing as expected. Solaredge has also rmad an optimizer. And again Inverter 2 unit 2.2 is being offline during morning hours and started producing at mid-day from 08/25 | 1.SR105544
Q405 | NY | SOL-10409 | 62369.25 | 69200.43 | -6831.18 | -9.872% | 61404.24 | 965.01 | 1.572% | 1.4 Inverter modules are offline. Will investigate next time on site. Module 1.0.64 Module 4.0.39 , 3.0.20 ,1.0.64 | 1.SR093324
Q435 | NY | SOL-10923 | 53191.585 | 63905.8 | -10714.215 | -16.77% | 75413 | -22221.415 | -29.47% | 1. The meter has been capturing only 222 kW at peak, which suggests that two inverters may be offline. As there is no communication with the inverters, we are currently unable to confirm which specific units are affected. | 1. SR107329
Q485 | NY | SOL-10869 | 73485.0625 | 58334.67 | 15150.3925 | 25.97% | 71188.38 | 2296.6825 | 3.226% | 1.Inverter 1 left unit tripped offline at 14:00 on 08/12. It came back online on 08/18 2.Meter screen is blinking on and off and only showing the Elkor main screen. Meter is recording and reporting correctly from 08/13 . No action to be taken 3. Actual vs expected delta is showing 26% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1.SR106170 2.SR106173 | SR106173
Q490 | NY | SOL-10411 | 53147.5 | N/A |  |  | 53310.72 | -163.22 | -0.3062% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1.SR093326
Q620 | NY | SOL-10867 | 81466.9698 | 82633.92 | -1166.9502 | -1.412% | 75574.26 | 5892.7098 | 7.797%
QMOA | NY | SOL-10415 | 6866.2 |  |  |  | 6860.454 | 5.746 | 0.08376%
X024 | NY | SOL-10419 | 31611.1562 | 31815.6 | -204.4438 | -0.6426% | 28668 | 2943.1562 | 10.27%
X026 | NY | SOL-10420 | 27837.3 | 26063.156 | 1774.144 | 6.807% | 39147 | -11309.7 | -28.89% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1. SR095662
X090 | NY | SOL-10925 | 23964.406 | 21033.108 | 2931.298 | 13.94% | 22204 | 1760.406 | 7.928%
X117 | NY | SOL-10422 | 20148.2 | 22042.705 | -1894.505 | -8.595% | 20981 | -832.8 | -3.969%
X125 | NY | SOL-10423 | 36752.25 | 37712.455 | -960.205 | -2.546% | 34285 | 2467.25 | 7.196%
X134 | NY | SOL-10424 | 35656.938 | 7290.89 | 28366.048 | 389.1% | 33773 | 1883.938 | 5.578% | 1. Weather Station is showing erroneous (0 w/m^2) values at mid day from 07/20 at 09:30. | 1.SR105932
X135 | NY | SOL-10425 | 28076.75 | 34094.176 | -6017.426 | -17.65% | 26680 | 1396.75 | 5.235% | 1. Inverter 1 unit 1.2 is derating by 30kW since 07/15. On 08/08 Technicain has replaced the faulty external fan in inverter unit 1.2 and it producing normally | 1.SR104744
X139 JHS 222 | NY | SOL-10426 | 42297.89 | 47616.439 | -5318.549 | -11.17% | 43069 | -771.11 | -1.79% | 1. Inverter 1 right unit (Unit 1.7) is still experiencing multiple tripping events. Entire inverter 1 offline from 08/27 at 2:00 | 1.SR105933
X140 | NY | SOL-10926 | 24351.8125 | 21025.03 | 3326.7825 | 15.82% | 22757 | 1594.8125 | 7.008% | 1. Inverter 2 unit 2 tripped offline at 14:45 on 08/01 and reporting grid voltage. It producing normally from 08/11 2.Inverter 3 unit 3.3 tripped offline at 14:45 on 08/21 and reporting "Ground Current - RCD". It came back online at 11:15 on 08/22 and also Unit 3.3 is experiencing late starts every day since 08/27 . Followed up with SE | 1.SR105525 2.SR106721 | SR106721
X166 | NY | SOL-10427 | 26016.5 | 25940.26 | 76.24 | 0.2939% | 25236 | 780.5 | 3.093%
Murphy | MN | SOL-10094 | 945100 | 994462.4 | -49362.4 | -4.964% | 991358.7 | -46258.7 | -4.666% | 1.Inverter 1 is producing at its half production through out the month. 1 IGBT needs replacement to get inverter fully functional. 2.Inverter 5 tripped offline from 08/27 at 12:15 and it came back online at 14:00 on 08/29 | 1.SR104403 2.SR107039 | SR107039
Terning | MN | SOL-10093 | 967929.3133 | 1034158 | -66228.6867 | -6.404% | 973544.6 | -5615.2867 | -0.5768%
Boas Road 04 | NY | SOL-10908 | 0 | 563.26 | -563.26 | -100% | 366693.531 | -366693.531 | -100% | 1.Inverter 2 is derating by 100kW during the peak hours, Possibly due to increase in Heatsink T temperature. On 08/14 inverters Fans verified operating normally 2. Meter was not communicated for whole month. | 1.SR105772 2. SR098641 | SR098641
Kelly Bridge Farm | NY | SOL-10911 | 279986 | 291537.2 | -11551.2 | -3.962% | 367668.78 | -87682.78 | -23.85% | 1. Site lost communication from 08/22 to end of the month. 2.Meter stopped communicating from 14:05 on 03/16 till date. | 1. SR106726 2.SR098641 | SR098641
Pool Brook Road | NY | SOL-10909 | 314912 | 314914 | -2 | -0.0006351% | 367442.207 | -52530.207 | -14.3% | 1. Inverter 8 was back online at 10:40 on 08/11 2.Inverter 28 tripped offline at 13:55 on 08/16 and was back online at 08/21. 3.All inverters were experiencing multiple trippings due to fluctuatins in voltages since 07/29 and was resolved | 1.SR104724 2.SR106386 3.SR105002 | SR106386 | SR105002
Sackett Lake | NY | SOL-10910 | 269810 | 0 | 269810 |  | 368427.307 | -98617.307 | -26.77% | 1. Meter was not communicated from 20:40 on 8/21 to end of the month. 2.Weather station lost communication from 07/15 | 1. SR106732 2.SR106732 | SR106732
Burritt Road | NY | SOL-10913 | 398500 | 430529.9 | -32029.9 | -7.44% | 378656.343 | 19843.657 | 5.241% | 1.Site tripped offline at 13:10 and was back online at 13:40 on 08/05. | 1.SR105660
Villa Roma 1 | NY | SOL-10914 | 347648 | 235.4 | 347412.6 | 147584% | 332963.716 | 14684.284 | 4.41% | 1.Expected energy values are reporting very low. Created a case #66639 with GPM, As per GPM the BOM has been frozen from 02/27. | 1.SR099403
Villa Roma 2 | NY | SOL-10915 | 328208 | 363593.2 | -35385.2 | -9.732% | 323112.718 | 5095.282 | 1.577%
Washington 1 | NY | SOL-10912 | 363420 | 429002.3 | -65582.3 | -15.29% | 374337.905 | -10917.905 | -2.917% | 1.Inverters 2 tripped offline at 06:15 on 08/01 and is reporting "Ph. T Blower Fault"and was back online at 10:25 on 04/08,again tripped offline at 06:15 on 08/05 and was back online at 10:35 on 08/06. | 1.SR105475
Washington 3 | NY | SOL-10828 | 407946 | 1087185.71 | -679239.71 | -62.48% | 457165.092 | -49219.092 | -10.77% | 1. POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1.SR093024
Washington 4 | NY | SOL-10829 | 475165 | 509908.8 | -34743.8 | -6.814% | 458187.626 | 16977.374 | 3.705%
Big Tree | NY | SOL-10966 | 406110 | 405140 | 970 | 0.2394% | 378199.1 | 27910.9 | 7.38%
Canoga | NY | SOL-10965 | 1069950 | N/A |  |  | 0 | 1069950 |  | 1.Inverter 2 was offline at 06:25 on 08/22 and was back online at 11:30 on 08/22 2.2.Inverter 1 was derating by 60kw during peak hours throughout the month. | 1.SR106735 2.SR105776 | SR105776
County Route 84 | NY | SOL-10967 | 1025200 | 944680 | 80520 | 8.524% | 965891.884 | 59308.116 | 6.14% | 1.Inverter 1 was underperforming by 100kw , inverter 2 by 60kw and inverter 3 by 50kw during peak hours through out the month | 1.SR105777
Donati | NY | SOL-10968 | 351070 | N/A |  |  | 486664.691 | -135594.691 | -27.86% | 1. Trackers A01,5-7,10: B17-23,D19-23,29: F19-23,27,33:G13-14 were stuck. Further troubleshooting is required | 1.SR095253,SR098877 | SR098877
Henrietta | NY | SOL-10972 | 1061840 | 1060120 | 1720 | 0.1622% | 1004776.373 | 57063.627 | 5.679% | 1.Inverter 1 was underperforming by 100kw, inverter 2 by 50kw, inverter 3 by 120kw and was back to normal on 08/21. 2.Trackers 6,14 15 were struck throughout the month. | 1.SR105778 2.SR106622 | SR106622
NY 70 | NY | SOL-10970 | 1145390 | 1142500 | 2890 | 0.253% | 1091441.21 | 53948.79 | 4.943% | 1.Site tripped offline at 03:15 on 08/31 and meter voltages were dropped to 0 2.Inverters 3 &4 were experiencing multiple trippings from 11:00 on 08/27 and were back to normal on 08/28. 3.44 trackers were currently struck . Further troubleshooting required. 4.Inverter 1 was derating by 70kw and inverter 3 is derating by 120kw due to inverter internal temperature throughout the month. | 1.SR107254 2.SR107042 3.SR106503 4.SR1057754 | SR107042 | SR106503 | SR105775
Reid | NY | SOL-10991 | 892282.9984 | 914463.5 | -22180.5016 | -2.426% | 880052 | 12230.9984 | 1.39% | 1.Inverter 32 was tripped offline at 14:15 on 08/09 and back at 08:45 on 08/13, again tripped offline at 14:15 on 08/18 and was back at 11:00 on 08/20 ,again tripped offline at 12:45pm on 08/31 reporting "Grid voltage out of range" . 2.Inverter 36 tripped offline at 13:30 on 08/28 and reporting "Bus Imbalance - Protect0070". 3. Inverter 9 was offline on multiple days of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim". 4. Inverter 29 tripped offline at 14:15 on 08/15 and was back online at 11:00 on 08/20 ,again tripped offline at 01:50pm on 08/22. reporting "Grid Phase Voltage Out of Range - GridV.OutLim" . 5.Inverters 28 was frequently trippping on and off and was completely tripped offline at 01:30pm on 08/21 reporting"Grid Phase Voltage Out of Range - GridV.OutL" 6.Inverter 23 tripped offline at 14:45 on 08/11 and reporting Grid Line Voltage Out of Range - GridV.OutLim and was back online at 08:45 on 08/13 7. Inverter 5 tripped offline at 14:00 on 08/08 and reporting "Grid Line Voltage Out of Range - GridV.OutLim"and was back online at 13:15 on 08/13 8.Inverter 30 was tripped offline at 14:15 on 08/01 was back online at 08:45 on 08/13, again tripped offline at 11:45 on 08/15 and was back online at 11:00 on 08/20. 9.Inverter 3 powerhead was swapped and issue was resolved on 08/13.From then on,inverter was back online and producing. | 1.SR107253,SR105960,SR106340 2.SR107147 3.SR106786,SR105526,SR106340 4.SR106755,SR106340 5.SR106662,SR106271 6.SR106031 7.SR105923 8.SR106340 9.SR105423 | SR105960 | SR106340 | SR107147 | SR106786 | SR105526 | SR106340 | SR106755 | SR106340 | SR106662 | SR106271 | SR106031 | SR105923 | SR106340 | SR105423
Sangolqui | NY | SOL-10975 | 516940 | 464570 | 52370 | 11.27% | 474404.415 | 42535.585 | 8.966% | 1. Inverter 2 was offline from 08:45 to 11:30 on 08/21. | 1. SR105799
State Highway 17B | NY | SOL-10988 | 895960 | [6 empty] | 1. The site tripped offline at 15:50 on 08/13 and came back online at 09:30 on 08/14. | 1. SR106209
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 983561.84 | -983561.84 | -100% | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required. On 07/02 technician was after pulling event files from the SEL for analysis. The site remains offline. | 1. SR099347, SR101820, SR103655 | SR101820 | SR103655
West Creek | NY | SOL-10995 | 961630 | 793500 | 168130 | 21.19% | 976026.254 | -14396.254 | -1.475% | 1. The site went offline at 02:00 on 08/08 and came back online at 10:25 on 08/10. 2. The site went offline at 02:00 on 08/12 and came back online at 09:50 on 08/13. 3. The site went offline at 02:00 on 08/26 and came back online at 08:50 on 08/27. It went offline again at 16:50 on 08/28 and has remained offline since then. | 1. SR105915 2. SR106037 3. SR106926 | SR106037 | SR106926
Wildflower | NY | SOL-10982 | 877224 | 874959 | 2265 | 0.2589% | 939540.5 | -62316.5 | -6.633% | 1. Inverter 1 is derating by 140 kW and Inverter 4 by 70 kW during peak hours throughout the month. 2. Inverters 1 and 2 were taken offline from 09:45 to 12:45 on 08/01 while a technician was on site working on CB11. Both the positive and negative feeder 11 wires were relocated to the spare terminal on the DC switch due to damage at the original terminal. | 1. SR105775 2. SR104674 | SR104674
Glen Mary 1 | NY | SOL-10993 | 971890 | 968460 | 3430 | 0.3542% | 977485.509 | -5595.509 | -0.5724% | 1. The site tripped offline at 18:00 on 08/03 and came back online at 16:20 on 08/05. | 1. SR105048
Glen Mary 2 | NY | SOL-10994 | 423580 | 256240 | 167340 | 65.31% | 416453.558 | 7126.442 | 1.711% | 1. The site tripped offline at 18:00 on 08/03 and came back online at 16:20 on 08/05. 2. The meter is reporting erroneous values for both power and current. 3.The POA Pyranometer Up has been reporting 0 W/m² since 08/18 | 1. SR105049 2. SR106574 3.SR105649 | SR106574 | SR105649
Telegraph 1 | NY | SOL-11003 | 718090 | N/A |  |  | 685999.967 | 32090.033 | 4.678% | 1. The site was offline from 11:05 to 13:30 on 08/13. 2. The site was offline from 07:20 to 10:50 and from 16:15 to 17:55 on 08/26. 3. Inverter 1 has been derating at 1343 kW since 08/17. | 1. SR106194 2. SR106923 3. SR107234 | SR106923 | SR107234
Telegraph 2 | NY | SOL-11004 | 352930 | N/A |  |  | 357075.716 | -4145.716 | -1.161% | 1. The site was offline from 07:20 to 10:50 and from 16:15 to 17:55 on 08/26. 2. Inverter 1 has been derating at 1343 kW since 08/17. 3. The site was offline from 11:05 to 13:30 on 08/13. | 1. SR106924 2. SR107236 3. SR106195 | SR107236 | SR106195
Cafferty Hill | NY | SOL-10996 | 1036120 | 1073271.7 | -37151.7 | -3.462% | 938020.137 | 98099.863 | 10.46%
Dunkleman | NY | SOL-11008 | 1233230 | 1230210 | 3020 | 0.2455% | 1151573.604 | 81656.396 | 7.091%
Route 19 1 | NY | SOL-11001 | 477750 | 474670 | 3080 | 0.6489% | 470708.472 | 7041.528 | 1.496% | 1. The site was offline from 11:05 to 13:30 on 08/13. 2. The inverter was offline on 08/25 and came back online at 15:05 on the same day, but strings 4 and 5 remain offline, and 2 Y-connectors along with repair wires need to be replaced. | 1. SR106192 2. SR106797, SR107188 | SR106797 | SR107188
Route 19 2 | NY | SOL-11002 | 1221980 | 1218200 | 3780 | 0.3103% | 1157576.844 | 64403.156 | 5.564% | 1. The site was offline from 11:05 to 13:30 on 08/13. 2. The site was offline from 07:20 to 17:55 on 08/26. | 1. SR106193 2. SR106920 | SR106920
Yellow Mills 1 | NY | SOL-11006 | 444762 | 442702 | 2060 | 0.4653% | 398351.768 | 46410.232 | 11.65%
Yellow Mills 2 | NY | SOL-11005 | 439886 | N/A |  |  | 413553.443 | 26332.557 | 6.367% | 1. The site tripped offline at 18:35 on 08/05 and came back online on 08/06. | 1. SR105728
Yellow Mills 3 | NY | SOL-11007 | 417387 | 415519 | 1868 | 0.4496% | 393360.933 | 24026.067 | 6.108%
Catskill | NY | SOL-11021 | 444125 |  |  |  | 723755.754 | -279630.754 | -38.64% | 1. Inverters 1 and 2 were offline from 07/14. Inverter 2 came back online at 14:40 on 08/08, and Inverter 1 came back online at 11:30 on 08/12. 2. The site went offline at 15:40 on 08/06 and came back online at 14:10 on 08/08. 3. The site tripped offline at 09:55 on 08/21 and came back online at 10:00 on 08/22. 4. Inverter 1 has been offline since 08/25. 5. The site tripped offline at 10:45 on 08/26 and came back online at 14:55 on the same day. | 1. SR104383 2. SR105857 3. SR106643 4. SR106843 5. SR106934 | SR105857 | SR106643 | SR106843 | SR106934
Eddy Ridge | NY | SOL-11054 | 545135 | 543196 | 1939 | 0.357% | 569140 | -24005 | -4.218% | 1. Trackers 1 through 49 have been stuck since 07/28. | 1. SR105180
Ridgeway #1 | NY | SOL-11018 | 1299305 | 1294543 | 4762 | 0.3679% | 1207231.49 | 92073.51 | 7.627% | 1. Inverter 2 started production late on 08/01, 08/02, 08/04, 08/05, 08/06, and 08/07 due to a ground fault. 2. Inverter 2 was offline from 14:50 on 08/25 and came back online at 09:35 on 08/27. 3. Inverter 1 tripped offline at 15:00 on 08/28 due to "Overall Work STOP" and came back online at 17:30 on 08/29. | 1. SR105779 2. SR106925, SR107064 3. SR107142 | SR106925 | SR107064 | SR107142
Rivard 1 | NY | SOL-11011 | 1066472.45 | 1106229 | -39756.55 | -3.594% | 935669.4 | 130803.05 | 13.98%
Rivard 2 | NY | SOL-11012 | 1031069.239 | 1013938 | 17131.239 | 1.69% | 899150.6 | 131918.639 | 14.67% | 1. Trackers 156, 158, 159, and 161 have been stuck since 08/09, and tracker 16 has been stuck since 08/18. | 1. SR105938
Ridgeway #2 | NY | SOL-11027 | 664930 | 662501 | 2429 | 0.3666% | 615124.08 | 49805.92 | 8.097%
Spencer | NY | SOL-11017 | 1330141 | 1327536 | 2605 | 0.1962% | 1194000 | 136141 | 11.4% | 1. Tracker 169 is stuck from 07/17 | 1. SR101152
Reisender | NY | SOL-10886 | 404190 | 404110 | 80 | 0.0198% | 375809.64 | 28380.36 | 7.552%
Finney | NY | SOL-10999 | 982830 | 981420 | 1410 | 0.1437% | 1213585.291 | -230755.291 | -19.01% | 1. The site tripped offline at 14:10 on 07/31 due to the SEL relay being in an open state. The relay was closed at 16:10 on 07/31, but the site remained offline and later came back online at 12:05 on 08/01. 2. The site went offline at 09:30 on 08/18 and later came back online at 15:00 on 08/27. | 1. SR105450 2. SR106428, SR106658 | SR106428 | SR106658
Davis Solar | NY | SOL-10958 | 415510 | 442179.7 | -26669.7 | -6.031% | 433878 | -18368 | -4.233% | 1. Inverter tripped offline at 14:10 on 08/03 due to "STOP" and came back online at 17:10 on the same day after a remote reset. | 1. SR104691
Genesee | NY | SOL-10951 | 812550.8 | 480122.63 | 332428.17 | 69.24% | 925244.37 | -112693.57 | -12.18% | 1. Trackers 23, 24, 33, 37, and 72 through 151 have been stuck since 06/02 | 1. SR102328
Landau I | NY | SOL-10891 | 428570 | N/A |  |  | 408213.173 | 20356.827 | 4.987%
Landau II | NY | SOL-10895 | 730570 | N/A |  |  | N/A |  |  | 1. Inverter 2 tripped offline at 09:40 on 08/01 due to a ground fault and came back online at 12:35 by remote reset; tripped offline again at 10:45 on 08/02 due to a ground fault and came back online at 16:30 by remote reset; tripped offline at 08:25 on 08/03 and came back online at 10:40 by remote reset; tripped offline at 12:45 on 08/03 due to the AC breaker being in the open state and came back online at 15:35; tripped offline at 09:40 on 08/06 due to the AC breaker being in the open state and came back online at 12:40 by remote reset; and tripped offline again at 09:20 on 08/07 due to the AC breaker being in the open state and came back online at 15:15 by remote reset. 2. Inverter 1 tripped offline at 16:20 on 08/22 due to the AC breaker being in the open state and later came back online at 18:30 by remote reset. | 1. SR105474 2. SR106767 | SR106767
New Beginnings | NY | SOL-10890 | 428040 | 428030 | 10 | 0.002336% | 396674.288 | 31365.712 | 7.907%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 1070595 | 1105629.977 |  | 0% | 1113535.59 | -42940.59 | -3.856% | 1. The site tripped offline at 18:30 on 08/23 due to the SEL relay being open and later came back online at 13:05 on 08/29. | 1. SR106794
Brodhead Solar, LLC | NY | SOL-10899 | 451438 | 465571.518 | -14133.518 | -3.036% | 489955.64 | -38517.64 | -7.861% | 1. NCU1 tracker 10 was stuck from 07/07 and resumed tracking from 08/18. | 1. SR104075
Svenski | NY | SOL-10894 | 427100 | N/A |  |  | 413086.075 | 14013.925 | 3.392%
Bantam | NY | SOL-10986 | 58580 | 466200 | -407620 | -87.43% | 1170207.33 | -1111627.33 | -94.99% | 1. Inverter 1 was offline from 16:40 on 05/26 due to the AC breaker being in an "Open" state and came back online at 13:00 on 08/27 after the inverter was re-energized. 2. tracker NCU3 1041 was stuck on 08/12 and later resumed tracking from 08/21 and tracker NCU4 1056 was stuck from 08/15. | 1. SR105283 2. SR106058 | SR106058
Bogart | NY | SOL-10887 | 329160 | 327850 | 1310 | 0.3996% | 389805.55 | -60645.55 | -15.56% | 1. The inverter was offline from 06/28 because the AC breaker switch was in the "Open" state and later came back online at 15:10 on 08/06. | 1. SR103685
Dubois | NY | SOL-10892 | 129520 | 129539.39 | -19.39 | -0.01497% | N/A |  |  | 1. The site has been offline since 06:20 on 08/10 due to a transformer failure. | 1. SR105964, SR106921 | SR106921
Salt Point | NY | SOL-10888 | 407890 | 407890 | 0 | 0% | 453414.964 | -45524.964 | -10.04% | 1. The site went offline at 19:03 on 08/04 and was brought back online at 08:12 on 08/05 via a remote reset. It experienced further outages from 18:44 on 08/07 to 09:45 on 08/08, then again from 19:00 on 08/08 to 11:45 on 08/09, and once more from 19:00 on 08/09 to 07:00 on 08/10. Another outage occurred from 19:30 on 08/17 to 12:30 on 08/18, followed by one from 10:25 on 08/18 to 02:10 on 08/19. The site was also offline from 11:30 to 15:00 on 08/25, and again from 10:30 to 16:20 on 08/26. 2. Inverter 1, module 4 went offline at 11:50 on 08/11 and later came back online at 12:25 on 08/13. Again module 4 was offline from 09:30 on 08/21 to 16:15 on 08/26. 3. Inverter 1, module 2 went offline at 15:40 on 08/12 and later came back online at 12:25 on 08/13. | 1. SR105637, SR106985, SR105305 2. SR106002 3. SR106164 | SR106985 | SR105305 | SR106002 | SR106164
Wheatland 2A | NY | SOL-10971 | 1060290 | 1058220 | 2070 | 0.1956% | 1030493.057 | 29796.943 | 2.892% | 1. Fourteen trackers have been stuck since 04/11: NCU1 SPC 111, 112, 118, 205, 305, 307, 310, 311, and NCU2 SPC 125, 126, 136, 242, 338, 341. Actuator replacement is required. | 1. SR099686
Wheatland 2B | NY | SOL-10961 | 1068130 | 1066040 | 2090 | 0.1961% | 1019707.76 | 48422.24 | 4.749% | 1. Fifteen trackers have been stuck since 03/21: NCU1 SPC 101, 206, 218, 314, and NCU2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, 343. | 1. SR098860
Brickchurch | NY | SOL-10889 | 0 | 0 | 0 |  | 474590.737 | -474590.737 | -100% | 1. Nineteen trackers have been stuck throughout the month: NCU1 SPC 115–127 and NCU2 SPC 216, 220, 230, 240, 253, 329, and 338. Additional troubleshooting is required as the terminal blocks need to be replaced. 2. Inverter 1 offline from 07/01 is reporting the AC breaker state as OPEN. Inverter 1 to be RMA'ed and remain offline through out the month. | 1. SR097454 2. SR106501, SR103824 | SR106501 | SR103824
McCarthy Solar | NY | SOL-10992 | 52900 | 0 | 52900 |  | 411227 | -358327 | -87.14% | 1. Site was offline at 17:35 on 07/18. Site came back online at 11:35 on 08/28 | 1.SR104633
Costanza | NY | SOL-10907 | 398520 | 398745.4 | -225.4 | -0.05653% | 404374.041 | -5854.041 | -1.448% | 1.Inverter tripped offline at 17:06 on 08/02 and it came back online at 08:30 on 08/04 2.Site tripped offline from 13:35 to 15:00 on 08/13. And again tripped offline from 08/14 at 19:00 and came back online at 15:53 on 08/14 3.Site tripped offline from 06:27 to 10:09 on 08/18 4. Site was taken offline from 09:30 to 14:26 on 08/19 due to utility to perform some emergency repair works. 5.Inverter tripped offline from 09:30 to 13:29 on 08/27 | 1.SR105543 2.SR106211 3.SR106418 4.SR106495 5. SR107013 | SR106211 | SR106418 | SR106495 | SR107013
Lockenhurst Pond | NY | SOL-11000 | 473563 | 531616.3 | -58053.3 | -10.92% | 491418 | -17855 | -3.633% | 1.Inverter 1 tripped offline on 08/22 at 17:00 and reporting "Error" and it came back online at 10:00 on 08/23, and also CB 8 offline from ground fault from 08/23 and it came back online at 11:30 on 08/27 | 1.SR106766
Drinkwater | NY | SOL-10896 | 472030 | 470980 | 1050 | 0.2229% | 425241.187 | 46788.813 | 11%
Altamont | NY | SOL-11085 | 902582 | 934730.4 | -32148.4 | -3.439% | 675235.9 | 227346.1 | 33.67%
Krumkill North | NY | SOL-11086 | 753529 | 949033.7 | -195504.7 | -20.6% | 791744.9 | -38215.9 | -4.827% | 1.Site offline from 08:30 on 08/10 and it came back online at 17:30 on 08/12 | 1.SR105304
Krumkill South | NY | SOL-11087 | 632808 | 746375.2 | -113567.2 | -15.22% | 620704.3 | 12103.7 | 1.95% | 1.Site offline from 08:30 on 08/10 and it came back online at 17:30 on 08/12 | 1. SR105307
X092 | NY | SOL-11189 | 21515.4 | 21675.78 | -160.38 | -0.7399% | 20398 | 1117.4 | 5.478%
X093 | NY | SOL-10932 | 16320.0607 | 15183.08 | 1136.9807 | 7.488% | 14577 | 1743.0607 | 11.96%
X095 | NY | SOL-10929 | 21548.5234 | 20519.35 | 1029.1734 | 5.016% | 19827 | 1721.5234 | 8.683%
X181 | NY | SOL-10428 | 38662.2344 | 34110.07 | 4552.1644 | 13.35% | 36480 | 2182.2344 | 5.982% | 1.- Inverter 2 unit 1 (7E9B4E78) tripped offline at 14:15 on 08/06 and reporting "Grid voltage". On 08/11 Inveretr AC fuse replaced, inverter is producing normally. | 1.SR105865
X415 | NY | SOL-10429 | 25028.6953 | 21501.05 | 3527.6453 | 16.41% | 21338 | 3690.6953 | 17.3%
K198 | NY | SOL-10930 | 18123.5547 | 17490.82 | 632.7347 | 3.618% | 16970 | 1153.5547 | 6.798%
K203 | NY | SOL-11190 | 23166.5 | 20780.64 | 2385.86 | 11.48% | 22817 | 349.5 | 1.532%
K213 | NY | SOL-11191 | 26129.5 | 27518.5 | -1389 | -5.048% | 23876 | 2253.5 | 9.438%
K217 | NY | SOL-10933 | 14145.7891 | 13313.86 | 831.9291 | 6.249% | 12983 | 1162.7891 | 8.956%
K307 | NY | SOL-10876 | 29099.3281 | 29912.22 | -812.8919 | -2.718% | 27002 | 2097.3281 | 7.767%
K610 | NY | SOL-11158 | 24809.1 | 33741.06 | -8931.96 | -26.47% | 31771 | -6961.9 | -21.91% | 1. Inverter 2 (as per SE Inverter 1) — Units 1.1 and 1.2 tripped offline at 12:00, and Unit 1.3 tripped offline at 16:15 on 06/18. The inverter has remained offline and SolarEdge has rmad the center unit. | 1. SR103141
M025 | NY | SOL-10392 | 24718.7812 | 30789.33 | -6070.5488 | -19.72% | 27850 | -3131.2188 | -11.24% | 1. Inverter 1 On 06/30 at 14:15, Inverter 1 tripped offline. Parts are being RMAd, including Inverter 1 Unit 1.4. On 08/14 at 13:15, Inverter 1 Unit 1.4 tripped offline again. On 08/21, the inverter was producing normally. On 08/26 at 14:30, Inverter 1 tripped offline once more, reporting "3 Phase Possible Arc Detection". On 08/27, the inverter was reset, and all powerheads resumed normal production. 2.Inverter 3 center unit 3.1 tripped offline at 14:00 on 08/09. On 08/11 terminated DC homeruns and inverter is producing normally. Inverter 3 center 3.1 unit tripped offline at 13:00 on 08/24 and reporting "3 Phase Possible Arc Detection" | 1. SR103710 2.SR103871 | SR103871
M028 | NY | SOL-10381 | 24147.6953 | 22986.88 | 1160.8153 | 5.05% | 21408 | 2739.6953 | 12.8%
Q030 | NY | SOL-10878 | 28121.2031 | 27692.87 | 428.3331 | 1.547% | 25556 | 2565.2031 | 10.04%
Q130 | NY | SOL-10877 | 15751.1484 | 14699.77 | 1051.3784 | 7.152% | 14803.11 | 948.0384 | 6.404%
Q196 | NY | SOL-10879 | 20805.4828 | 21379.83 | -574.3472 | -2.686% | 19108 | 1697.4828 | 8.884%
Q220 | NY | SOL-10873 | 24446 | 28043.91 | -3597.91 | -12.83% | 21931 | 2515 | 11.47% | 1. The inverters are experiencing minor shading. | 1.SR103361
Q205 | NY | SOL-10922 | 26670.4688 | 34551.76 | -7881.2913 | -22.81% | 26035 | 635.4688 | 2.441% | 1.Inverter 2, Unit 2.1 did not start for production on 08/19. | 1.SR106530
Q400 | NY | SOL-10871 | 27564.7188 | N/A |  |  | 42213 | -14648.2812 | -34.7% | 1.Inverter 3 and unit 3.1 tripped offline at 13:45 on 06/29 and has been offline since then. 2.Inverter 1 unit 1.1 tripped offline at 16:30 on 08/06. Inverter 1 unit 1.2 tripped offline at 12:45 on 08/09. On 08/22 inveretr 1 center and left unit. Units were reenergized and have been operating normally. 3.Inveretr 2 center is offline from 08/14. On 08/22 Inveretr 2 left unit swapped optimizer and isolated string 2 to reenergize. Center unit reenergized. 4. Inverter 2 tripped offline at 13:15 and reporting "Fault". On 08/22 technician swapped optimizers and reenergized inverter 1 left and center units, inverter 2 left and center units, and inverter 3 center unit. Strings were isolated in inverter 2 left unit and inverter 3 left unit. | 1.SR103641 2.SR105731 3. SR105732 4. SR106387 | SR105731 | SR105732 | SR106387
R003 | NY | SOL-10416 | 35994.7188 | 40860.95 | -4866.2312 | -11.91% | 39191 | -3196.2812 | -8.156% | 1. Inverter 2, Unit 2.1 tripped offline at 11:45 on 06/19 and has been offline since then. The unit is being RMA’d. | 1. SR103246
R007 | NY | SOL-10417 | 44587.8125 | 44275.8 | 312.0125 | 0.7047% | 43538.53 | 1049.2825 | 2.41%
BK16 | NY | SOL-11093 | 45382.7969 | 44880.84 | 501.9569 | 1.118% | 41908 | 3474.7969 | 8.291%
Trenton - Trenton East | IL | SOL-11060 | 437519 | 471397.7 | -33878.7 | -7.187% | 510301 | -72782 | -14.26% | 1.Inverter 1 underperforming by 100 kW Inverter 2 underperforming by 5 kW Inverter 7 underperforming by 15 kW Inverter 8 underperforming by 37 kW Trackers have not communicated since 04/23 due to storm damage; EPC is working on partial energization, with trackers in stow and inverters expected to be derated. 2.Site tripped offline on 08/19 at 10:45 due to Casey Electric is onsite doing work on the Mian Transformer. Site came back online at 8:15 on 08/20 | 1.SR100220 2. SR106493 | SR106493
Trenton - Trenton West | IL | SOL-11061 | 277637 | 402211.7 | -124574.7 | -30.97% | 512464 | -234827 | -45.82% | 1.Inverters 7, 12 & 14 has stopped communicating from 08/27, production cannot be verified at meter level. | 1. SR107059
Dakota - Dakota Solar 1 | IL | SOL-11113 | 498585 | 531606.8 | -33021.8 | -6.212% | 386240 | 112345 | 29.09% | 1.Trackers 1 and 55 are stuck at 15degrees from 19:00CDT on 08/05. 2.Inverter 11 offline from 08/19 and it being RMAD 3. Inverter 6 tripped offline at 14:45 on 08/26. Inverter came back online at 13:15 on 08/27 | 1. SR105922 2.SR106486 3. SR106986 | SR106486 | SR106986
X018 | NY | SOL-10418 | 22069.125 | 12142.44 | 9926.685 | 81.75% | 20832 | 1237.125 | 5.939% | 1. Inverter 1 has been underperforming by 13 kW due to a 'Fault' since 07/11. 2.Inverters were offline from 09:00 to 09:45 on 08/27. Inverter 3 came back online at 11:00. | 1.SR104292 2.SR107019 | SR107019
Janiak Solar | NY | SOL-10898 | 410322 | 429489.1 | -19167.1 | -4.463% | 413602 | -3280 | -0.793% | 1.Site offline from 08:50 on 08/21 and it came back online on 08/22 at 11:00 | 1.SR106630
County Route 11B | NY | SOL-10983 | 1379609 | 1375713 | 3896 | 0.2832% | N/A |  |  | 1.Meter 2 was not capturing the actual production of Inverter 2, resulting in a deviation of approximately 700 to 900 kW in the overall meter production. Throughout the month of July, voltage drops were observed on Phases 2-3 and 3-1, while Phase 3 currents increased. Meter 2 resumed accurately capturing production data as of 08/12 | 1.SR105531
Barone | NY | SOL-11034 | 742933 | 740175 | 2758 | 0.3726% | 675605 | 67328 | 9.966%
Cedarville | IL | SOL-11069 | 417515 | 416555.5 | 959.5 | 0.2303% | 502198.2 | -84683.2 | -16.86% | 1.All trackers have been stuck at 0.99 degrees since 05/07. 2.Casey Electric checked in for punch list items. They will deenergize equipment from 19:41 to 19:51 on 08/19 to work with the transformer. The checked out. 3.Site taken offline from 09:15 to 15:15 due to EPC is replacing a board in DAS cabinet. | 1. SR101228 2.SR106480 3.SR106626 | SR106480 | SR106626
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | N/A |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 1128495 | 1128378 | 117 | 0.01037% | N/A |  |  | 1. Tracker T02.E.57 , Tracker B05 & 17 are offline. 2.- Site tripped offline at 10:30 from 07/31 and it came back online at 10:00 on 08/01 3.Inverter 2 offline from 08/02 and it came back online at 14:25 on 08/04 | 1.SR105354 2.SR105433 3. SR105530 | SR105433 | SR105530
Trinity - Freeport | IL | SOL-11057 | 477281 | 555388.9 | -78107.9 | -14.06% | 510656 | -33375 | -6.536% | 1.Site tripped offline from 18:15 to 19:15 on 08/18 and reporting " Fault Grid Phase Voltage Out of Range - GridV.OutLim" | 1.SR106471
Ransom | NY | SOL-11157 | 1140073 | 1136262 | 3811 | 0.3354% | N/A
Horseheads - Wedge | NY | SOL-11160 | 706301 | 704786 | 1515 | 0.215% | N/A |  |  | 1. Trackers 8, 9, 11, 42, 43, 109 & 110 are deviating. Will investigate next time from 08/06 | 1.SR105284
Otisville - Shoddy Hollow | NY | SOL-11185 | 1152646 | 1148442 | 4204 | 0.3661% | N/A |  |  | 1.Site offline from 08/21 at 08:45 due to planned outage and it came back online at 13:35 on 08/22 | 1. SR106448
Wellsville - Chenunda Creek | NY | SOL-11187 | 506741 | 505549 | 1192 | 0.2358% | N/A |  |  | 1. Inverter tripped offline at 16:05 on 08/06 and it came back online at 11:45 on 08/08 2.Site tripped offline at 17:45 on 08/22 and it came back online at 12:20 on 08/25 | 1.SR105769 2. SR106769 | SR106769
DC: Washington - Essex Condominium | DC | SOL-10036 | 4135 | 5246.241 | -1111.241 | -21.18% | 4946.606 | -811.606 | -16.41% | 1.Site expired in AE on 08/31
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 12597 | 11777.15 | 819.85 | 6.961% | 12293.69 | 303.31 | 2.467% | 1. Meter voltages dropped to zero at 03:30 on 08/30. 2. Inverter 2 tripped offline 15:30 on 08/31. | 1. SR100771 2. SR107263 | SR107263
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 13869 | 10867.52 | 3001.48 | 27.62% | 12294.02 | 1574.98 | 12.81%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 442807 | 542577.7 | -99770.7 | -18.39% | 561204 | -118397 | -21.1% | 1. The site tripped offline at 11:30 on 08/22 and back online at 12:45 on 08/24. 2. The site tripped offline at 05:45 on 08/25 and came back online at 08:15 on 08/27. 3. The site tripped offline at 05:15 on 08/30 and came back online at 07:45 on 08/30. | 1. SR106749 2. SR106773 3. SR107225 | SR106773 | SR107225
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 1239495 | 1259795.19 | -20300.19 | -1.611% | 1339153.7 | -99658.7 | -7.442%
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 499196 | 520375.831 | -21179.831 | -4.07% | 569975.15 | -70779.15 | -12.42% | 1. The site has been offline since 08:30 on 08/31. | 1. SR107245
NY: Cambridge - Cambridge (PW) | NY
NY: Whitesville - Independence North | NY
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Sep
Generate Capital |  |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  |  | 46243954.25 | 40838857.248 | 5405097.002 | 13.24% | 41547617.912 | 4696336.338 | 11.3% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
K026 | NY | SOL-10356 | 20034 | 32719.934 | -12685.934 | -38.77% | 29140.105 | -9106.105 | -31.25% | 1. Meter B phase currents dropped to Zero whole month. Need to replace CT | 1. SR107464
K041 | NY | SOL-10357 | 22897.875 | 26147.875 | -3250 | -12.43% | 23136 | -238.125 | -1.029%
K043 | NY | SOL-10358 | 28120.125 | 29339.769 | -1219.644 | -4.157% | 5129 | 22991.125 | 448.3% | 1. Inverter 3 has been underproducing by 12 kW since 12:45 on 09/11, as unit 3.1 (right unit) is underproducing. 2.Estimated values are low in AE we have also verified the file which was given by GC | 1. SR108295
K058 | NY | SOL-10360 | 22120.813 | 22796.144 | -675.331 | -2.962% | 21889.193 | 231.62 | 1.058%
K115 | NY | SOL-10361 | 12486.703 | 14691.922 | -2205.219 | -15.01% | 13101.525 | -614.822 | -4.693% | 1. 96 optimizers are down for site construction. GenC says EPC is remapping, appears complete on 09/17 | 1.SR093291
K152 | NY | SOL-10362 | 8545.188 | 8860.98 | -315.792 | -3.564% | 8454 | 91.188 | 1.079%
K166 | NY | SOL-10363 | 26930.25 | 33458.021 | -6527.771 | -19.51% | 30858.887 | -3928.637 | -12.73% | 1.3 optimizers are offline: 2.0.160, 3.0.17, 3.0.33 | 1.SR095666
K206 | NY | SOL-10927 | 18832.75 | 17073.18 | 1759.57 | 10.31% | 17056 | 1776.75 | 10.42%
K251 | NY | SOL-10365 | 20008.375 | 0 | 20008.375 |  | 19826.177 | 182.198 | 0.919% | 1. Weather station stopped communicating on 11/22 at 07:00. 2. Inverter module 1.0.153 12D31EC2-C5 is offline, reporting no comms with power optimizer. | 1. SR093633 2. SR093292 | SR093292
K269 | NY | SOL-10366 | 18597.063 | 22080.493 | -3483.43 | -15.78% | 18330.395 | 266.668 | 1.455% | 1.Inverters producing as expected and expected value and forecasted energy values diffrence.
K273 | NY | SOL-10367 | 12091 | 0 | 12091 |  | 23,678.5 |  |  | 1. Inverter 2, unit 2.2, was offline for multiple days and came back online at 09:30 on 09/18. 2. 26 optimizers are down for roof repair. 3. Weather station stopped communicating since 06/14/24. 4. Meter was reading inaccurate Valuses for whole month likely bad CT. | 1. SR104856 2. SR093924 3. SR086842 4. SR103245 | SR093924 | SR086842 | SR103245
K287 | NY | SOL-10919 | 16091.063 | 14086.846 | 2004.217 | 14.23% | 15813 | 278.063 | 1.758% | 1. Actual vs expected delta is showing 16% due to expected energy recording low possibly due to data glitch (similar event observe last years).
K298 | NY | SOL-10368 | 17325.438 | 18788.528 | -1463.09 | -7.787% | 17581 | -255.562 | -1.454%
K335 | NY | SOL-10370 | 18447.875 | 20337.054 | -1889.179 | -9.289% | 19788.5 | -1340.625 | -6.775%
K345 | NY | SOL-10920 | 21438.75 | 12870.767 | 8567.983 | 66.57% | 20845.5 | 593.25 | 2.846% | 1. Inverter 3 is underproducing due to unit(7E9C82CA) underproducing from 13:30 on 06/20 and reporting "external fan" fault. 2. Actual vs expected delta is showing 72% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1. SR103259
K445 | NY | SOL-10373 | 17136.844 | 19679.906 | -2543.062 | -12.92% | 16981.73 | 155.114 | 0.9134%
K495 | NY | SOL-10374 | 70875.75 | 77150.45 | -6274.7 | -8.133% | 79570.816 | -8695.066 | -10.93% | 1. Inverter 7, unit 7.1, was offline from 11:15 on 08/27 and came back online at 10:15 on 09/19. 2. Inverter 8, unit 8.3, was offline from 12:45 on 08/30 and came back online at 11:15 on 09/05. 3. Inverter 11 (left unit) was offline since 04/18 and came back online at 09:45 on 09/19. | 1. SR108228 2. SR107240 3. SR101786 SR102902 | SR107240 | SR101786 | SR102902
M020 | NY | SOL-10380 | 19863.531 | 20320.193 | -456.662 | -2.247% | 19905.5 | -41.969 | -0.2108%
M092 | NY | SOL-10383 | 19248.5 | 20469.432 | -1220.932 | -5.965% | 18463.289 | 785.211 | 4.253%
M143 | NY | SOL-10384 | 21054.938 | 24875.928 | -3820.99 | -15.36% | 20535.715 | 519.223 | 2.528% | 1. Inverter 3 left unit is having multiple trippings since 06/08 on high irradiance day. | 1. SR102672
M144 | NY | SOL-10385 | 31845.75 | 35186.455 | -3340.705 | -9.494% | 37663.851 | -5818.101 | -15.45% | 1.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
M167 | NY | SOL-10386 | 22903.438 | 17813.538 | 5089.9 | 28.57% | 25249.074 | -2345.636 | -9.29% | 1. Actual vs expected delta is showing 29% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
M188 | NY | SOL-10387 | 16372.875 | 17248.113 | -875.238 | -5.074% | 19189.209 | -2816.334 | -14.68% | 1.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
EMHC | NY | SOL-10351 | 7118.828 | 5168.558 | 1950.27 | 37.73% | 7595.843 | -477.015 | -6.28% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline 2.Actual vs expected delta is showing 36% due to expected energy recording low possibly due to data glitch (similar event observe last years). | 1.SR093236
Q008 | NY | SOL-10397 | 22429.156 | 26778.117 | -4348.961 | -16.24% | 25128 | -2698.844 | -10.74% | 1.Inverter unit 1.2 has been underperforming by approx 20kW since the site was re-energized on 8/27. | 1.SR107361
Q018 | NY | SOL-10398 | 16961.875 | 18599.816 | -1637.941 | -8.806% | 11166 | 5795.875 | 51.91% | 1.Estimated values are low in AE we have also verified the file which was given by GC
Q021 | NY | SOL-10399 | 13777.063 | 14090.446 | -313.383 | -2.224% | 12908.234 | 868.829 | 6.731%
Q025 | NY | SOL-10400 | 23244.125 | 23357.883 | -113.758 | -0.487% | 12092.5 | 11151.625 | 92.22% | 1. Actual vs Forcasted delta is showing 103% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Q074 | NY | SOL-10402 | 11384.75 | 11141.717 | 243.033 | 2.181% | 14623.435 | -3238.685 | -22.15% | 1. Home run Solar shut off the site at 08:30am on 09/22 to perform roof repairs. | 1.SR102529
Q115 | NY | SOL-10872 | 19770.813 | 21410.148 | -1639.335 | -7.657% | 19479.759 | 291.054 | 1.494%
Q139 | NY | SOL-10403 | 11696.875 | 11986.462 | -289.587 | -2.416% | 12223 | -526.125 | -4.304% | 1.Some optimizers with production issues 1264FFBB-30 - Half production ,12639DA9-BB - Half production | 1.SR088282
Q157 | NY | SOL-10404 | 19666.563 | 24651.896 | -4985.333 | -20.22% | 18871.048 | 795.515 | 4.216% | 1. Inverter 1 is back online at 10:45am on 09/11 | 1.SR105502
Q192 | NY | SOL-10406 | 32135 | 36121.082 | -3986.082 | -11.04% | 31753.192 | 381.808 | 1.202% | 1.Inverter 2 unit 2.3 was offline from 10:15 on 09/29 to end of the month | 1.SR108939
Q210 | NY | SOL-10407 | 26615.125 | 26548.079 | 67.046 | 0.2525% | 26544 | 71.125 | 0.268%
Q229 | NY | SOL-10408 | 11342.875 | 13057.554 | -1714.679 | -13.13% | 9846.137 | 1496.738 | 15.2% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1.SR088813
Q231 | NY | SOL-10870 | 39584.75 | 45767.991 | -6183.241 | -13.51% | 42636.5 | -3051.75 | -7.158% | 1. Inverter 2 unit 2.2 is being offline during morning hours and started producing at mid-day from 08/25 and mostly offline for whole day and self resolving for the next couple of days. | 1.SR105544
Q405 | NY | SOL-10409 | 48143.5 | 54005.925 | -5862.425 | -10.86% | 47283.572 | 859.928 | 1.819% | 1.Inverter 3 unit 3.3 tripped offline at 12:00PM on 08/30. 2.4 Inverter modules are offline. Will investigate next time on site. Module 1.0.64 Module 4.0.39 , 3.0.20 ,1.0.64 | 1.SR107242 2.SR093324 | SR093324
Q435 | NY | SOL-10923 | 57195.29 | 47737.007 | 9458.283 | 19.81% | 60533.5 | -3338.21 | -5.515% | 1.The meter has been capturing only 222 kW at peak since 14:15 on 08/13, later inverter 2 is back online at 11:15 on 09/12 | 1.SR107329
Q485 | NY | SOL-10869 | 58657.75 | 48085.236 | 10572.514 | 21.99% | 57296.479 | 1361.271 | 2.376% | 1.Actual vs expected delta is showing 26% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years)
Q490 | NY | SOL-10411 | 39358.5 | 0 | 39358.5 |  | 41167.805 | -1809.305 | -4.395% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. 2.Inverter 10 was underproducing by approximately 10kW on 08/28 as string 10.1 was offline.On 09/10 inverter 10 is being RMA'd | 1.SR093326 2.SR107164 | SR107164
Q620 | NY | SOL-10867 | 63311.78 | 64228.413 | -916.633 | -1.427% | 60821.093 | 2490.687 | 4.095% | 1.Inverter modules 3.0.144 and 5.0.100 are offline 4.0.66 - 30513B3F-FB - half production because split between 4 modules | 1.SR093327
QMOA | NY | SOL-10415 | 5473.6 |  |  |  | 5544.898 | -71.298 | -1.286%
X024 | NY | SOL-10419 | 25082.031 | 24457.917 | 624.114 | 2.552% | 21695 | 3387.031 | 15.61%
X026 | NY | SOL-10420 | 21192.8 | 20624.916 | 567.884 | 2.753% | 29182.126 | -7989.326 | -27.38% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1.SR095662
X090 | NY | SOL-10925 | 18101.813 | 15022.557 | 3079.256 | 20.5% | 17858 | 243.813 | 1.365%
X117 | NY | SOL-10422 | 15410.1 | 17247.805 | -1837.705 | -10.65% | 15770.38 | -360.28 | -2.285% | 1.Inverter 1 having morning shading issue
X125 | NY | SOL-10423 | 28874.625 | 30335.623 | -1460.998 | -4.816% | 26767.069 | 2107.556 | 7.874%
X134 | NY | SOL-10424 | 27962.188 | 7766.624 | 20195.564 | 260% | 26554 | 1408.188 | 5.303% | 1.During peak hours, the Plane of Array (POA) and GHI values we’re receiving from the site are unusually low, while the other parameters are within expected ranges from 07/20 at 09:30. This suggests there may be an issue with the Pyranometer sensor at the site, as the settings on the PowerTrack appear to be configured correctly. I recommend sending a technician to the site to investigate and resolve this issue. 2. 6 modules are offline: Module 1.2.1 Module 1.2.13 Module 1.2.14 Module 1.11.5 Module 2.1.12 Module 2.1.16 3.Weather Station is showing erroneous (0 w/m^2) values at mid day from 07/20 at 09:30. | 1.SR105932 2.SR098241 3. SR105932 | SR098241 | SR105932
X135 | NY | SOL-10425 | 22733.563 | 27306.838 | -4573.275 | -16.75% | 21711 | 1022.563 | 4.71% | 1.Inverter 1 unit 1.3 having morning shading issue and inverter 2 having evening shading issues
X139 JHS 222 | NY | SOL-10426 | 28952.608 | 37791.582 | -8838.974 | -23.39% | 32926.5 | -3973.892 | -12.07% | 1. Inverter 1, unit 1.7(Right unit) tripped offline at 10:00 on 09/13. 2. Inverter 1 tripped offline at 12:00 on 08/27, later back online at 13:30 on 09/11 | 1.SR107934 2.SR105933 | SR105933
X140 | NY | SOL-10926 | 19931.188 | 16423.798 | 3507.39 | 21.36% | 18287 | 1644.188 | 8.991% | 1.Inverter 3 Unit 3.3 is experiencing late starts every day, later Inverter has not experienced any issues since 9/13 | 1.SR106721
X166 | NY | SOL-10427 | 20321.6 | 21154.851 | -833.251 | -3.939% | 20083 | 238.6 | 1.188%
Murphy | MN | SOL-10094 | 786990 | 882687.634 | -95697.634 | -10.84% | 811622.1 | -24632.1 | -3.035% | 1.Inverter 5 tripped offline at 13:45 on 09/15, later technician troubleshooted the inverter and it was back online at 14:45 but modules 2 & 3 are kept offline. 2.Inverter 1 is producing at its half production through out the month. 1 IGBT needs replacement to get inverter fully functional. | 1.SR108007, SR108411 2.SR104403 | SR108411 | SR104403
Terning | MN | SOL-10093 | 852315.355 | 908127.667 | -55812.312 | -6.146% | 794890.25 | 57425.105 | 7.224%
Boas Road 04 | NY | SOL-10908 | 0 | 0 | 0 |  | 318906.342 | -318906.342 | -100% | 1. Meter was not communicated for whole month. | 1.SR098641
Kelly Bridge Farm | NY | SOL-10911 | 0 | 0 | 0 |  | 321832.089 | -321832.089 | -100% | 1. Site lost communication from 08/22, technician confirmed that the site is online onsite. GPM is shipping the equipment. | 1.SR106726
Pool Brook Road | NY | SOL-10909 | 269516 | 269514 | 2 | 0.0007421% | 306366.022 | -36850.022 | -12.03% | 1. The meter is showing a phase voltage imbalance of ~130V. Phases A & B are reading 270V and phase 3 is ~140V but is occasionally in-line with the other phases. Inverter voltage normal from 09/09. | 1.SR107702
Sackett Lake | NY | SOL-10910 | 445918 | 0 | 445918 |  | 318187.219 | 127730.781 | 40.14% | 1.Weather station lost communication from 07/15 2. Inverters filters has been replaced on 09/03. | 1.SR107603 2.SR107011 | SR107011
Burritt Road | NY | SOL-10913 | 360510 | 0 | 360510 |  | 331204.76 | 29305.24 | 8.848%
Villa Roma 1 | NY | SOL-10914 | 293402 | 0 | 293402 |  | 278783.229 | 14618.771 | 5.244% | 1.Inverter 2 did not start for production on 09/23, later back online at 11:10 on 09/24 2.Expected energy values are reporting very low. Created a case #66639 with GPM, As per GPM the BOM has been frozen from 02/27. | 1.SR108390 2.SR099403 | SR099403
Villa Roma 2 | NY | SOL-10915 | 274880 | 312522.5 | -37642.5 | -12.04% | 269917.332 | 4962.668 | 1.839% | 1.Inverter 2 having shading issue
Washington 1 | NY | SOL-10912 | 336020 | 373089.69 | -37069.69 | -9.936% | 326068.017 | 9951.983 | 3.052% | 1. Site was offline from 08:40 to 10:55 on 09/10 due to planned outage. | 1.SR107750
Washington 3 | NY | SOL-10828 | 257026 | 850868 | -593842 | -69.79% | 398744.737 | -141718.737 | -35.54% | 1. Site was offline from 08:40 to 10:55 on 09/10 due to planned outage. 2.The energy meter at Washington 3 is showing an issue with C-phase PT where the voltage measurement is drifting from 07/24, later site remain offline from 12:15 on 09/23 due to inverter to XFMR busbars had thermal damage and need to be replaced 3. Site was offline from 05:20am to 15:30 on 09/05 4.POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1.SR107751 2.SR105816 3.SR107490 4.SR093024 | SR105816 | SR107490 | SR093024
Washington 4 | NY | SOL-10829 | 351554 | 394430.9 | -42876.9 | -10.87% | 399610.639 | -48056.639 | -12.03% | 1. Site was offline from 08:40 to 10:55 on 09/10 due to planned outage. 2. Site was offline from 05:20am to 15:30 on 09/05 3.Site lost communication at 12:15 on 09/24, possibly offline. | 1.SR107758 2.SR107491 3.SR108045 | SR107491 | SR108045
Big Tree | NY | SOL-10966 | 366820 | 365800 | 1020 | 0.2788% | 308895.6 | 57924.4 | 18.75% | 1. Site tripped offline at14:05 on 09/10, later back online at 08:00 on 09/11 | 1.SR107780
Canoga | NY | SOL-10965 | 924320 | N/A |  |  | 0 | 924320
County Route 84 | NY | SOL-10967 | 926220 | 923630 | 2590 | 0.2804% | 806605.684 | 119614.316 | 14.83% | 1. Inverter 4 has been experiencing multiple trip events on 09/19 and back to normal production on 09/20. | 1.SR108277
Donati | NY | SOL-10968 | 458000 | N/A |  |  | 393379.846 | 64620.154 | 16.43% | 1.site tripped offline at 10:05am on 09/24 and back online at 14:30 on 09/24 2.All trackers are stuck from 1PM on 09/04 | 1.SR108456 2.SR107506 | SR107506
Henrietta | NY | SOL-10972 | 838690 | 836970 | 1720 | 0.2055% | 793970.349 | 44719.651 | 5.632% | 1.site tripped offline at 2:30PM on 09/24 2. 7-8 trackers were struck throughout the month. | 1.SR108486 2.SR106622 | SR106622
NY 70 | NY | SOL-10970 | 943650 | 941250 | 2400 | 0.255% | 820222.136 | 123427.864 | 15.05% | 1. Site is back online at 11:00 on 09/01. 2.Site tripped offline from 8:20AM to 18:30 on 09/17 due to utility outage. 3.44 trackers were struck through out the month. Further troubleshooting required. 4.Inverter 1 was derating by 70kw and inverter 3 is derating by 120kw due to inverter internal temperature throughout the month. | 1.SR107254 2.SR108118 3.SR106503 4.SR105774 | SR108118 | SR106503 | SR105774
Reid | NY | SOL-10991 | 755783.021 | 407513.824 | 348269.197 | 85.46% | 700567.5 | 55215.521 | 7.882% | 1. Inverter 30 tripped offline at 15:00 on 09/01 and back online at 09:45 on 09/03 2.Inverter 33 tripped offline at 11:45 on 09/20 and later back online at 11:00 on 09/21 3. Inverter 23 tripped offline at 14:00 on 09/02 and later back online at 09:13 on 09/03 4.Inverter 19 has been RMA'd from 09/15 5. Inverter 28 is back online at 08:00 and again tripped offline at 13:00 on 09/03 6.Inverter 29 is back online at 08:00 and again tripped offline at 15:00 on 09/03 and back online at 09:00 on 09/08 7. Inverter 29 tripped offline at 14:00 on 09/09 and back online at 10:00 on 09/21 8. Inverter 28 & 30 have tripped offline on 09/08 and back online on 09/21 9.inverter 9 has derated to 100kW from 08/31 10. Inverter 9 is back online at 09:00 on 09/03 11.Inverter 9 tripped offline at 10:45 on 09/15 | 1.SR107267 2.SR108310 3.SR107323 4.SR108010 5.SR106662 6.SR106755 7.SR107706 8.SR107651 9.SR107331 10.SR106786 11.SR108010 | SR108310 | SR107323 | SR108010 | SR106662 | SR106755 | SR107706 | SR107651 | SR107331 | SR106786 | SR108010
Sangolqui | NY | SOL-10975 | 66500 | 48130 | 18370 | 38.17% | 383539.736 | -317039.736 | -82.66% | 1.10 trackers are stuck from 09/22 2.Meter have stopped communicating from 13:00 on 09/04 and reporting 0 values, production can be verified at inverter level. 3.Site tripped offline from 09:55am to 14:25 on 09/24 | 1.SR108338 2.SR107449 3.SR108470 | SR107449 | SR108470
State Highway 17B | NY | SOL-10988 | 744680 | 715450 | 29230 | 4.086% | N/A |  |  | 1.All inverter experiencing multiple trip events due to Phase 2 voltage fluctuations at meter. Inverters 3 and 4 are offline on 09/17 and later back online at 16:30 on 09/17 | 1.SR108139
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 831585.981 | -831585.981 | -100% | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required. On 07/02 technician was after pulling event files from the SEL for analysis. The site remains offline. | 1.SR101820
West Creek | NY | SOL-10995 | 986880 | 844610 | 142270 | 16.84% | 803415.521 | 183464.479 | 22.84% | 1.Site started communication on 09/02 the data of august was bacfilled to september due to that actual was high
Wildflower | NY | SOL-10982 | 747029 | 745204 | 1825 | 0.2449% | 779828.53 | -32799.53 | -4.206% | 1. Inverter 1 is derating by 140 kW and Inverter 4 by 70 kW during peak hours throughout the month. | 1.SR105775
Glen Mary 1 | NY | SOL-10993 | 879050 | 874930 | 4120 | 0.4709% | 817647.657 | 61402.343 | 7.51%
Glen Mary 2 | NY | SOL-10994 | 379830 | 0 | 379830 |  | 346254.488 | 33575.512 | 9.697% | 1.POA Pyranometer UP irradiance reporting 0W/m2 since 08/18. Due to this expected energy values in monthly reports has been affected | 1.SR105649
Telegraph 1 | NY | SOL-11003 | 671379 | N/A |  |  | 561734.447 | 109644.553 | 19.52% | 1. Inverter 1 has been derating at 1343 kW since 08/17, later back to normal production at 13:40 on 09/02 2.Site tripped offline from 08:25 AM to 11:55 AM and again 13:45 to 18:45 on 09/17. | 1.SR107234 2.SR108143 | SR108143
Telegraph 2 | NY | SOL-11004 | 358560 | N/A |  |  | 291844.727 | 66715.273 | 22.86% | 1.Site tripped offline from 08:25 AM to 11:55 AM and again 13:45 to 18:45 on 09/17. 2.Inverter 1 has been derating at 1343 kW since 08/17, later back to normal production at 13:40 on 09/02 3. Site lost communication from 08:30am on 09/18 and later regained at 02:05am on 09/19 energy has not backfilled, possibly offline. | 1.SR108145 2.SR107236 3.SR105659, SR108266 | SR107236 | SR105659 | SR108266
Cafferty Hill | NY | SOL-10996 | 876020 | 906739.44 | -30719.44 | -3.388% | 793235.026 | 82784.974 | 10.44%
Dunkleman | NY | SOL-11008 | 1056180 | 1052940 | 3240 | 0.3077% | 883883.249 | 172296.751 | 19.49% | 1. Pad 1 trackers 1, 63 ,109 are stuck at 0 deg and trackers 57, 119 are stuck at 255 deg. Additionally, Pad 2 trackers 43 , 114 are stuck at 0 deg and trackers 86, 124 are stuck at 255 deg from 09/07. Charging panel and node is being RMA'd | 1.SR107585
Route 19 1 | NY | SOL-11001 | 226090 | 225640 | 450 | 0.1994% | 358017.672 | -131927.672 | -36.85% | 1.The inverter was offline on 08/25 and came back online at 15:05 on the same day, but strings 4 and 5 remain offline, and 2 Y-connectors later the strings has been replaced on 09/12 2. Site is not communicating from 09/16 to DAS but producing onsite. | 1.SR106797 2.SR108023 | SR108023
Route 19 2 | NY | SOL-11002 | 1022560 | 1019080 | 3480 | 0.3415% | 888708.564 | 133851.436 | 15.06% | 1.Site tripped offline from 08:25 AM to 11:55 AM and again 13:45 to 18:45 on 09/17. | 1.SR108111
Yellow Mills 1 | NY | SOL-11006 | 107931 | 106753 | 1178 | 1.103% | 329702.798 | -221771.798 | -67.26% | 1.Site tripped offline at 08:00 on 09/09 and meter voltage dropped to 0V and remained offline throughout the month. | 1.SR107665
Yellow Mills 2 | NY | SOL-11005 | 105779 | N/A |  |  | 342267.643 | -236488.643 | -69.09% | 1.Meter is reporting 0 values since 09/04 and even stopped capturing data throughout the month. 2.Site stopped communicating from 09/09 | 1.SR107450 2.SR107667 | SR107667
Yellow Mills 3 | NY | SOL-11007 | 101186 | 84818 | 16368 | 19.3% | 326250.238 | -225064.238 | -68.99% | 1.Site tripped offline at 08:00 on 09/09 and meter voltage dropped to 0V and remained offline throughout the month. | 1.SR107666
Catskill | NY | SOL-11021 | 471584 | N/A |  |  | 627325.808 | -155741.808 | -24.83% | 1.Inverter 1 has been offline since 08/25 and was back online at 09:00 on 09/09 | 1.SR106843
Eddy Ridge | NY | SOL-11054 | 427871 | 425818 | 2053 | 0.4821% | 447750 | -19879 | -4.44% | 1. Trackers 1 through 49 have been stuck since 07/28. | 1.SR105180
Ridgeway #1 | NY | SOL-11018 | 1147207 | 1142921 | 4286 | 0.375% | 1142921 | 4286 | 0.375% | 1.Inverter 1 is facing multiple trippings and each time it trips its reporting "Overall Work STOP" since 09/04 and issue was resolved on 09/12. | 1.SR107142
Rivard 1 | NY | SOL-11011 | 854070.365 | 928806.68 | -74736.315 | -8.046% | 724471.91 | 129598.455 | 17.89%
Rivard 2 | NY | SOL-11012 | 876610.97 | 857273.84 | 19337.13 | 2.256% | 693618.81 | 182992.16 | 26.38%
Ridgeway #2 | NY | SOL-11027 | 576344 | 574553 | 1791 | 0.3117% | 492013.43 | 84330.57 | 17.14%
Spencer | NY | SOL-11017 | 675104.05 | 672343.15 | 2760.9 | 0.4106% | 936295 | -261190.95 | -27.9% | 1.Site tripped offline at 15:35 on 09/15 and it came back online at 09:35 on 09/16 and again site tripped offline form 09:40 on 09/22 and it came back online at 12:25 on 09/23 | 1.SR107955
Reisender | NY | SOL-10886 | 334820 | 334730 | 90 | 0.02689% | 325840.167 | 8979.833 | 2.756%
Finney | NY | SOL-10999 | 297560 | 285270 | 12290 | 4.308% | 962613.79 | -665053.79 | -69.09% | 1.Site tripped offline at 15:03 on 09/04 and was back online 09/05 2.Site tripped offline at 07:25 on 09/05 and SEL voltage dropped to 1V and back at 12:07 on 09/08 but inverter 1 left offline since then. Site again tripped offline at 09:32 on 09/10 and was back online at 10:53 on 09/24. | 1.SR107478 2.SR107493,SR107781 | SR107493 | SR107781
Davis Solar | NY | SOL-10958 | 350384 | 374766.43 | -24382.43 | -6.506% | 368671 | -18287 | -4.96% | 1.Inverter tripped offline at 16:00 on 09/06 and reporting "AC breaker switch open" and was back online on 09/07.Inverter again tripped offline at 16:30 on 09/09 reporting AC contactor is in "Open" state and was back at 18:00 on the same day.Inverter again tripped offlinr at 11:00 on 09/22 and was back at 13:15 on 09/22. | 1.SR107090
Genesee | NY | SOL-10951 | 745988 | 744584.55 | 1403.45 | 0.1885% | 725375.638 | 20612.362 | 2.842% | 1. Trackers 23, 24, 33, 37, and 72 through 151 have been stuck since 06/02 | 1.SR102328
Landau I | NY | SOL-10891 | 349600 | N/A |  |  | 351386.537 | -1786.537 | -0.5084%
Landau II | NY | SOL-10895 | 540650 | N/A |  |  | N/A
New Beginnings | NY | SOL-10890 | 344350 | 344300 | 50 | 0.01452% | 343001.807 | 1348.193 | 0.3931%
Bullitt Farm Solar, LLC | NY | SOL-10998 | 365107 | 383050.134 | -17943.134 | -4.684% | 403105.53 | -37998.53 | -9.426%
Brodhead Solar, LLC | NY | SOL-10899 | 977279 | 1028065.607 | -50786.607 | -4.94% | 871698.31 | 105580.69 | 12.11%
Svenski | NY | SOL-10894 | 360081 | N/A |  |  | 351104.111 | 8976.889 | 2.557%
Bantam | NY | SOL-10986 | 32790 | 689420 | -656630 | -95.24% | 926335.493 | -893545.493 | -96.46% | 1. Tracker NCU4 1056 was stuck from 08/15 and later self-resolved. Tracker NCU2 1005 got stuck on 09/08 and resumed tracking on 09/11. 2. Inverter 1 was offline from 13:00 on 09/09 and came back online at 07:00 on 09/10. The inverter went offline again on 09/16. 3. The meter is missing phase A throughout the month, resulting in incomplete production data for both inverters. | 1. SR106058 2. SR106176 3. SR108248 | SR106176 | SR108248
Bogart | NY | SOL-10887 | 349730 | 348570 | 1160 | 0.3328% | 340590.939 | 9139.061 | 2.683%
Dubois | NY | SOL-10892 | [7 empty] | 1. The site has been offline since 06:20 on 08/10 due to a transformer failure. | 1. SR105964, SR106921 | SR106921
Salt Point | NY | SOL-10888 | 288960 | 288960 | 0 | 0% | 373365.487 | -84405.487 | -22.61% | 1. Module 4 was offline from 09/01 and came back online at 09:40 on 09/03. 2. The site was offline on 09/15 and came back online at 07:05 on 09/16. 3. The site was offline on 09/18 and came back online at 12:25 on 09/19. 4. The site was offline from 07:20 to 11:20 on 09/21. 5. The site was offline from 07:15 to 09:15 on 09/23. 6. Module 4 was offline from 07:30 on 09/21 and came back online at 11:50 on 09/23. | 1. SR107313 2. SR107939 3. SR108225 4. SR108330 5. SR108395 6. SR108400 | SR107939 | SR108225 | SR108330 | SR108395 | SR108400
Wheatland 2A | NY | SOL-10971 | 777430 | 775310 | 2120 | 0.2734% | 814850.225 | -37420.225 | -4.592% | 1. The site tripped offline at 10:30 on 09/03 and came back online at 11:05 on 09/05. 2. Inverter 1 tripped offline at 09:25 on 09/14 and came back online at 12:15 on 09/15. 3. The site was offline from 12:55 to 14:30 on 09/23 while the technician was onsite for preventive maintenance. | 1. SR107376 2. SR107937 3. PM9480 | SR107937
Wheatland 2B | NY | SOL-10961 | 877860 | 875560 | 2300 | 0.2627% | 804178.799 | 73681.201 | 9.162%
Brickchurch | NY | SOL-10889 | 0 | 0 | 0 |  | 374561.079 | -374561.079 | -100% | 1. Inverter 1 offline from 07/01 is reporting the AC breaker state as OPEN. Inverter 1 to be RMA'd and remain offline through out the month. 2. Nineteen trackers have been stuck throughout the month: NCU1 SPC 115–127 and NCU2 SPC 216, 220, 230, 240, 253, 329, and 338. Additional troubleshooting is required as the terminal blocks need to be replaced. | 1. SR106501 2. SR097454 | SR097454
McCarthy Solar | NY | SOL-10992 | 364240 | 0 | 364240 |  | 350611.85 | 13628.15 | 3.887%
Costanza | NY | SOL-10907 | 381550 | 366527.32 | 15022.68 | 4.099% | 350492.93 | 31057.07 | 8.861% | 1. The site tripped offline at 02:20 on 09/06 and came back online at 17:32 on the same day. 2. The site tripped offline at 07:15 on 09/12 and came back online at 14:15 on the same day. 3. The site tripped offline at 07:45 on 09/22 and came back online at 09:35 on the same day. | 1. SR107556 2. SR107893 3. SR108334 | SR107893 | SR108334
Lockenhurst Pond | NY | SOL-11000 | 382747 | 410378.178 | -27631.178 | -6.733% | 382545 | 202 | 0.0528%
Drinkwater | NY | SOL-10896 | 402780 | 401580 | 1200 | 0.2988% | 353111.54 | 49668.46 | 14.07%
Altamont | NY | SOL-11085 | 771306 | 808528.373 | -37222.373 | -4.604% | 565272.03 | 206033.97 | 36.45%
Krumkill North | NY | SOL-11086 | 705400 | 804517.54 | -99117.54 | -12.32% | 657287.14 | 48112.86 | 7.32% | 1.Inverter 2 having heavy shading isuue from afternoon to evening hours
Krumkill South | NY | SOL-11087 | 617530 | 639693.761 | -22163.761 | -3.465% | 515283.25 | 102246.75 | 19.84%
X092 | NY | SOL-11189 | 16742.8 | 16770.178 | -27.378 | -0.1633% | 16607.5 | 135.3 | 0.8147%
X093 | NY | SOL-10932 | 12987.717 | 12203.745 | 783.972 | 6.424% | 11630 | 1357.717 | 11.67%
X095 | NY | SOL-10929 | 16558.438 | 16975.633 | -417.195 | -2.458% | 15647 | 911.438 | 5.825%
X181 | NY | SOL-10428 | 31569.219 | 27160.68 | 4408.539 | 16.23% | 28857 | 2712.219 | 9.399%
X415 | NY | SOL-10429 | 19582.922 | 16711.879 | 2871.043 | 17.18% | 16452.5 | 3130.422 | 19.03%
K198 | NY | SOL-10930 | 14193.039 | 13846.802 | 346.237 | 2.5% | 13571.5 | 621.539 | 4.58%
K203 | NY | SOL-11190 | 18451.9 | 16311.15 | 2140.75 | 13.12% | 18078.5 | 373.4 | 2.065%
K213 | NY | SOL-11191 | 20538.4 | 22358.422 | -1820.022 | -8.14% | 19254.5 | 1283.9 | 6.668%
K217 | NY | SOL-10933 | 10837.977 | 10607.658 | 230.319 | 2.171% | 10100.5 | 737.477 | 7.301%
K307 | NY | SOL-10876 | 22645.766 | 25851.782 | -3206.016 | -12.4% | 20995 | 1650.766 | 7.863% | 1. Inverter 2 experiencing minor shading issue
K610 | NY | SOL-11158 | 20083.4 | 26649.622 | -6566.222 | -24.64% | 25554 | -5470.6 | -21.41% | 1. Inverter 2 (as per SE Inverter 1) — Units 1.1 and 1.2 tripped offline at 12:00, and Unit 1.3 tripped offline at 16:15 on 06/18. The inverter has remained offline and SolarEdge has rmad the center unit and Left unit being RMA'd. | 1.SR103141
M025 | NY | SOL-10392 | 21902.109 | 25290.633 | -3388.524 | -13.4% | 22627.5 | -725.391 | -3.206% | 1.Inverter 3 left unit tripped offline at 13:00 on 09/04 and was back online at 11:00 on 09/13. 2.Inverter 1 tripped offline at 13:30 on 09/04 displaying "generic fault in AE" and no fault in SE and was back online at 12:30 on 09/10. | 1.SR103871 2.SR103710 | SR103710
M028 | NY | SOL-10381 | 18832.828 | 18450.27 | 382.558 | 2.073% | 16699.5 | 2133.328 | 12.77%
Q030 | NY | SOL-10878 | 21987.531 | 22008.785 | -21.254 | -0.09657% | 20328 | 1659.531 | 8.164%
Q130 | NY | SOL-10877 | 12071.445 | 11539.963 | 531.482 | 4.606% | 11688.512 | 382.933 | 3.276%
Q196 | NY | SOL-10879 | 15831.259 | 16625.3 | -794.041 | -4.776% | 15117 | 714.259 | 4.725%
Q220 | NY | SOL-10873 | 18870.906 | 22142.483 | -3271.577 | -14.78% | 17206 | 1664.906 | 9.676% | 1. The inverters are experiencing minor shading.
Q205 | NY | SOL-10922 | 19051.906 | 27873.993 | -8822.087 | -31.65% | 20799 | -1747.094 | -8.4% | 1.Inverter 2 , unit 2.1 started prodduction on 09/15 | 1.SR106530
Q400 | NY | SOL-10871 | 24972.609 | N/A |  |  | 32920 | -7947.391 | -24.14% | 1.Inverter 1 unit 1.1 tripped offline at 1:45pm on 09/02 and was back online at 8:45am on 09/04. 2.Inverter 2 unit 2.1 tripped offline since 02:15pm on 08/23 flagging "03*9B" error and was back online at 08:30 am on 09/04. 3.Inverter 3 unit 3.2 was offline from 09/12 and remained throughout the month. | 1.SR107411 2.SR106387 3.SR107805,SR103641 | SR106387 | SR107805 | SR103641
R003 | NY | SOL-10416 | 31126.137 | 32647.877 | -1521.74 | -4.661% | 31715 | -588.863 | -1.857% | 1. Inverter 2, Unit 2.1 tripped offline at 11:45 on 06/19 and was back online at 09:30am on 09/16. | 1.SR103246
R007 | NY | SOL-10417 | 33838.344 | 35931.706 | -2093.362 | -5.826% | 37087.147 | -3248.803 | -8.76% | 1.Inverter 1 unit 1.2 was offline since 09/16 and remained offline throughout the same. | 1.SR108093
BK16 | NY | SOL-11093 | 35419.531 | 35684.722 | -265.191 | -0.7431% | 33985 | 1434.531 | 4.221%
Trenton - Trenton East | IL | SOL-11060 | 385246 | 370788.592 | 14457.408 | 3.899% | 414731 |  | 0% | 1.Inveter was offline from 07:30cdt to 08:45cdt on 09/05. 2.Inverter 1 underperforming by 100 kW, inverter 2 underperforming by 5 kW, inverter 7 underperforming by 15 kW, inverter 8 underperforming by 37 kW, inverter 10 dropped 15kW since 8/28/25,inverter 9 dropped 7 kW since 9/4/25. | 1.SR107495 2.SR100220 | SR100220
Trenton - Trenton West | IL | SOL-11061 | 200204 | 314115.898 | -113911.898 | -36.26% | 418327.5 | -218123.5 | -52.14% | 1.Inverter 8 has stopped communicating at 07:15cdt on 09/23,no production at meter level and was back at 12:30cdt on 09/23. 2.Inverter 6 has stop communicating since 5:30cdt on 09/22,no production at meter level 3.Inverter 10 stop communicating at 07:00cdt on 09/02, no production at meter level and was back at 17:00cdt on 09/04. 4.Inverter 11 has stopped communicating since 08/27 ,no production at meter level.Inverters 7, 12 & 14 has stopped communicating since 08/27, production cannot be verified at meter level.Inverter 12 was back at 17:00cdt on 09/04. | 1.SR108427 2.SR108396 3.SR107295 4.SR107059 | SR108396 | SR107295 | SR107059
Dakota - Dakota Solar 1 | IL | SOL-11113 | 453465 | 466964.159 | -13499.159 | -2.891% | 338951 | 114514 | 33.78% | 1.Trackers 1 and 55 are stuck at 15degrees from 19:00CDT on 08/05. 2.Inverter 11 offline from 08/19 and was back online at 10:00CDT on 09/11. | 1.SR105922 2.SR106486 | SR106486
X018 | NY | SOL-10418 | 17922.438 | 17687.56 |  | 0% | 18838.5 | -916.062 | -4.863%
Janiak Solar | NY | SOL-10898 | 364927 | 388586.723 | -23659.723 | -6.089% | 348105 | 16822 | 4.832%
County Route 11B | NY | SOL-10983 | 1158494.01 | 1155494.09 | 2999.92 | 0.2596% | N/A
Barone | NY | SOL-11034 | 509899 | 507654 | 2245 | 0.4422% | 553220 | -43321 | -7.831% | 1.Site tripped offline at 09:35 on 09/03 and was back online at 03:20 on 09/04 .Site again tripped offline at 09:20 on 09/15,meter voltages dropped to 0V. Additionally both Z-phase and Y- phase voltages are also dropped to 0V and site was back online at 08:30 on 09/17. | 1.SR107368,SR107988 | SR107988
Cedarville | IL | SOL-11069 | 401966 | 398283.639 | 3682.361 | 0.9246% | 406725.14 | -4759.14 | -1.17%
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | N/A |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 970564 | 970445 | 119 | 0.01226% | N/A |  |  | 1.All trackers are currently operating. | 1.SR105354,SR106824 | SR106824
Trinity - Freeport | IL | SOL-11057 | 440093 | 490266.228 | -50173.228 | -10.23% | 417863.5 | 22229.5 | 5.32% | 1.Currently trackers TCU 33 through 66 are currently stuck and 3,19,50,54,62,64 are stuck. Waiting for permission to dispatch 2.Inverter 2 is derating by anywhere from 5 kW to ~20 kW in the afternoons. Issue looks to have started on 03/28. Doesn't look like shading should be an issue here, and we do not have data from this time last year. No alerts present. | 1. SR098066 2. SR099545 | SR099545
Ransom | NY | SOL-11157 | 879502 | 875614 | 3888 | 0.444% | N/A |  |  | 1. Inverter 1 has been underproducing by 300 kW and Inverter 2 by 2,000 kW since 09/08, as all trackers except 92–119 and 169–175 (out of 175 trackers) were stuck at 49°. The issue was later resolved at 12:20 on 09/11. | 1. SR107641
Horseheads - Wedge | NY | SOL-11160 | 538382 | 536973 | 1409 | 0.2624% | N/A |  |  | 1. Trackers 8, 9, 11, 42, 43, 109, and 110 were deviating. Trackers 11, 42, 43, 109, and 110 resumed tracking on 09/11, and currently, trackers 8 and 9 are still deviating. | 1. SR105284
Otisville - Shoddy Hollow | NY | SOL-11185 | 958525 | 954010 | 4515 | 0.4733% | N/A
Wellsville - Chenunda Creek | NY | SOL-11187 | 429386 | 428161 | 1225 | 0.2861% | N/A |  |  | 1. The site went offline at 12:45 on 09/05 and came back online at 15:25 on 09/08. 2. The site went offline at 09:35 on 09/11 and came back online at 19:40 on the same day. | 1. SR107529 2. SR107809, SR107813 | SR107809 | SR107813
DC: Washington - Essex Condominium | DC | SOL-10036 | 3165 | 4005.132 | -840.132 | -20.98% | 4042.779 | -877.779 | -21.71% | 1. The site is performing as expected, but the expected and forecasted values are high. A similar event was observed over the past two years.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 7461 | 11389.514 | -3928.514 | -34.49% | 12766.551 | -5305.551 | -41.56% | 1. Inverter 2 was offline from 09/01 and came back online on 09/23. 2. Meter voltages dropped to zero at 12:45 on 09/07 and were restored at 12:45 on 09/11. | 1. SR107263 2. SR100771 | SR100771
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 12995 | 10270.552 | 2724.448 | 26.53% | 12759.719 | 235.281 | 1.844%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 441656 | 451979.629 | -10323.629 | -2.284% | 467435.56 | -25779.56 | -5.515%
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 867778 | 1010152.24 | -142374.24 | -14.09% | 1121564 | -253786 | -22.63% | 1. Pad 2 has been offline since 11:45 on 09/23. | 1. SR108424
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 441290 | 325978.842 | 115311.158 | 35.37% | 456126.23 | -14836.23 | -3.253% | 1. The site tripped offline at 08:30 on 08/31 and came back online at 10:00 on 09/03. 2. The weather station stopped communicating at 08:00 on 09/22. | 1. SR107245 2. SR108392 | SR108392
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 859803.23 | 883303.58 | -23500.35 | -2.661% | 839014.5 |  | 0%
NY: Whitesville - Independence North | NY | SOL-11186 | 765233 | N/A |  |  | N/A
IL: Beecher - Cottage Grove North (PW) | IL
IL: Beecher - Cottage Grove South (PW) | IL
IL: Harvard - 9618 US HWY 14 (PW) | IL
IL: Beecher - 701 E Goodenow Rd (PW) | IL
NY: Stormville - Green Haven - (IRA) | NY
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Oct
Generate Capital |  |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  |  | 39009950.0944 | 14999937.291 | 24010012.8034 | 160.1% | 32192167.075 | 6817783.0194 | 21.18% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
K026 | NY | SOL-10356 | 15322.125 | 25865.84 | -10543.715 | -40.76% | 24623.61 | -9301.485 | -37.77% | 1. Meter B phase currents dropped to Zero whole month. Need to replace CT's | 1. SR107464 | 1. Pending
K041 | NY | SOL-10357 | 17728.1562 | 20661.97 | -2933.8138 | -14.2% | 17613 | 115.1562 | 0.6538% | 1. Inverter 2 has afternoon shading.
K043 | NY | SOL-10358 | 20883.7831 | 22521.48 | -1637.6969 | -7.272% | 3897 | 16986.7831 | 435.9% | 1. Inverter 3 has been underproducing by 12 kW and reporting "External Fan Fault" since 12:45 on 09/11, as unit 3.1 (right unit) is underproducing. 2.Estimated values are low in AE we have also verified the file which was given by GC | 1. SR108295 | 1. Completed
K058 | NY | SOL-10360 | 17473.1875 | 18255.69 | -782.5025 | -4.286% | 19098.85 | -1625.6625 | -8.512%
K115 | NY | SOL-10361 | 10477.875 | 11459.6 | -981.725 | -8.567% | 9801.668 | 676.207 | 6.899% | 1. 96 optimizers are down for site construction. GenC says EPC is remapping, appears complete on 09/17 | 1.SR093291 | 1.Closed
K152 | NY | SOL-10362 | 6524.75 | 6954.571 | -429.821 | -6.18% | 7441 | -916.25 | -12.31% | 1.Site production was low due to low irradiance on 10/30
K166 | NY | SOL-10363 | 19095.625 | 25560.51 | -6464.885 | -25.29% | 26412.32 | -7316.695 | -27.7% | 1.3 optimizers are offline: 2.0.160, 3.0.17, 3.0.33 | 1.SR095666 | 1. Pending
K206 | NY | SOL-10927 | 13546.1562 | 12440.67 | 1105.4862 | 8.886% | 12467 | 1079.1562 | 8.656%
K251 | NY | SOL-10365 | 15420.4375 | 0 | 15420.4375 |  | 17427.71 | -2007.2725 | -11.52% | 1. Weather station stopped communicating on 11/22 at 07:00. pending replacement POA. 2. Inverter module 1.0.153 (12D31EC2-C5) went offline on 11/15/24, reporting “no communication with power optimizer,” and came back online at 12:00 on 10/09. | 1. SR093633 2. SR093292 | 1. Pending 2. Pending | SR093292
K269 | NY | SOL-10366 | 14114.0625 | 17502.91 | -3388.8475 | -19.36% | 13588.61 | 525.4525 | 3.867% | 1.Inverters producing as expected and expected value and forecasted energy values diffrence.
K273 | NY | SOL-10367 | 10509.4375 | 0 | 10509.4375 |  | 20518 | -10008.5625 | -48.78% | 1. Inverter 2, unit 2.2, was offline for multiple days and After the RMA’d board was replaced, the inverter came back online at 09:30 on 10/10. 2. 26 optimizers are down for roof repair. 3. Weather station stopped communicating since 06/14/24. 4. Meter was reading inaccurate Valuses form 06/20/25. After the technician replaced the CTs on 10/22, the meter is reading correctly. | 1. SR104856 2. SR093924 3. SR086842 4. SR103245 | 1. Closed 2. Closed 3. Closed 4. Work in Progress | SR093924 | SR086842 | SR103245
K287 | NY | SOL-10919 | 12717.2812 | 11438.47 | 1278.8113 | 11.18% | 11897 | 820.2812 | 6.895% | 1. Actual vs expected delta is showing 16% due to expected energy recording low possibly due to data glitch (similar event observe last years).
K298 | NY | SOL-10368 | 12865.3125 | 14909.92 | -2044.6075 | -13.71% | 12316 | 549.3125 | 4.46% | 1. Inverter 2 tripped offline at 14:46 to 15:45 on 10/07 later self resolved. | 1. SR109161 | 1. Closed
K335 | NY | SOL-10370 | 13563.0625 | 15975.83 | -2412.7675 | -15.1% | 17347 | -3783.9375 | -21.81% | 1. Inverter 1 has minor shading issue.
K345 | NY | SOL-10920 | 16271.7812 | 10617.07 | 5654.7113 | 53.26% | 15094 | 1177.7812 | 7.803% | 1. Inverter 3 is underproducing due to unit(7E9C82CA) underproducing from 13:30 on 06/20 and reporting "external fan" fault. 2. Actual vs expected delta is showing 72% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1. SR103259 | 1. Completed
K445 | NY | SOL-10373 | 9833.2862 | 15889.4 | -6056.1138 | -38.11% | 12274.88 | -2441.5938 | -19.89% | 1. Inverter 1, Unit 12, was offline from 10/01 to 10/16, and two strings were isolated from Unit 1.2 from 10/16. | 1. PM8307, SR109623 | 1. Completed, Pending
K495 | NY | SOL-10374 | 57601.625 | 63443.04 | -5841.415 | -9.207% | 63000.45 | -5398.825 | -8.57% | 1. Inverter 12 tripped offline at 17:00 on 10/20. | 1. SR110132 | 1. pending
M020 | NY | SOL-10380 | 15019.9375 | 15837.73 | -817.7925 | -5.164% | 15061 | -41.0625 | -0.2726%
M092 | NY | SOL-10383 | 14068.1875 | 15915.89 | -1847.7025 | -11.61% | 13368.61 | 699.5775 | 5.233% | 1.Site production was low due to low irradiance on 10/30
M143 | NY | SOL-10384 | 16474.625 | 18416.57 | -1941.945 | -10.54% | 15146.07 | 1328.555 | 8.772% | 1. Inverter 3 left unit is having multiple trippings since 06/08 on high irradiance day. After the technician replaced the DC relay board on 10/03, the inverter came back online and has been producing as expected. | 1. SR102672 | 1. Closed
M144 | NY | SOL-10385 | 23735.4375 | 27682.29 | -3946.8525 | -14.26% | 30843.31 | -7107.8725 | -23.05% | 1. Inverter 2 has afternoon shading.
M167 | NY | SOL-10386 | 16164.4062 | 14225.12 | 1939.2862 | 13.63% | 17650.07 | -1485.6637 | -8.417% | 1. Actual vs expected delta is showing 29% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
M188 | NY | SOL-10387 | 12373.6875 | 13753.56 | -1379.8725 | -10.03% | 16022.87 | -3649.1825 | -22.77% | 1. Inverter 3 has heavy morning shading.
EMHC | NY | SOL-10351 | 5036.5938 | 3712.476 | 1324.1177 | 35.67% | 4938.833 | 97.7608 | 1.979% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline | 1.SR093236 | 1.Pending
Q008 | NY | SOL-10397 | 19059.5625 | 21709.07 | -2649.5075 | -12.2% | 18843 | 216.5625 | 1.149% | 1.Inverter unit 1.2 has been underperforming by approx 20kW since the site was re-energized on 8/27 and fans were replaced on 10/06. | 1.SR107741 | 1.Closed
Q018 | NY | SOL-10398 | 13329.5625 | 14739.7 | -1410.1375 | -9.567% | 13629.77 | -300.2075 | -2.203%
Q021 | NY | SOL-10399 | 10328.3125 | 11597.72 | -1269.4075 | -10.95% | 11279.66 | -951.3475 | -8.434% | 1.Site production was low due to low irradiance on 10/30
Q025 | NY | SOL-10400 | 17661.375 | 18436.69 | -775.315 | -4.205% | 9900 | 7761.375 | 78.4% | 1. Actual vs Forcasted delta is showing 78% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 13063 | -13063 | -100% | 1. Home run Solar shut off the site at 08:30am on 09/22 to perform roof repairs. | 1.SR102529 | 1.Pending
Q115 | NY | SOL-10872 | 15241.9375 | 17179.18 | -1937.2425 | -11.28% | 17055.62 | -1813.6825 | -10.63% | 1. Inverter 1 left unit offline from 10/29 | 1. SR110250 | 1.Pending
Q139 | NY | SOL-10403 | 8826.8125 | 9185.824 | -359.0115 | -3.908% | 10659 | -1832.1875 | -17.19% | 1.Some optimizers with production issues 1264FFBB-30 - Half production ,12639DA9-BB - Half production | 1.SR088282 | 1.Pending
Q157 | NY | SOL-10404 | 15808.375 | 20001.04 | -4192.665 | -20.96% | 19280 | -3471.625 | -18.01% | 1.Inverter 2 expericing afternoon shading issue
Q192 | NY | SOL-10406 | 20984.75 | 28074.19 | -7089.44 | -25.25% | 27986.62 | -7001.87 | -25.02% | 1. Inverter 2 unit 2.3 was being RMA'd | 1.SR108939 | 1.Pending
Q210 | NY | SOL-10407 | 20535.375 | 20691.1 | -155.725 | -0.7526% | 23419 | -2883.625 | -12.31% | 1. Inverter 1 producing as expected from 10/03 | 1. SR089666 | 1.Closed
Q229 | NY | SOL-10408 | 8171.6875 | 10096.77 | -1925.0825 | -19.07% | 8650 | -478.3125 | -5.53% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1.SR088813 | 1.Pending
Q231 | NY | SOL-10870 | 33472.625 | 39024.29 | -5551.665 | -14.23% | 30569 | 2903.625 | 9.499% | 1.Inverter 2 unit 2.2 resolved from 10/15 | 1. SR105544 | 1.Closed
Q405 | NY | SOL-10409 | 38302.75 | 43609.51 | -5306.76 | -12.17% | 41663.05 | -3360.3 | -8.065% | 1.Inverter 3 unit 3.3 tripped offline at 12:00PM on 08/30. 2.4 Inverter modules are offline Module 1.0.64 Module 4.0.39 3.0.20 1.0.64 | 1.SR107242 2.SR093324 | 1.Completed 2.Pending | SR093324
Q435 | NY | SOL-10923 | 50565.5 | 36680.84 | 13884.66 | 37.85% | 44849 | 5716.5 | 12.75% | 1. Weather station has morning shading due to that expected values are low.
Q485 | NY | SOL-10869 | 43347.25 | 38010.84 | 5336.41 | 14.04% | 42385.08 | 962.17 | 2.27% | 1.Actual vs expected delta is showing 14% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years)
Q490 | NY | SOL-10411 | 30568 | 0 | 30568 |  | 36013.56 | -5445.56 | -15.12% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. 2.Inverter 10 was underproducing by approximately 10kW on 08/28 as string 10.1 was offline and later back online on 10/15 as the power head was swapped. | 1.SR093326 2.SR107164 | 1.Pending 2.Completed | SR107164
Q620 | NY | SOL-10867 | 49130 | 50485.44 | -1355.44 | -2.685% | 46090.57 | 3039.43 | 6.594% | 1.Inverter modules 3.0.144 and 5.0.100 are offline 4.0.66 - 30513B3F-FB - half production because split between 4 modules | 1.SR093327 | 1.Pending
QMOA | NY | SOL-10415 | 4287.9 | N/A |  |  | 4127.039 | 160.861 | 3.898%
X024 | NY | SOL-10419 | 19157.625 | 19462.55 | -304.925 | -1.567% | 18573 | 584.625 | 3.148%
X026 | NY | SOL-10420 | 15160.7 | 16267.21 | -1106.51 | -6.802% | 24659.12 | -9498.42 | -38.52% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1.SR109950 | 1.Pending
X090 | NY | SOL-10925 | 7869.7188 | 10452.05 | -2582.3312 | -24.71% | 12975 | -5105.2812 | -39.35% | 1. Inverter 1 unit 1.1 was offline for whole month and unit 1.2 was offline from 10/19. | 1. SR110586 | 1. New
X117 | NY | SOL-10422 | 11156.7 | 13548.14 | -2391.44 | -17.65% | 13801.31 | -2644.61 | -19.16% | 1.Inverter 1 having morning shading issue
X125 | NY | SOL-10423 | 21704.0625 | 23787.01 | -2082.9475 | -8.757% | 20245.09 | 1458.9725 | 7.207%
X134 | NY | SOL-10424 | 20769.875 | 16055.73 | 4714.145 | 29.36% | 19866 | 903.875 | 4.55% | 1.During peak hours, the Plane of Array (POA) and GHI values we’re receiving from the site are unusually low, while the other parameters are within expected ranges from 07/20 at 09:30. This suggests there may be an issue with the Pyranometer sensor at the site, as the settings on the PowerTrack appear to be configured correctly. I recommend sending a technician to the site to investigate and resolve this issue. 2. 6 modules are offline: Module 1.2.1 Module 1.2.13 Module 1.2.14 Module 1.11.5 Module 2.1.12 Module 2.1.16 3.Weather Station is showing erroneous (0 w/m^2) values at mid day from 07/20 at 09:30. | 1.SR105932 2.SR098241 3. SR105932 | 1.Pending 2.Pending 3.Pending | SR098241 | SR105932
X135 | NY | SOL-10425 | 17511.8125 | 22283.25 | -4771.4375 | -21.41% | 16253 | 1258.8125 | 7.745% | 1.Inverter 1 unit 1.3 having morning shading issue and inverter 2 having evening shading issues
X139 JHS 222 | NY | SOL-10426 | 26151.5164 | 27313.86 | -1162.3436 | -4.256% | 23270 | 2881.5164 | 12.38%
X140 | NY | SOL-10926 | 15207.125 | 12538.88 | 2668.245 | 21.28% | 13726 | 1481.125 | 10.79% | 1. Inverter 3 right unit tripped offline at 07:00 on 10/12 and back online at 13:00 on 10/12.
X166 | NY | SOL-10427 | 15296.6 | 17519.31 | -2222.71 | -12.69% | 14295 | 1001.6 | 7.007% | 1. Inverter 2 has afternoon shading.
Murphy | MN | SOL-10094 | 561770 | 691938.9 | -130168.9 | -18.81% | 663600.4 | -101830.4 | -15.35% | 1. Inverter 1 is producing at its half production through out the month. 1 IGBT needs replacement to get inverter fully functional. | 1. SR104403 | 1. pending
Terning | MN | SOL-10093 | 663260 | 709175.4 | -45915.4 | -6.474% | 637880.7 | 25379.3 | 3.979%
Boas Road 04 | NY | SOL-10908 | 0 | 0 | 0 |  | 240886.442 | -240886.442 | -100% | 1. Inverters 1 and 2 tripped offline at 08:50 on 10/16. Inverter 2 back online at 13:45 on 10/17, and Inverter 1 back online at 11:10 on 10/21. 2. Meter was not communicated for whole month. | 1. SR109570 2. SR098641 | 1. Closed 2. Pending | SR098641
Kelly Bridge Farm | NY | SOL-10911 | 109520 | N/A |  |  | 250638.93 | -141118.93 | -56.3% | 1. Site lost communication to DAS from 08/22, technician confirmed that the site is online onsite. Site regained it's communication at 10:20 on 10/16. Additionally, Inverters 21 to 27 and 30 to 33 have been offline since 10/17, and Inverter 13 has been offline since 10/18. | 1.SR106726 | 1. Pending
Pool Brook Road | NY | SOL-10909 | 225178 | 225180 | -2 | -0.0008882% | 241349.439 | -16171.439 | -6.7% | 1. The meter is showing a phase voltage imbalance of ~130V. Phases A & B are reading 270V and phase 3 is ~140V but is occasionally in-line with the other phases. meter voltage normal from 10/14. 2. Inverter 19 (4.3) tripped offline 14:40 on 9/28 and is reporting "Grid line voltage over limit" and back online at 09:40 on 10/14. | 1. SR107702 2. SR108697 | 1. Closed 2. Closed | SR108697
Sackett Lake | NY | SOL-10910 | 261090 | 0 | 261090 |  | 255140.835 | 5949.165 | 2.332% | 1. Weather station lost communication from 07/15. 2. IInverter 2 went offline at 07:00 on 10/01, reporting a “SE PHASE R BLOWER FAIL (98)” fault, and came back online at 11:05 on 10/02. It went offline again at 07:00 on 10/05 and was restored at 16:05 on 10/07. Once more, it went offline at 07:00 on 10/09; after a remote fan test and reset, the inverter came back online at 12:15 on the same day. The inverter went offline again at 07:00 on 10/17, reporting a “PHASE S BLOWER FAULT.” After the fan was replaced, the inverter was back online at 14:30 on 10/17. | 1.SR107603 2. SR108823, SR109086, SR109267, SR109625 | 1. Pending 2. Closed | SR108823 | SR109086 | SR109267 | SR109625
Burritt Road | NY | SOL-10913 | 266280 | 0 | 266280 |  | 240156.512 | 26123.488 | 10.88%
Villa Roma 1 | NY | SOL-10914 | 255964 | 0 | 255964 |  | 238394.14 | 17569.86 | 7.37% | 1. Expected energy values are reporting very low. Created a case #66639 with GPM, As per GPM the BOM has been frozen from 02/27. | 1. SR099403 | 1. Closed
Villa Roma 2 | NY | SOL-10915 | 236611 | N/A |  |  | 230513.342 | 6097.658 | 2.645%
Washington 1 | NY | SOL-10912 | 267410 | N/A |  |  | 235438.84 | 31971.16 | 13.58%
Washington 3 | NY | SOL-10828 | 0 | N/A |  |  | 287963.374 | -287963.374 | -100% | 1. The energy meter at Washington 3 is showing an issue with C-phase PT where the voltage measurement is drifting from 07/24, later site remain offline from 12:15 on 09/23 due to inverter to XFMR busbars had thermal damage and need to be replaced 2. POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1. SR105816 2.SR093024 | 1. Pending 2. Closed | SR093024
Washington 4 | NY | SOL-10829 | 311789 | N/A |  |  | 288480.551 | 23308.449 | 8.08% | 1. Inverter 2 tripped offline from 12:55 to 17:20 on 10/06. It tripped offline again at 09:40 on 10/08 after the technician replaced the SIM card. The inverter came back online at 13:05 on 10/08. 2. Inverter 2 went offline at 07:00 on 10/10, and Inverter 1 went offline at 11:50 on 10/10. After the technician reset both inverters, Inverter 2 back online at 11:10 on 10/14, and Inverter 1 back online at 13:40 on 10/14. 3. Inverter 2 tripped offline again at 07:00 on 10/15, reporting an "AC Contactor Fault." After the technician power-cycled the inverter, it came back online at 15:30 on 10/17. and tripping on and off throughout the month. 4. Inverter 1 tripped offline at 08:35 on 10/25, reporting an "AC Contactor Fault." After the technician replaced the AC filter fuse, it came back online at 10:20 on 10/28. | 1. SR108045 2. SR109320, SR109505 3. SR109505 4. SR109987 | 1. Closed 2. Closed 3. Closed 4. pending | SR109320 | SR109505 | SR109505 | SR109987
Big Tree | NY | SOL-10966 | 291940 | 290390 | 1550 | 0.5338% | 233651.8 | 58288.2 | 24.95%
Canoga | NY | SOL-10965 | 713910 | N/A |  |  | N/A |  |  | 1. Site lost communication to DAS at 02:00 from 10/19, technician confirmed that the site is online onsite. Site regained it's communication at 13:30 on 10/21.but data was not backfilled. | 1. SR109668 | 1. Completed
County Route 84 | NY | SOL-10967 | 745120 | 730020 | 15100 | 2.068% | 598634.4 | 146485.6 | 24.47% | 1. The site went offline at 08:10 on 10/03 due to USNE work at the site and came back online at 18:50 on 10/03. 2. The site went offline at 12:05 on 10/07 due to USNE performing meter testing and back online at 16:50 on 10/07. | 1. SR108636 2. SR107181 | 1. Closed 2. Pending | SR107181
Donati | NY | SOL-10968 | 275810 | 260880 | 14930 | 5.723% | 254656.474 | 21153.526 | 8.307% | 1. Site lost communication to DAS at 08:55 from 10/22, technician confirmed that the site is online onsite. Site regained it's communication at 02:05 on 10/23.but data was not backfilled. 2. All trackers were stuck from 13:00 on 09/04. After the technician replaced the RevPi, all racking began tracking as expected. | 1. SR109840 2. SR107506 | 1. Closed 2. Closed | SR107506
Henrietta | NY | SOL-10972 | 582710 | 572670 | 10040 | 1.753% | 501403.111 | 81306.889 | 16.22%
NY 70 | NY | SOL-10970 | 564940 | 561130 | 3810 | 0.679% | 612530.103 | -47590.103 | -7.769% | 1. 44 trackers were stuck since 08/29. After the technician installed a new motor, all trackers began tracking as expected. 2. Inverter 1 was derating by 70kw and inverter 3 is derating by 120kw due to inverter internal temperature throughout the month. 3. The site went offline at 07:45 on 10/08 due to a planned outage and back online at 14:25 on 10/08. and again tripped offline at 08:10 on 10/14 and back online at 12:20 on 10/14. 4. The site tripped offline at 13:50 on 10/15 and back online at 16:15 on 10/15 . | 1. SR106503 2. SR105774 3. SR109185 4. SR109523 | 1. Completed 2. pending 3. Closed 4. Closed | SR105774 | SR109185 | SR109523
Reid | NY | SOL-10991 | 583317.979 | 640176.3 | -56858.321 | -8.882% | 540119 | 43198.979 | 7.998% | 1. Inverter 19 was RMA'd on 09/15. After the technician replaced the power head, the inverter came back online at 13:30 on 10/22. 2. inverter 9 has derated to 100kW from 08/31 3. IInverter 29 tripped offline at 12:15 on 10/01. After the technician reset the main breaker, inverters back online at 13:30 on 10/22. The inverter tripped offline again at 12:30 on 10/27. 4. Inverter 32 tripped offline at 14:15 on 10/02. After the technician reset the main breaker, inverter back online at 13:30 on 10/22. 5. inverter 12 tripped offline at 14:00 on 10/15 and inverter is under RMA'd since 10/22. 6. Inverters 1 to 11, 13 to 18, and 20 tripped offline at 07:45 on 10/19, reporting "Grid Line Voltage Out of Range." After the technician reset the main breaker, all these inverters came back online at 11:30 on 10/22. 7. Inverter 23 tripped offline at 12:45 on 10/21, reporting "Grid Line Voltage Out of Range." After the technician reset the main breaker, the inverter back online at 13:30 on 10/22. | 1. SR108010 2. SR107331 3. SR108847, SR110116 4. SR108922 5. SR109568 6. SR109669 7. SR109669 | SR109669 | SR107331 | SR108847 | SR110116 | SR108922 | SR109568 | SR109669
Sangolqui | NY | SOL-10975 | 188210 | 129980 | 58230 | 44.8% | 245669.923 | -57459.923 | -23.39% | 1. 10 trackers were stuck from 09/22. On 10/08, 8 trackers resumed tracking, while 2 remained stuck. On 10/17, an additional tracker resumed tracking. TCU 255 is currently under RMA. 2. Meter have stopped communicating from 13:00 on 09/04 and resumed communication at 17:10 on 10/08. | 1.SR108338 2.SR107449 | 1. pending 2. Closed | SR107449
State Highway 17B | NY | SOL-10988 | 691270 | 678040 | 13230 | 1.951% | 625045.87 | 66224.13 | 10.6%
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 620433.191 | -620433.191 | -100% | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required. On 07/02 technician was after pulling event files from the SEL for analysis. The site remains offline. | 1. SR101820 | 1. Pending
West Creek | NY | SOL-10995 | 745120 | 709670 | 35450 | 4.995% | 587744.558 | 157375.442 | 26.78%
Wildflower | NY | SOL-10982 | 619955 | 592101 | 27854 | 4.704% | 627017.63 | -7062.63 | -1.126% | 1. Inverter 2 tripped offline at 09:25 on 09/30. After the technician replaced the DC contactor, inverter back online at 09:50 on 10/02. 2. Site went offline at 14:50 to 21:45 on 10/19. | 1. SR105775 2. SR109680 | 1. Closed 2. Closed | SR109680
Glen Mary 1 | NY | SOL-10993 | 743960 | 705610 | 38350 | 5.435% | 677715.864 | 66244.136 | 9.775%
Glen Mary 2 | NY | SOL-10994 | 322050 | 0 | 322050 |  | 284624.291 | 37425.709 | 13.15% | 1.POA Pyranometer UP irradiance reporting 0W/m2 since 08/18. Due to this expected energy values in monthly reports has been affected | 1.SR105649 | 1. Pending
Telegraph 1 | NY | SOL-11003 | 498030 | N/A |  |  | 443415.343 | 54614.657 | 12.32% | 1. The site went offline from 07:50 to 10:05 and again from 12:55 to 15:05 on 10/08. It tripped offline again at 08:20 on 10/14 and back online at 16:05 on 10/15. 2. The Site tripped offline at 14:00 on 10/20 and back online at 08:15 on 10/21. 3. The Site tripped offline from 10:10 to 12:10 and again from 13:15 to 16:50 on 10/24. | 1. SR109223 2. SR109728 3. SR109937 | 1. Closed 2. Closed 3. Closed | SR109728 | SR109937
Telegraph 2 | NY | SOL-11004 | 258440 | N/A |  |  | 229927.776 | 28512.224 | 12.4% | 1. The site went offline from 07:50 to 10:05 and again from 12:55 to 15:05 on 10/08. It tripped offline again at 08:20 on 10/14 and back online at 16:05 on 10/15. 2. Site was offline from 08:20 on 10/18 and back online at 02:05 on 10/19. 3. The Site tripped offline at 14:00 on 10/20 and back online at 08:15 on 10/21. 4. The Site tripped offline from 10:10 to 12:10 and again from 13:15 to 16:50 on 10/24. | 1. SR109224, SR109343 2. SR109343 3. SR109729 4. SR109938 | 1. Closed 2. Closed 3. Closed 4. Closed | SR109343 | SR109343 | SR109729 | SR109938
Cafferty Hill | NY | SOL-10996 | 729450 | 734715.78 | -5265.78 | -0.7167% | 608266.82 | 121183.18 | 19.92%
Dunkleman | NY | SOL-11008 | 788740 |  |  |  | 681852.792 | 106887.208 | 15.68% | 1. Pad 1 trackers 1, 63 ,109 are stuck at 0 deg and trackers 57, 119 are stuck at 255 deg. Additionally, Pad 2 trackers 43 , 114 are stuck at 0 deg and trackers 86, 124 are stuck at 255 deg from 09/07. After the technician installed the charger panel and node, the trackers have been tracking as expected since 10/27. | 1. SR107585 | 1. Completed
Route 19 1 | NY | SOL-11001 | 85381.1 | 84652.17 | 728.93 | 0.8611% | 249315.928 | -163934.828 | -65.75% | 1. Site lost communication to DAS from 09/16, technician confirmed that the site is online onsite. Site regained it's communication at 15:20 on 10/21.but data was not backfilled. 2. Site tripped offline at 10:10 to 12:10 on 10/24. | 1. SR108023, SR109726 2. SR109939 | 1. Completed 2. Closed | SR109726 | SR109939
Route 19 2 | NY | SOL-11002 | 688610 | 684290 | 4320 | 0.6313% | 630759.324 | 57850.676 | 9.172% | 1. The site went offline from 07:50 to 10:05 and again from 12:55 to 15:05 on 10/08. It tripped offline again at 08:20 on 10/14 and back online at 16:05 on 10/15. 2. The Site tripped offline at 14:00 on 10/20 and back online at 08:15 on 10/21. 3. The Site tripped offline from 10:10 to 12:10 and again from 13:15 to 16:50 on 10/24. | 1. SR109225 2. SR109727 3. SR109940 | 1. Closed 2. Closed 3. Closed | SR109727 | SR109940
Yellow Mills 1 | NY | SOL-11006 | 254545 | 251901 | 2644 | 1.05% | 228051.99 | 26493.01 | 11.62% | 1.Site is offline since 08:00 on 09/09 and back online at 15:25 on 10/03 | 1.SR107665 | 1.Completed
Yellow Mills 2 | NY | SOL-11005 | 160545 | N/A |  |  | 236588.974 | -76043.974 | -32.14% | 1. Meter is intermittently lossing communication since 09/04, production can be verified at inverter level. 2.Site is offline since 08:00 on 09/09 and back online at 15:25 on 10/03 | 1.SR107450 2.SR107667 | 1.Pending 2.Completed | SR107667
Yellow Mills 3 | NY | SOL-11007 | 240148 | 238031 | 2117 | 0.8894% | 225149.685 | 14998.315 | 6.661% | 1.Site is offline since 08:00 on 09/09 and back online at 15:25 on 10/03 | 1.SR107666 | 1.Completed
Catskill | NY | SOL-11021 | 520918 | 0 | 520918 |  | 472047.376 | 48870.624 | 10.35% | 1.Weather station is not communicating for whole month. 2. Site tripped offline at 02:30 on 10/20 and back online at 09:35 on 10/22 | 1.SR106739 2.SR109707 | 1.Pending 2.Completed | SR109707
Eddy Ridge | NY | SOL-11054 | 287315 | 284895 | 2420 | 0.8494% | 303475 | -16160 | -5.325% | 1. Trackers 1 through 49 have been stuck since 07/28. | 1.SR109604 | 1.Pending
Ridgeway #1 | NY | SOL-11018 | 787103 | 779465 | 7638 | 0.9799% | 635692.43 | 151410.57 | 23.82%
Rivard 1 | NY | SOL-11011 | 610444 | 639127 | -28683 | -4.488% | 507876.1 | 102567.9 | 20.2%
Rivard 2 | NY | SOL-11012 | 586380.92 | 579785.1 | 6595.82 | 1.138% | 484208.1 | 102172.82 | 21.1%
Ridgeway #2 | NY | SOL-11027 | 407899 | 404959 | 2940 | 0.726% | 329308.82 | 78590.18 | 23.87%
Spencer | NY | SOL-11017 | 796809.53 | 769468.24 | 27341.29 | 3.553% | 663665 | 133144.53 | 20.06% | 1.Meter lost communication at 10:05 on 10/23 and later site tripped offline at 13:50 on 10/25 and was back online at 08:10 on 10/27 | 1.SR109988 | 1.Completed
Reisender | NY | SOL-10886 | 278720 | 278640 | 80 | 0.02871% | 255766.956 | 22953.044 | 8.974%
Finney | NY | SOL-10999 | 493630 | 491240 | 2390 | 0.4865% | 617297.956 | -123667.956 | -20.03% | 1.Inverter 1 is offline from 09/10 and back online at 12:10 on 10/23 2. Tracker motor 1 has stuck from starting of the month has resolved at 11:10 on 10/28 | 1.SR107781 2.SR108776 | 1.Completed 2.Work in progress | SR108776
Davis Solar | NY | SOL-10958 | 294666 | 320015.6 | -25349.6 | -7.921% | 292669 | 1997 | 0.6823%
Genesee | NY | SOL-10951 | 494011.2 | 480122.63 | 13888.57 | 2.893% | 430901.366 | 63109.834 | 14.65% | 1. Trackers 23, 24, 33, 37, and 72 through 151 have been stuck since 06/02. Further troubleshooting is needed to program the gateways associated with NCU 2 | 1.SR102328 | 1.Closed
Landau I | NY | SOL-10891 | 275640 | N/A |  |  | 276046.645 | -406.645 | -0.1473%
Landau II | NY | SOL-10895 | 541660 | N/A |  |  | N/A |  |  | 1.Site tripped offline at 11:00 on 10/03 and back online at 11:55 on 10/04 2.Both inverters tripped offline from 12:00 to 13:30 on 10/14 | 1.SR108983 2.SR109461 | 1.Closed 2.Closed | SR109461
New Beginnings | NY | SOL-10890 | 72340 | 72320 | 20 | 0.02765% | 278665.034 | -206325.034 | -74.04% | 1.Inverter tripped offline at 09:00 on 10/01 and remained offline through out the month | 1.SR108827 | 1.Pending
Bullitt Farm Solar, LLC | NY | SOL-10998 | 648453.0652 | 714320.9 | -65867.8348 | -9.221% | 553668.3 | 94784.7652 | 17.12% | 1.Site tripped offline at 08:30 on 10/11 and back online at 11:15 on 10/12 | 1.SR109390 | 1.Closed
Brodhead Solar, LLC | NY | SOL-10899 | 320511 | 352139 | -31628 | -8.982% | 301492.2 | 19018.8 | 6.308%
Svenski | NY | SOL-10894 | 277486 | N/A |  |  | 272117.891 | 5368.109 | 1.973% | 1.Inverter started late at 10:15 and again tripped at 13:20 and back online at 15:50 by remote reset. 2.Inverter was offline from 10:40 to 13:30 on 10/07 as tech was onsite to replace the IGBTs in DPS 2. When he was working he found that the backplane between port 1 and 2 was faulty as well. The DPS will not function with the faulty backplane. SMA to order more parts and return to replace them. 3.Inverter was offline from 08:15 to 13:40 on 10/14 4.Inverter started late for production at 08:55 on 10/17 and again tripped offline at 10:00 and back online at 13:15 | 1.SR108808 2.SR106270 3.SR109462 4.SR109620 | 1.Closed 2.Pending 3.Closed 4.Closed | SR106270 | SR109462 | SR109620
Bantam | NY | SOL-10986 | 44580 | 469320 | -424740 | -90.5% | 590709.679 | -546129.679 | -92.45% | 1.The meter is missing phase A throughout the month, resulting in incomplete production data for both inverters. GC will review in 2026 2.Inverter 1 is back online at 15:05 on 10/21 3.Combiner box 02-09 is offline from 10:40 to 14:55 on 10/21 due to damaged module 4.NCU 1 is missing communications and tracker angles cannot be confirmed, NCU 4 SPC 1015 is stuck. | 1.SR108248 2.SR106176 3.SR109493 4.SR108120 | 1.Completed 2.Completed 3.Closed 4.Pending | SR106176 | SR109493 | SR108120
Bogart | NY | SOL-10887 | 289530 | 217280 | 72250 | 33.25% | 265631.136 | 23898.864 | 8.997%
Dubois | NY | SOL-10892 | 0 | 0 | 0 |  |  |  |  | 1. The site has been offline since 06:20 on 08/10 due to a transformer failure. | 1.SR106921 | 1.Pending
Salt Point | NY | SOL-10888 | 274500 | 266540 | 7960 | 2.986% | 263654.784 | 10845.216 | 4.113% | 1.Inverter module 1.4 has started for the production late at 12:00 on 10/17 and again offline whole day on 10/20 and again back online at 15:40 on 10/21 | 1.SR109619 | 1.Work in progress
Wheatland 2A | NY | SOL-10971 | 582600 | 580410 | 2190 | 0.3773% | 509021.597 | 73578.403 | 14.45% | 1.Site tripped offline at 09:35 on 10/19 and back online at 09:25 on 10/20 | 1.SR109675 | 1.Closed
Wheatland 2B | NY | SOL-10961 | 608220 | 605890 | 2330 | 0.3846% | 502325.851 | 105894.149 | 21.08% | 1.Site tripped offline at 09:35 on 10/19 and back online at 09:25 on 10/20 2.15 trackers are stuck: NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 | 1.SR109676 2.SR098860 | 1. Closed 2.Pending | SR098860
Brickchurch | NY | SOL-10889 | 55150 | 55040 | 110 | 0.1999% | 224030.441 | -168880.441 | -75.38% | 1.Inverter is back online at 12:55 on 10/22 2. 7 trackers 119,216,220,329, 338, 143, and 240 have seized slew drives. | 1.SR106501 2.SR109998 | 1.Closed 2.Pending | SR109998
McCarthy Solar | NY | SOL-10992 | 71190 | 0 | 71190 |  | 276553.03 | -205363.03 | -74.26% | 1. Inverter tripped offline at 17:45 on 10/05 and remained offline for rest of the month 2.Weather station is not communicating through out the month. | 1.SR109080 2.SR109079 | 1.Pending 2.Pending | SR109079
Costanza | NY | SOL-10907 | 304060 | 303984.25 | 75.75 | 0.02492% | 264626.717 | 39433.283 | 14.9% | 1. Site tripped offline at 04:28 and back online at 11:20 on 10/08 2. Site started for the production late at 11:45 on 10/17 3. Site tripped offline from 07:40 to 11:00 on 10/27 | 1.SR109187 2.SR109632 3.SR110017 | 1. Closed 2. Closed 3. Closed | SR109632 | SR110017
Lockenhurst Pond | NY | SOL-11000 | 318818 | 345078.9 | -26260.9 | -7.61% | 287759 | 31059 | 10.79% | 1. Site tripped offline from 00:14 and back online at 00:24 on 10/26. | 1.SR109990 | 1. Closed
Drinkwater | NY | SOL-10896 | 332380 | 331060 | 1320 | 0.3987% | 250301.454 | 82078.546 | 32.79%
Altamont | NY | SOL-11085 | 616338 | 665783.1 | -49445.1 | -7.427% | 420982.6 | 195355.4 | 46.4%
Krumkill North | NY | SOL-11086 | 515455 | 636140.4 | -120685.4 | -18.97% | 530658.8 | -15203.8 | -2.865% | 1.Inverter 2 having heavy shading isuue from afternoon to evening hours
Krumkill South | NY | SOL-11087 | 466720 | 508822.7 | -42102.7 | -8.275% | 416020 | 50700 | 12.19% | 1. Site tripped offline at 12:45 om 10/21 and later back online at 14:00 on 10/22 | 1.SR109794 | 1.Completed
X092 | NY | SOL-11189 | 12600.1 | 12960.93 | -360.83 | -2.784% | 12338 | 262.1 | 2.124%
X093 | NY | SOL-10932 | 9719.4062 | 9495.526 | 223.8803 | 2.358% | 8699 | 1020.4062 | 11.73%
X095 | NY | SOL-10929 | 12763.2656 | 14734.83 | -1971.5644 | -13.38% | 11699 | 1064.2656 | 9.097% | 1. Panel 1.0.7 124BD3FC-2C Panel 1.0.65 124CF1D2-21 Panel 1.0.84 124BDFF4-30 Panel 3.0.28 124A7869-3D Panel 3.0.31 124CF59F-F2 are offline later technician has replaced 4 optimizers on 10/01 | 1.SR095946 | 1.Completed
X181 | NY | SOL-10428 | 23583.7656 | 22296.69 | 1287.0756 | 5.772% | 21210 | 2373.7656 | 11.19%
X415 | NY | SOL-10429 | 14487.022 | 12761.31 | 1725.712 | 13.52% | 11741 | 2746.022 | 23.39%
K198 | NY | SOL-10930 | 11087.6875 | 11280 | -192.3125 | -1.705% | 10487 | 600.6875 | 5.728%
K203 | NY | SOL-11190 | 14366.1 | 12720.55 | 1645.55 | 12.94% | 13958 | 408.1 | 2.924%
K213 | NY | SOL-11191 | 15240.7 | 17509.86 | -2269.16 | -12.96% | 14843 | 397.7 | 2.679% | 1. Inverters 3 and 4 had heavy shading in morning.
K217 | NY | SOL-10933 | 7801.1172 | 8503.552 | -702.4348 | -8.26% | 7153 | 648.1172 | 9.061%
K307 | NY | SOL-10876 | 17488.0156 | 23418.64 | -5930.6244 | -25.32% | 14771 | 2717.0156 | 18.39% | 1. Inverter 2 experiencing minor shading issue
K610 | NY | SOL-11158 | 19819.6 | 20843.41 | -1023.81 | -4.912% | 18914 | 905.6 | 4.788%
M025 | NY | SOL-10392 | 16248.1953 | 20668.76 | -4420.5647 | -21.39% | 17635 | -1386.8047 | -7.864% | 1. Inverter 1 unit 1.5 was offline from 10/10 to end of the month. 2. Inverter 3 unit 3.1 was offline from 10/10 to end of the month. | 1. SR110156 2. SR110155 |  | SR110155
M028 | NY | SOL-10381 | 13964.5469 | 13884.17 | 80.3769 | 0.5789% | 12198 | 1766.5469 | 14.48%
Q030 | NY | SOL-10878 | 16894.7812 | 17490.12 | -595.3387 | -3.404% | 15243 | 1651.7812 | 10.84%
Q130 | NY | SOL-10877 | 8591.7109 | 9775.902 | -1184.1911 | -12.11% | 8293.744 | 297.9669 | 3.593% | 1. Inverter 1 unit 1.2 has heavy shading in the afternoon.
Q196 | NY | SOL-10879 | 11576.375 | 12951.76 | -1375.385 | -10.62% | 10846 | 730.375 | 6.734% | 1. Inverter 3 has heavy shading in morning and evening.
Q220 | NY | SOL-10873 | 11859.2031 | 17078.35 | -5219.1469 | -30.56% | 11811 | 48.2031 | 0.4081% | 1. The inverters are experiencing minor shading.
Q205 | NY | SOL-10922 | 17762.7188 | 22208.54 | -4445.8213 | -20.02% | 15510 | 2252.7188 | 14.52% | 1. Inverter 3 has afternoon shading.
Q400 | NY | SOL-10871 | 18383.7812 | N/A |  |  | 23463 | -5079.2188 | -21.65% | 1. Inverter 3 middle unit was back online at 14:00 on 10/20 and again tripped offline at 16:00 on 10/21, inverter 1 right unit is under underperforming by 10kW later from 10/20 inverter is producing as expected. | 1.SR107411 | 1.Pending
R003 | NY | SOL-10416 | 26215.7693 | 25469.34 | 746.4293 | 2.931% | 23556 | 2659.7693 | 11.29% | 1. Site was producing as expected
R007 | NY | SOL-10417 | 27178.7188 | 29091.52 | -1912.8013 | -6.575% | 29298.79 | -2120.0713 | -7.236% | 1. Inverter 1 unit 1.2 was offline since 09/16 and later technician has replaced the blown fuses on 10/22 | 1.SR109644 | 1.Completed
BK16 | NY | SOL-11093 | 26814.9062 | 27664.22 | -849.3138 | -3.07% | 25000 | 1814.9062 | 7.26%
Trenton - Trenton East | IL | SOL-11060 | 362392 | 347090.1 | 15301.9 | 4.409% | 334977 | 27415 | 8.184% | 1.Inverters 1 and 9 have had late starts each morning since 9/19 due to isolation faults. They self-resolve and come back online by 8 or 9 am each day. 2. Trackers A1 S 4, A1 S 16, A1 S 28, A1 S 41, A1 S 49, A1 S 68 are stuck since 10/10 3. Inverters 1, 7, 8 are offline from 11:00 to 17:30 on 10/22 | 1.SR108394 2.SR109330 3.SR109858 | 1.Pending 2.Pending 3.Closed | SR109330 | SR109858
Trenton - Trenton West | IL | SOL-11061 | 273805 | 254733.5 | 19071.5 | 7.487% | 339504 | -65699 | -19.35% | 1. Inverter 11 derating at 75kW from 10/01 and resolved on 10/17 2. Inverter 6 has regained its communication at 11:45 on 10/17 but energy has not backfilled. 3.Inverter 16 tripped offline on 10/2/25 at 16:37 and back online at 15:15 on 10/16 4.Inverter 7 is back online at 09:30 on 10/01, Inverter 14 is back online at 09:00 on 10/02 | 1.SR108936 2.SR108396 3.SR108982 4.SR107059 | 1.Closed 2.Closed 3.Closed 4.Closed | SR108396 | SR108982 | SR107059
Dakota - Dakota Solar 1 | IL | SOL-11113 | 341684 | 335706.8 | 5977.2 | 1.78% | 265320 | 76364 | 28.78% | 1. The site tripped offline at 14:15 on 10/14 and back online at 16:45 on 10/14. 2. Tracker TCU 1, 2, 7, 30, 34, 55, 62, 70 and 85 are stuck since 10/14. | 1. SR108972 2. SR105922 | 1. Closed 2. Pending | SR105922
X018 | NY | SOL-10418 | 13335.1875 | 13788.46 | -453.2725 | -3.287% | 13680 | -344.8125 | -2.521%
Janiak Solar | NY | SOL-10898 | 321409 | 332661.2 | -11252.2 | -3.382% | 279683 | 41726 | 14.92% | 1. The site tripped offline at 11:45 on 10/20 and later auto-reclosed, back online at 12:00 on 10/20. | 1. SR109734 | 1. Closed
County Route 11B | NY | SOL-10983 | 776669.75 | 772546.88 | 4122.87 | 0.5337% | N/A |  |  | 1. Trackers 93 through 190 have been stuck since 10/20 and later resumed tracking from 10/22. | 1. SR109715 | 1. Pending
Barone | NY | SOL-11034 | 447305 | 443968 | 3337 | 0.7516% | 409940 | 37365 | 9.115% | 1. The site tripped offline at 10:00 on 10/06 and later auto-reclosed, back online at 16:45 on 10/06. 1. The site tripped offline at 09:45 on 10/07 and back online at 09:45 on 10/08. | 1. SR109096 2. SR109144 | 1. Closed 2. Closed | SR109144
Cedarville | IL | SOL-11069 | 287282 | 286434.4 | 847.6 | 0.2959% | 303211.8 | -15929.8 | -5.254% | 1. Trackers 50 and 61 have been stuck since 10/14. 2. Inverter 7 underperforming by 14kW from 9/24 (2 strings). Inverter 10 underperforming by 14kW from 8/28. | 1. SR109450 2. SR109452 | 1. Pending 2. Pending | SR109452
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | N/A |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | 1. Pending | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 675090 | 674985 | 105 | 0.01556% | N/A |  |  | 1. All trackers were stuck between 53° and 55° on 10/27 and later self-resolved, back online at 13:30 on 10/27. | 1. SR110025 | 1. Completed
Trinity - Freeport | IL | SOL-11057 | 320506 | 359435.7 | -38929.7 | -10.83% | 296864 | 23642 | 7.964% | 1. Currently, tracker TCUs 3, 19, 39, 50, 60, 62, and 64 have been stuck since 10/14. After a remote reset, TCUs 3, 62, and 64 resumed tracking, while the remaining TCUs are still stuck. 2.Inverter 2 is derating by anywhere from 5 kW to ~20 kW in the afternoons. Issue looks to have started on 03/28. Doesn't look like shading should be an issue here, and we do not have data from this time last year. No alerts present. | 1. SR098066 2. SR099545 | 1. Pending 2. Pending | SR099545
Ransom | NY | SOL-11157 | 659665 | 654273 | 5392 | 0.8241% | N/A |  |  | 1. The site tripped offline at 10:00 on 10/06 and back online at 13:45 on 10/06. 2. Trackers E-098, 168, & 169 are stuced since 10/10 and later resumed tracking from 10/16. 3. The site was offline at 10:15 on 10/19 and back online at 19:20 on 10/21. | 1. SR109097 2. SR109353 3. SR109692 | 1. Closed 2. Closed 3. Closed | SR109353 | SR109692
Horseheads - Wedge | NY | SOL-11160 | 412424 | 405092 | 7332 | 1.81% | N/A |  |  | 1. Trackers 8 and 9 had been deviating since 07/29 and resumed normal tracking on 10/01. 2. Tracker 33 getting stucked since 10/16. | 1. SR105284 2. SR109592 | 1. Closed 2. Pending | SR109592
Otisville - Shoddy Hollow | NY | SOL-11185 | 703087 | 678670 | 24417 | 3.598% | N/A |  |  | 1. The site tripped offline at 09:30 on 10/10 and back online at 15:45 on 10/13. | 1. SR109335 | 1. Closed
Wellsville - Chenunda Creek | NY | SOL-11187 | 349774 | 343685 | 6089 | 1.772% | N/A |  |  | 1. The site was taken offline from 10:55 to 11:25 on 10/03 as EV Solar was on-site to replace a UPS device. 2. The site was taken offline from 07:00 to 11:25 on 10/07 due to a planned outage. 3. The site was taken offline from 12:35 to 13:25 on 10/08 as EV Solar was on-site to install a UPS device. 4. he site was taken offline from 10:00 to 16:05 on 10/10 due to utility works at the site | 1. SR108961 2. SR109101 3. SR109195 4. SR109326 | 1. Closed 2. Closed 3. Closed 4. Closed | SR109101 | SR109195 | SR109326
DC: Washington - Essex Condominium | DC | SOL-10036 | 2803 | 3602.191 | -799.191 | -22.19% | 3707.346 | -904.346 | -24.39% | 1. The site is performing as expected, but the expected and forecasted values are high. A similar event was observed over the past two years.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 4217 | 10946.41 | -6729.41 | -61.48% | 11602.42 | -7385.42 | -63.65% | 1. Inverter 2 was offline at 07:00 on 10/11. 2. The meter has been communicating intermittently throughout the month. | 1. SR109524 2. SR100771 | 1. Pending 2. Closed | SR100771
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 12446 | 9834.705 | 2611.295 | 26.55% | 11596.21 | 849.79 | 7.328%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 302465 | 363338.3 | -60873.3 | -16.75% | 346777.8 | -44312.8 | -12.78% | 1. The site tripped offline at 10:00 on 10/11 due to the SEL relay being in an open state. After the EPC reset the SEL relay, the site came back online at 16:00 on 10/11. 2. All trackers are strucked since 09/27 after remote reset all trackers are back online at 10/06. 3. Tracker TCU 11 had been intermittently getting stuck since 10/07. The EPC found a loose fuse and tightened it, after which the tracker returned to normal operation. 4. The site went offline at 07:00 on 10/18 and back online at 14:20 on 10/18. 5. Inverter 15 went offline at 07:00 on 10/18 and later self-resolved, back online at 17:00 on 10/18. 6. The site tripped offline at 07:15 on 10/19 due to the SEL relay being in an open state. After the EPC remotely closed the relay, the site came back online at 11:45 on 10/20. 7. All trackers have been intermittently getting stuck since 10/21/25 and reporting snow alarms. After the technician cleared the snow, all trackers resumed normal operation. 8. The site tripped offline at 10:30 on 10/26. After a remote reset, the site came back online at 16:45 on 10/26. | 1. SR108678 2. SR108984 3. SR109158 4. SR109664 5. SR109665 6. SR109681 7. SR109851 8. SR109995 | SR109995 | SR108984 | SR109158 | SR109664 | SR109665 | SR109681 | SR109851
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 637027.7765 | 664991.4 | -27963.6235 | -4.205% | 803920 | -166892.2235 | -20.76% | 1. Pad 2 inverters (2.01 through 2.20) tripped offline at 09:15 on 09/26. Pad 1 inverters (1.01 through 1.20) tripped offline at 07:45 on 09/27, reporting the fault “Grid Phase Voltage Out of Range – GridV.OutLim.” Additionally, the site went offline on 09/30 due to an infestation in the main breaker and was brought back online at 09:30 on 10/08. | 1. SR108599 | 1. Closed
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 357255 | 0 | 357255 |  | 326891 | 30364 | 9.289% | 1. The weather station stopped communicating at 08:00 on 09/22. 2. The site tripped offline at 09:30 on 10/22 due to SEL relay open and also All inverters reporting fault grid phase voltage out of range - GridV.OutLim and later site is back online at 18:20 on 10/22. | 1. SR108392 2. SR109809 | 1. Pending 2. Closed | SR109809
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 477254.77 | 688404 | -211149.23 | -30.67% | 612495 | -135240.23 | -22.08% | 1. Site was offline from 02:15 on 10/23 to 13:00 on 10/29. | 1. SR110198 | 1. Closed
NY: Whitesville - Independence North | NY | SOL-11186 | 486766 | N/A |  |  | N/A |  |  | 1. Site tripped offline at 09:05 to 11:30 on 10/07 due to planned outage. 2. Site tripped offline at 09:10 to 16:05 on 10/10 due to repairs at the site. 3. Site tripped offline at 09:10 to 16:25 on 10/13 and later self reolved. | 1. SR109102, SR109103 2. SR109325 3. SR109403 | 1. Closed 2. Closed 3. Closed | SR109103 | SR109325 | SR109403
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 356324 | 371592.7 | -15268.7 | -4.109% | 346960 | 9364 | 2.699% | 1. Trackers TCU 41 Strucked on 10/07. | 1. SR109160 | 1. Pending
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 354185 | 443551.4 | -89366.4 | -20.15% | 325794 | 28391 | 8.714% | 1. inverter 4 is underperforming by 10 kW from 10/07. | 1. SR109156 | 1. Pending
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 312636 | 501258 | -188622 | -37.63% | 284225 | 28411 | 9.996% | 1. Trackers TCU 39 Strucked on 10/07 and TCU 33 and 66 strucked on 10/14. | 1. SR109157 | 1. Pending
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 344052 | 385536 | -41484 | -10.76% | 291184 | 52868 | 18.16% | 1. The site tripped offline from 10:30 to 15:15 on 10/16 due to car on pole. | 1. SR109198, SR109525 SR109585 | 1. Closed | SR109525 | SR109585
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 2002613 | N/A |  |  | N/A
IL: Hillsboro - Anacott (PW) | IL
IL: Manhattan - Gougar (PW) | IL

## Nov
Generate Capital |  |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  |  | 19972387.8276 | 16030213.194 | 3942174.6336 | 24.59% | 22096297.204 | -2123909.3764 | -9.612% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
K026 | NY | SOL-10356 | 9316 | 16506.62 | -7190.62 | -43.56% | 12235.73 | -2919.73 | -23.86% | 1. Meter B phase currents dropped to Zero whole month. Need to replace CT's | 1. SR107464 | 1.Pending
K041 | NY | SOL-10357 | 10472.2188 | 12670.92 | -2198.7013 | -17.35% | 11963 | -1490.7812 | -12.46% | 1. Inverter 2 has afternoon shading.
K043 | NY | SOL-10358 | 12557.7794 | 14003 | -1445.2206 | -10.32% | 2700 | 9857.7794 | 365.1% | 1. Estimated values are low in AE we have also verified the file which was given by GC
K058 | NY | SOL-10360 | 10157.75 | 11357.2 | -1199.45 | -10.56% | 9904.477 | 253.273 | 2.557%
K115 | NY | SOL-10361 | 5727.542 | 6963.147 | -1235.605 | -17.74% | 6362.231 | -634.689 | -9.976% | 1. Inverter 1 middle unit was offline on 11/25 | 1.SR111795 | 1.New
K152 | NY | SOL-10362 | 3772.5938 | 4200.513 | -427.9192 | -10.19% | 3871 | -98.4062 | -2.542%
K166 | NY | SOL-10363 | 11908.625 | 15709.6 | -3800.975 | -24.2% | 13335.22 | -1426.595 | -10.7% | 1.3 optimizers are offline: 2.0.160, 3.0.17, 3.0.33 | 1.SR095666 | 1. Pending
K206 | NY | SOL-10927 | 7900.2188 | 7300.277 | 599.9417 | 8.218% | 8303 | -402.7812 | -4.851%
K251 | NY | SOL-10365 | 9121.5625 | 0 | 9121.5625 |  | 9176.452 | -54.8895 | -0.5982% | 1. Weather station stopped communicating on 11/22 at 07:00. replacement POA. | 1. SR093633 | 1. Pending
K269 | NY | SOL-10366 | 8324.0988 | 10481.22 | -2157.1212 | -20.58% | 9295.581 | -971.4822 | -10.45% | 1.Inverters producing as expected and expected value and forecasted energy values diffrence.
K273 | NY | SOL-10367 | 8721.8125 | 0 | 8721.8125 |  | 10468 | -1746.1875 | -16.68% | 1. 26 optimizers are down for roof repair. 2. Weather station stopped communicating since 06/14/24. | 1.SR093924 2. SR086842 | 1. Pending 2. Closed | SR086842
K287 | NY | SOL-10919 | 7501.25 | 7166.586 | 334.664 | 4.67% | 8320 | -818.75 | -9.841% | 1. Actual vs expected delta is showing 16% due to expected energy recording low possibly due to data glitch (similar event observe last years).
K298 | NY | SOL-10368 | 6919.5 | 9283.998 | -2364.498 | -25.47% | 7584 | -664.5 | -8.762%
K335 | NY | SOL-10370 | 7915.125 | 9866.188 | -1951.063 | -19.78% | 8935 | -1019.875 | -11.41% | 1. Inverter 1 has minor shading issue.
K345 | NY | SOL-10920 | 9400.4062 | 6990.002 | 2410.4042 | 34.48% | 8732 | 668.4062 | 7.655% | 1. Inverter 3 is underproducing due to unit(7E9C82CA) underproducing from 13:30 on 06/20 and reporting "external fan" fault. 2. Actual vs expected delta is showing 34% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1. SR103259 | 1. Closed
K445 | NY | SOL-10373 | 6804.495 | 9924.432 | -3119.937 | -31.44% | 8343.926 | -1539.431 | -18.45% | 1. Inverter 1, Unit 12, was offline from 10/01 to 10/16. Two strings were isolated from Unit 1.2 on 10/16. The technician re-landed the strings and paired the inverter, and the inverters units have been producing as expected since 11/15. | 1. PM8307, SR109623 | 1. Closed
K495 | NY | SOL-10374 | 33907.5 | 38076.52 | -4169.02 | -10.95% | 48974.71 | -15067.21 | -30.77% | 1. Inverter 12 tripped offline at 17:00 on 10/20. After the technician power-cycled the inverter, it came back online at 08:00 on 11/20. | 1. SR110132 | 1. Closed
M020 | NY | SOL-10380 | 8519.625 | 9212.245 | -692.62 | -7.518% | 10258 | -1738.375 | -16.95% | 1.Site was offline from 15:15 on 11/12 and back online at 12:15 on 11/14 | 1.SR111002 | 1.Closed
M092 | NY | SOL-10383 | 8241.1875 | 9823.6 | -1582.4125 | -16.11% | 9410.011 | -1168.8235 | -12.42%
M143 | NY | SOL-10384 | 9215.25 | 10648.48 | -1433.23 | -13.46% | 10083.92 | -868.67 | -8.614%
M144 | NY | SOL-10385 | 13733.25 | 16821.61 | -3088.36 | -18.36% | 23182.88 | -9449.63 | -40.76% | 1. Inverter 2 has afternoon shading.
M167 | NY | SOL-10386 | 8672.6562 | 8439.219 | 233.4372 | 2.766% | 10189.85 | -1517.1938 | -14.89% | 1. Actual vs forcasted delta is showing 15% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
M188 | NY | SOL-10387 | 7381.3438 | 8688.007 | -1306.6632 | -15.04% | 12627.36 | -5246.0163 | -41.54% | 1. Inverter 2 has morning shading.
EMHC | NY | SOL-10351 | 2700.75 | 2130.825 | 569.925 | 26.75% | 2751.524 | -50.774 | -1.845% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline | 1. SR093236 | 1.Pending
Q008 | NY | SOL-10397 | 11787.4688 | 13574.13 | -1786.6612 | -13.16% | 12978 | -1190.5312 | -9.173%
Q018 | NY | SOL-10398 | 8243.5625 | 8976.817 | -733.2545 | -8.168% | 7162.349 | 1081.2135 | 15.1%
Q021 | NY | SOL-10399 | 6298.3125 | 7577.821 | -1279.5085 | -16.88% | 5762.361 | 535.9515 | 9.301%
Q025 | NY | SOL-10400 | 11030 | 11646.7 | -616.7 | -5.295% | 7509 | 3521 | 46.89% | 1. Actual vs Forcasted delta is showing 47% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  |  |  |  | 1. Home run Solar shut off the site at 08:30am on 09/22 to perform roof repairs. | 1. SR102529 | 1. Pending
Q115 | NY | SOL-10872 | 6806.0625 | 10653.71 | -3847.6475 | -36.12% | 8877.85 | -2071.7875 | -23.34% | 1. Inverter 1’s left unit went offline on 10/29 and remained offline for the rest of the month. | 1. SR110250 | 1. Pending
Q139 | NY | SOL-10403 | 5406.25 | 5897.586 | -491.336 | -8.331% | 5595 | -188.75 | -3.374% | 1. Some optimizers with production issues 1264FFBB-30 - Half production 12639DA9-BB - Half production | 1. SR088282 | 1. Pending
Q157 | NY | SOL-10404 | 9578.4375 | 12694.15 | -3115.7125 | -24.54% | 9618.426 | -39.9885 | -0.4157% | 1. Inverter 2 expericing afternoon shading issue
Q192 | NY | SOL-10406 | 10982.875 | 17397.17 | -6414.295 | -36.87% | 14869.81 | -3886.935 | -26.14% | 1. Inverter 2, unit 2.3, was being RMA’d, and Inverter 2 went offline at 13:00 on 11/06. 2. Inverter 3 middle unit tripped offline at 12:15 on 11/17. | 1. SR108939, SR110231 2. SR112049 | 1. Closed 2. New | SR110231 | SR112049
Q210 | NY | SOL-10407 | 12714.25 | 12657.88 | 56.37 | 0.4453% | 12454 | 260.25 | 2.09%
Q229 | NY | SOL-10408 | 4777.6875 | 6275.149 | -1497.4615 | -23.86% | 4177.438 | 600.2495 | 14.37% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1. SR088813 | 1. Pending
Q231 | NY | SOL-10870 | 19893 | 26623.33 | -6730.33 | -25.28% | 20029 | -136 | -0.679% | 1.Inverter 1 has shading issue.
Q405 | NY | SOL-10409 | 23775.75 | 27520.16 | -3744.41 | -13.61% | 22257.55 | 1518.2 | 6.821% | 1. 4 Inverter modules are offline Module 1.0.64 Module 4.0.39 3.0.20 1.0.64 | 1. SR093324 | 1. Pending
Q435 | NY | SOL-10923 | 30844.5 | 22683.27 | 8161.23 | 35.98% | 30747 | 97.5 | 0.3171% | 1. Weather station has morning shading due to that expected values are low.
Q485 | NY | SOL-10869 | 24169.625 | 24389.8 | -220.175 | -0.9027% | 29073.75 | -4904.125 | -16.87% | 1. Inverter 1’s right unit went offline at 08:00 on 10/31 and remained offline throughout the month. | 1. SR111880 | 1. New
Q490 | NY | SOL-10411 | 18665.25 | 0 | 18665.25 |  | 18472.73 | 192.52 | 1.042% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1. SR093326, SR110229 | 1. Pending | SR110229
Q620 | NY | SOL-10867 | 28964.5 | 30478.66 | -1514.16 | -4.968% | 32340.4 | -3375.9 | -10.44% | 1.Inverter modules 3.0.144 and 5.0.100 are offline 4.0.66 - 30513B3F-FB - half production because split between 4 modules | 1. SR093327 | 1.Pending
QMOA | NY | SOL-10415 | 2746.6 | 0 | 2746.6 |  | 3040.201 | -293.601 | -9.657%
X024 | NY | SOL-10419 | 10428.5938 | 12244.82 | -1816.2262 | -14.83% | 9503 | 925.5938 | 9.74% | 1.Inverter 2 having heavy shading isuue in mid day hours
X026 | NY | SOL-10420 | 8707.6 | 10105.83 | -1398.23 | -13.84% | 12253.37 | -3545.77 | -28.94% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1. SR109950 | 1.Pending
X090 | NY | SOL-10925 | 5888.9688 | 6658.377 | -769.4083 | -11.56% | 8527 | -2638.0312 | -30.94% | 1. Inverter 1 unit 1.1 went offline at 09:30 on 09/27, and unit 1.2 went offline at 17:00 on 10/19. After the technician replaced the blown fuses in the inverter powerhead, the inverter began producing as expected. | 1. SR110586 | 1. Closed
X117 | NY | SOL-10422 | 6321.6 | 8474.138 | -2152.538 | -25.4% | 7106.625 | -785.025 | -11.05% | 1. Inverter 1 having morning shading issue.
X125 | NY | SOL-10423 | 13119.9375 | 15051.95 | -1932.0125 | -12.84% | 14143.7 | -1023.7625 | -7.238% | 1.Inverter 1 unit 1.2 having evening shading issue
X134 | NY | SOL-10424 | 11442.1875 | 14878.43 | -3436.2425 | -23.1% | 12502 | -1059.8125 | -8.477% | 1.During peak hours, the Plane of Array (POA) and GHI values we’re receiving from the site are unusually low, while the other parameters are within expected ranges from 07/20 at 09:30. This suggests there may be an issue with the Pyranometer sensor at the site, as the settings on the PowerTrack appear to be configured correctly. I recommend sending a technician to the site to investigate and resolve this issue. 2. 6 modules are offline: Module 1.2.1 Module 1.2.13 Module 1.2.14 Module 1.11.5 Module 2.1.12 Module 2.1.16 3.Weather Station is showing erroneous (0 w/m^2) values at mid day from 07/20 at 09:30. | 1. SR105932 2. SR098241 3. SR105932 | 1.Pending 2.Pending 3.Pending | SR098241 | SR105932
X135 | NY | SOL-10425 | 10523.0625 | 13728.07 | -3205.0075 | -23.35% | 11620 | -1096.9375 | -9.44% | 1.Inverter 1 unit 1.3 having morning shading issue and inverter 2 having evening shading issues
X139 JHS 222 | NY | SOL-10426 | 15036.7066 | 15046.13 | -9.4234 | -0.06263% | 15018 | 18.7066 | 0.1246%
X140 | NY | SOL-10926 | 9349.5762 | 7738.455 | 1611.1212 | 20.82% | 9515 | -165.4238 | -1.739%
X166 | NY | SOL-10427 | 8907.5 | 11172.59 | -2265.09 | -20.27% | 9160 | -252.5 | -2.757% | 1. Inverter 2 has afternoon shading.
Murphy | MN | SOL-10094 | 400900 | 526376.4 | -125476.4 | -23.84% | 491188.9 | -90288.9 | -18.38% | 1. Inverter 1 is producing at its half production through out the month. 1 IGBT needs replacement to get inverter fully functional. | 1. SR104403 | 1. pending
Terning | MN | SOL-10093 | 423557.4826 | 495028.5 | -71471.0174 | -14.44% | 455541.5 | -31984.0174 | -7.021% | 1. Inverter 2 derating by 150kW from 10/17/25. 2. The site went offline at 14:00 on 11/04 and came back online at 08:00 on 11/05 while the technician was onsite performing PM inspections. | 1. SR109775 2. PM1971 | 1. pending
Boas Road 04 | NY | SOL-10908 | 39623 | 39623 | 0 | 0% | 142386.318 | -102763.318 | -72.17% | 1. The meter lost communication at 14:05 on 03/16. After the technician re-installed and re-rigged the meter, it was back online at 16:50 on 11/19. | 1. SR098641 | 1. Closed
Kelly Bridge Farm | NY | SOL-10911 | 132198 | N/A |  |  | 174569.527 | -42371.527 | -24.27% | 1. Inverters 21 to 27 and 30 to 33 have been offline since 10/17, and Inverter 13 has been offline since 10/18. After the technician replaced the fuses, all these inverters were back online at 11:20 on 11/20. | 1. SR106726, SR110996 | 1. Closed | SR110996
Pool Brook Road | NY | SOL-10909 | 105643 | 105644 | -1 | -0.0009466% | 163526.559 | -57883.559 | -35.4% | 1. The Production was low on 11/12, 11/17, 11/18, 11/29, and 11/30 due to low irradiance.
Sackett Lake | NY | SOL-10910 | 157875 | 0 | 157875 |  | 188154.052 | -30279.052 | -16.09% | 1. Weather station lost communication from 07/15. | 1.SR107603 | 1. Denied
Burritt Road | NY | SOL-10913 | 116460 | 0 | 116460 |  | 142556.073 | -26096.073 | -18.31% | 1. The Production was low on 11/13, 11/17, 11/18, 11/29, and 11/30 due to low irradiance.
Villa Roma 1 | NY | SOL-10914 | 125785 | 0 | 125785 |  | 128062.968 | -2277.968 | -1.779%
Villa Roma 2 | NY | SOL-10915 | 118014 | N/A |  |  | 124122.569 | -6108.569 | -4.921%
Washington 1 | NY | SOL-10912 | 117260 | N/A |  |  | 137913.965 | -20653.965 | -14.98% | 1. The Production was low on 11/05, 11/09, 11/10 and 11/16 due to low irradiance.
Washington 3 | NY | SOL-10828 | 0 | N/A |  |  | 168483.581 | -168483.581 | -100% | 1. The energy meter at Washington 3 is showing an issue with C-phase PT where the voltage measurement is drifting from 07/24, later site remain offline from 12:15 on 09/23 due to inverter to XFMR busbars had thermal damage and need to be replaced 2. POA sensor continues to read inaccurately from 10/2 at 11:25am. Tech verified connections by testing both old and new sensors, with irradiance around 1 W/m². The original sensor was last calibrated in May 2024. GPM recommends replacing the run cable to the DAS to improve accuracy. | 1. SR105816 2.SR093024 | 1. Pending 2. Closed | SR093024
Washington 4 | NY | SOL-10829 | 141649 | N/A |  |  | 168883.531 | -27234.531 | -16.13% | 1. Inverter 2 tripped offline at 07:00 on 11/01, reporting an "AC Contactor Fault." After the technician Power cycling, it came back online at 11:40 on 11/03. and again tripped offline at 07:00 on 11/10 and back online at 14:55 on 11/14. 2. The site was taken offline from 12:05 to 13:25 on 11/04 while the technician was onsite troubleshooting Inverter 2. | 1. SR110488, SR111045 2. SR111045 | 1. Closed 2. Closed | SR111045 | SR111045
Big Tree | NY | SOL-10966 | 121800 | 120500 | 1300 | 1.079% | 133656.75 | -11856.75 | -8.871% | 1. The site tripped offline at 22:15 on 11/15 and later self-resolved, back online at 11:45 on 11/16. | 1. SR111167 | 1. Closed
Canoga | NY | SOL-10965 | 218690 | N/A |  |  | 368801.4 | -150111.4 | -40.7% | 1. Site stopped communication to DAS at 02:00 on 11/20. | 1. SR111378 | 1. Pending
County Route 84 | NY | SOL-10967 | 333660 | 330830 | 2830 | 0.8554% | 441192.042 | -107532.042 | -24.37% | 1. The site tripped offline at 14:00 on 11/05 and back online at 07:00 on 11/06. 2. The site was taken offline from 09:45 to 14:50 on 11/21 while the technician was onsite. Inverters 3 and 4 were taken offline and remained offline throughout the month. The site was taken offline again from 09:50 to 12:20 on 11/26 while the technician was onsite cleaning out a rodent infestation in Inverters 3 and 4. | 1. SR110681 2. SR105508 | 1. Closed 2. Pending | SR105508
Donati | NY | SOL-10968 | 121660 | 115500 | 6160 | 5.333% | 143677.777 | -22017.777 | -15.32% | 1. rackers A7, A10, F27, F33, G13, and G14 have been out of service since 10/23. These trackers need to be replaced and are pending replacement. 2. Site lost communication to DAS at 11:35 from 11/29, Site regained it's communication at 02:05 on 11/30.but data was not backfilled. | 1. SR109834 | 1. Pending
Henrietta | NY | SOL-10972 | 228280 | 223860 | 4420 | 1.974% | 274835.89 | -46555.89 | -16.94% | 1. Gateway 5 missing 3 trackers 6, 14 and 15 were strucked since 08/20. | 1. SR106622,SR110008 | 1. Pending | SR110008
NY 70 | NY | SOL-10970 | 200190 | 197550 | 2640 | 1.336% | 364301.52 | -164111.52 | -45.05% | 1. The site tripped offline at 20:05 on 11/16. After the technician replaced the switchgear and SEL, the site came back online at 10:05 on 11/19. 2. The site tripped offline at 09:30 on 11/23. After the technician reset the and SEL, the site came back online at 10:00 on 11/25. 3. The site tripped offline at 18:55 on 11/28 and later self-resolved. The site came back online at 16:35 on 11/29. | 1. SR111199 2. SR111498 3. SR111826 | 1. Closed 2. Closed 3. Closed | SR111498 | SR111826
Reid | NY | SOL-10991 | 257503.074 | 278209 | -20705.926 | -7.443% | 315841 | -58337.926 | -18.47% | 1. Inverter 12 tripped offline at 14:00 on 10/15. After the technician replaced the parts, the inverter came back online at 11:15 on 11/05. 2. Inverter 29 tripped offline at 12:30 on 10/27 and reported ‘Grid Phase Voltage Out of Range.’ After the technician reset the breaker, the inverter came back online at 12:15 on 11/05. | 1. SR109568 2. SR108847, SR110116 | 1. Closed 2. Closed | SR108847 | SR110116
Sangolqui | NY | SOL-10975 | 123510 | 53100 | 70410 | 132.6% | 139173.831 | -15663.831 | -11.25% | 1. 6 trackers were stuck from 10/17, an additional tracker resumed tracking. TCU 255 is currently under RMA. 2. Site lost communication to DAS at 11:40 on 11/20, Site regained it's communication at 22:05 on 11/20. 3.Weather station regained its communication at 14:45 on 11/30 | 1. SR108338 2. SR111393 | 1. Denied 2. Closed | SR111393
State Highway 17B | NY | SOL-10988 | 362770 | 359540 | 3230 | 0.8984% | 359873.2 | 2896.8 | 0.805%
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 439104.688 | -439104.688 | -100% | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required. On 07/02 technician was after pulling event files from the SEL for analysis. The site remains offline. | 1. SR101820 | 1. Pending
West Creek | NY | SOL-10995 | 375260 | 371590 | 3670 | 0.9876% | 413949.43 | -38689.43 | -9.346%
Wildflower | NY | SOL-10982 | 225943 | 142367 | 83576 | 58.7% | 429842.2 | -203899.2 | -47.44% | 1. POA Pyranometer UP stopped communicating from 11/16 and POA Pyranometer DOWN stopped communicating since past years | 1.SR112202 | 1. New
Glen Mary 1 | NY | SOL-10993 | 234530 | 231500 | 3030 | 1.309% | 460387.386 | -225857.386 | -49.06% | 1. Inverter 1 has been experiencing multiple trip events since 11:25 on 11/18. Additionally, the inverter tripped offline at 09:30 on 11/19. 2. The site went offline at 12:30 on 11/20 due to an MV issue and remained offline throughout the month. | 1. SR111271 2. SR111271 | 1. Pending 2. Pending | SR111271
Glen Mary 2 | NY | SOL-10994 | 179680 | 0 | 179680 |  | 190921.348 | -11241.348 | -5.888% | 1.POA Pyranometer UP irradiance reporting 0W/m2 since 08/18. Due to this expected energy values in monthly reports has been affected | 1.SR105649 | 1.Deined
Telegraph 1 | NY | SOL-11003 | 231050 | N/A |  |  | 268935.197 | -37885.197 | -14.09% | 1.Site tripped offline at 13:40 on 10/31 back online at 08:20 on 11/02 2.site tripped offline at 08:05 back online at 13:00 on 11/12 | 1.SR110436 2. SR110913 | 1.Closed 2.Closed | SR110913
Telegraph 2 | NY | SOL-11004 | 125680 | N/A |  |  | 138779.817 | -13099.817 | -9.439% | 1.site tripped offline at 08:05 back online at 13:00 on 11/12 | 1. SR110914 | 1.Closed
Cafferty Hill | NY | SOL-10996 | 375680 | 383668.84 | -7988.84 | -2.082% | 425240.903 | -49560.903 | -11.65% | 1.Inverters were taken offline from 09:55 to 11:55 on 11/04 while technician was onsite to update firware. | 1.SR109797 | 1.Closed
Dunkleman | NY | SOL-11008 | 287690 | 285870 | 1820 | 0.6367% | 382847.716 | -95157.716 | -24.86% | 1. 15 trackers are currently stuck on 11/11 Tracker 01 devices 11, 38, 44, 75, 92, 106, 119 Tracker 02 devices 21, 27, 36, 43, 52, 66, 88, 124 | 1. SR111019 | 1.Pending
Route 19 1 | NY | SOL-11001 | 122657.2 | 119767.6 | 2889.6 | 2.413% | 136625.128 | -13967.928 | -10.22% | 1.Site was offline at 13:40 on 10/31 and back online at 08:20 on 11/02 2.Site offline at 08:00 back online at 13:00 on 11/12 | 1.SR110434 2. SR110915 | 1.Closed 2.Closed | SR110915
Route 19 2 | NY | SOL-11002 | 306830 | 301810 | 5020 | 1.663% | 357089.22 | -50259.22 | -14.07% | 1.Site was offline at 13:45 on 10/31 back online at 08:20 on 11/02 2.Site offline at 08:00 back online at 13:00 on 11/12 | 1.SR110435 2. SR110918 | 1.Closed 2.Closed | SR110918
Yellow Mills 1 | NY | SOL-11006 | 134037 | 131732 | 2305 | 1.75% | 158372.843 | -24335.843 | -15.37% | 1.Inverter module 1-1 was offline whole day on 11/09. 2.Inverter module 1-2 was offline whole day on 11/10. 3.Modules startting late for the production most of the days during the month
Yellow Mills 2 | NY | SOL-11005 | 134735 | N/A |  |  | 163481.128 | -28746.128 | -17.58% | 1.Inverter module 1-1 was offline whole day on 11/09. 2.Inverter module 1-2 was offline whole day on 11/10. 3.Modules startting late for the production most of the days during the month 4.Meter is intermittently lossing communication since 09/04, production can be verified at inverter level. | 1.SR107667 | 1.Closed
Yellow Mills 3 | NY | SOL-11007 | 127582 | 125165 | 2417 | 1.931% | 153044.865 | -25462.865 | -16.64% | 1.Inverter module 1-1 was offline whole day on 11/09. 2.Inverter module 1-2 was offline whole day on 11/10. 3.Modules startting late for the production most of the days during the month
Catskill | NY | SOL-11021 | 232875 | 0 | 232875 |  | 326228.605 | -93353.605 | -28.62% | 1.Site is back online at 09:00 on 11/03 2.Site tripped offline at 00:00 on 11/04 and later tech closed the recloser at 11:00 on 11/04 | 1.SR110474 2.SR110575 | 1.Closed 2.Closed | SR110575
Eddy Ridge | NY | SOL-11054 | 127439 | 124693 | 2746 | 2.202% | 169294.275 | -41855.275 | -24.72% | 1. Trackers 1 through 49 have been stuck since 07/28. | 1.SR109604 | 1.Pending
Ridgeway #1 | NY | SOL-11018 | 334638 | 325910 | 8728 | 2.678% | 414052 | -79414 | -19.18% | 1.Inverter 1 & 2 module 2 has started late for the production at 12:00 on 11/09. 2.Modules started late for the production most of the days.
Rivard 1 | NY | SOL-11011 | 220362 | 235956.6 | -15594.6 | -6.609% | 281923.8 | -61561.8 | -21.84% | 1.Site production was low on 11/07 & 11/10 due to rain or snow
Rivard 2 | NY | SOL-11012 | 210880.08 | 208298 | 2582.08 | 1.24% | 268123.4 | -57243.32 | -21.35% | 1.Site production was low on 11/07 & 11/10 due to rain or snow
Ridgeway #2 | NY | SOL-11027 | 157103 | 153618 | 3485 | 2.269% | 214158.17 | -57055.17 | -26.64% | 1.Site tripped offline at 12:20pm on 11/27 and back online at 11:30 on 11/29 2.Tracker 30 has stuck at -44deg at 08:35 on 11/04 and later back to track at 14:30 on 11/17 | 1.SR111801 | 1.Completed
Spencer | NY | SOL-11017 | 334461.4 | 330410 | 4051.4 | 1.226% | 406955 | -72493.6 | -17.81% | 1.Site tripped offline at 3:45PM on 11/16 and later back online at 08:10 on 11/07 2. Site was offline from 12:05pm on 11/26 and remained offline throughout the month. | 1.SR111175 2.SR111776, SR111964 | 1.Closed 2. Pending | SR111776 | SR111964
Reisender | NY | SOL-10886 | 101430 | 101280 | 150 | 0.1481% | 183452.73 | -82022.73 | -44.71% | 1. Inverter is offline from 11/01 and back online at 11:35 on 11/05 | 1.SR110487 | 1.Closed
Finney | NY | SOL-10999 | 365990 | 364060 | 1930 | 0.5301% | 436477.811 | -70487.811 | -16.15% | 1.MTR 1 - 4 tracker has stuck at -3.31 deg from 12:30 on 10/31. Impacting production during morning and evening hours | 1.SR112194 | 1. New
Davis Solar | NY | SOL-10958 | 163436 | 192407.1 | -28971.1 | -15.06% | 203914 | -40478 | -19.85% | 1.The inverter tripped offline around 7:05am later ROC reset the inverter at 8:50am est on 11/15. 2.Inverter tripped offline at 15:45 on 11/29. ROC reset the inverter at 9:30am on 11/30 | 1.SR111157 2.SR111837 | 1.Closed 2.Closed | SR111837
Genesee | NY | SOL-10951 | 31923.3 | 31071.6 | 851.7 | 2.741% | 251275.242 | -219351.942 | -87.3% | 1.Site tripped offline at 04:25 on 11/01 and back online at 10:20 on 10/15. Again site tripped offline at 10:50 on 11/16 later back online at 11:50 on 11/17 again tripped offline at 13:45 on 11/18 and back online at 14:25 on 11/24 2.Site tripped offline at 12:30 to 14:35 on 11/26 3.All Inverter tripped offline at 14:25 on 11/28 and back online at 12:30 on 11/29 and again tripped offline at 11:55 on 11/30 | 1.SR110430 2.SR111779 3.SR111825 | 1.Completed 2.Completed 3.Pending | SR111779 | SR111825
Landau I | NY | SOL-10891 | 148040 | N/A |  |  | 200679.864 | -52639.864 | -26.23%
Landau II | NY | SOL-10895 | 301870 | N/A |  |  | N/A |  |  | 1.Site was offline at 01:20 on 11/03 back online at 13:20 on 11/05 | 1.SR110563 | 1.closed
New Beginnings | NY | SOL-10890 | 173890 | 173880 | 10 | 0.005751% | 209800.102 | -35910.102 | -17.12% | 1.Inverter tripped offline at 11:45 and back online at 13:20 on 11/12 | 1. SR108827 | 1.Closed
Bullitt Farm Solar, LLC | NY | SOL-10998 | 250857.9348 | 292506.5 | -41648.5652 | -14.24% | 343740.1 | -92882.1652 | -27.02% | 1.Site production was low on 11/09 & 11/10 , 11/11 due to rain or snow
Brodhead Solar, LLC | NY | SOL-10899 | 166943 | 189622.8 | -22679.8 | -11.96% | 218045.7 | -51102.7 | -23.44% | 1.Site production was low on 11/14 due to rain or snow
Svenski | NY | SOL-10894 | 143480 | N/A |  |  | 183433.949 | -39953.949 | -21.78% | 1.Inverter offline at 09:05 on 11/06 and came back online at 10:55 on 11/07 and again inverter offline at 06:00 came back online at 12:25 on 11/08 2.Site was offline at 08:20 came back online at 13:25 on 11/18 | 1.SR110716 2.SR111256 | 1.Closed 2.Closed | SR111256
Bantam | NY | SOL-10986 | 129900 | 198900 | -69000 | -34.69% | 366773.88 | -236873.88 | -64.58% | 1.The meter is missing phase A throughout the month, resulting in incomplete production data for both inverters. GC will review in 2026 2.NCU 1 is missing communications and tracker angles cannot be confirmed, NCU 4 SPC 1015 is stuck. | 1.SR108248 2.SR108120 | 1.Completed 2.Pending | SR108120
Bogart | NY | SOL-10887 | 155650 | 154200 | 1450 | 0.9403% | 199521.546 | -43871.546 | -21.99% | 1.Site is back online at 15:30 on 11/01 | 1.SR110483 | 1.Closed
Dubois | NY | SOL-10892 | 0 | 0 | 0 |  | 0 | 0 |  | 1. The site has been offline since 06:20 on 08/10 due to a transformer failure. | 1. SR106921 | 1.Pending
Salt Point | NY | SOL-10888 | 136530 | 136530 | 0 | 0% | 167108.81 | -30578.81 | -18.3% | 1.Site was offline on 11/01 and back online at 10:35 on 11/02 | 1.SR110473 | 1.Closed
Wheatland 2A | NY | SOL-10971 | 253880 | 252000 | 1880 | 0.746% | 304084.965 | -50204.965 | -16.51% | 1.25 trackers are currently stuck: NCU 1 SPC 101, 106, 111, 112, 116, 118, 201, 204, 301, 302, 305, 307, 309, 310 NCU 2 SPC 125, 126, 136, 141, 223, 234, 242, 324, 327, 338, 341 | 1. SR110135 | 1.Pending
Wheatland 2B | NY | SOL-10961 | 263920 | 81060 | 182860 | 225.6% | 300053.004 | -36133.004 | -12.04% | 1.15 trackers are stuck: NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 2.POA pyranometer stopped communicating from 14:05 on 11/07. Additionally, rPOA pyranometer is not communicating since past years | 1.SR098860 2.SR112216 | 1.Pending 2.New | SR112216
Brickchurch | NY | SOL-10889 | 66070 | 66930 | -860 | -1.285% | 124629.8 | -58559.8 | -46.99% | 1.7 trackers 119,216,220,329, 338, 143, and 240 have seized slew drives. 2.Site was offline on 10/30 and back online at 11:35 on 11/05 3.Site tripped offline at 09:25 back online at 14:05 on 11/09 4.Site tripped offline at 19:50 on 11/16 back online at 09:05 on 11/18 | 1.SR109998 2. SR110355 3. SR110838 4. SR111220 | 1.Pending 2.Closed 3.Closed 4.Closed | SR110355 | SR110838 | SR111220
McCarthy Solar | NY | SOL-10992 | 45370 | 0 | 45370 |  | 207683.3 | -162313.3 | -78.15% | 1.Weather station is not communicating through out the month. 2.Inverter tripped offline at 17:45 on 10/05 and back online at 11:55 on 11/21 | 1.SR109079 2.SR109080 | 1.Deined 2.Closed | SR109080
Costanza | NY | SOL-10907 | 146240 | 146436.7 | -196.7 | -0.1343% | 185414.084 | -39174.084 | -21.13% | 1.Site was offline on 11/01 and came back online on 11/02 2.Site was offline at 06:30 and back online at 09:03 on 11/05 3.Site tripped offline at 08:40 on 11/10 and came back online at 10:31 on 11/12 4.Site tripped offline at 06:47 came back online at 11:37 on 11/15 5.Site offline at 06:00 it came back online at 11:06 on 11/17 6.Site tripped offline at 07:25 it came back online at 14:23 on 11/30 | 1.SR110477 2.SR110660 3.SR110852 4. SR111161 5. SR111183 6. SR111841 | 1.Closed 2.Closed 3.Closed 4.Closed 5.Closed 6.Closed | SR110660 | SR110852 | SR111161 | SR111183 | SR111841
Lockenhurst Pond | NY | SOL-11000 | 162381 | 178371.2 | -15990.2 | -8.965% | 186277 | -23896 | -12.83% | Actual vs Forcasted delta is showing 13% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Drinkwater | NY | SOL-10896 | 139130 | 138060 | 1070 | 0.775% | 185773.391 | -46643.391 | -25.11% | Actual vs Forcasted delta is showing 25% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Altamont | NY | SOL-11085 | 317255 | 383759.9 | -66504.9 | -17.33% | 334880.9 | -17625.9 | -5.263% | 1.Site was tripped offline from 03:30 and back online 05:15 on 11/04 2. Inverters 2.01 to 2.24 are offline on 11/12 and came back online at 09:00 on 11/13 | 1.SR110576 2.SR110935 | 1.Closed 2.Completed | SR110935
Krumkill North | NY | SOL-11086 | 232343 | 299357.6 | -67014.6 | -22.39% | 419535.3 | -187192.3 | -44.62% | 1.Inverter 2 having heavy shading isuue from afternoon to evening hours
Krumkill South | NY | SOL-11087 | 218985 | 274991.7 | -56006.7 | -20.37% | 328902.5 | -109917.5 | -33.42% | 1.Site was offline at 11:00 on 11/04 and it came back online at 09:45 on 11/05 | 1.SR110655 | 1.Closed
X092 | NY | SOL-11189 | 7322.4 | 7811.581 | -489.181 | -6.262% | 8644 | -1321.6 | -15.29% | 1.Inverters 1,2 are having morning shading issue
X093 | NY | SOL-10932 | 5398.7109 | 5737.094 | -338.3831 | -5.898% | 5908 | -509.2891 | -8.62%
X095 | NY | SOL-10929 | 7256.0625 | 9892.355 | -2636.2925 | -26.65% | 8332 | -1075.9375 | -12.91% | 1.Site production was low due to low irradiance or snow on 11/10 , 11/12 , 11/26 , 11/30
X181 | NY | SOL-10428 | 13731.7188 | 14089.21 | -357.4912 | -2.537% | 13747 | -15.2812 | -0.1112%
X415 | NY | SOL-10429 | 8417.3842 | 7556.897 | 860.4872 | 11.39% | 7479 | 938.3842 | 12.55%
K198 | NY | SOL-10930 | 6419.0312 | 7026.188 | -607.1568 | -8.641% | 7080 | -660.9688 | -9.336%
K203 | NY | SOL-11190 | 8063.8 | 7575.097 | 488.703 | 6.451% | 9907 | -1843.2 | -18.61% | 1. Actual vs Forcasted delta is showing 19% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
K213 | NY | SOL-11191 | 8922.3 | 10729.72 | -1807.42 | -16.84% | 10161 | -1238.7 | -12.19% | 1. Inverters 3 and 4 had heavy shading in morning.
K217 | NY | SOL-10933 | 4463.4688 | 5474.212 | -1010.7433 | -18.46% | 4712 | -248.5312 | -5.274% | 1.Site production was low due to low irradiance or snow on 11/09 , 11/10 , 11/26 , 11/30
K307 | NY | SOL-10876 | 10209.7188 | 16185.57 | -5975.8512 | -36.92% | 9094 | 1115.7188 | 12.27% | 1. Inverter 2 experiencing minor shading issue
K610 | NY | SOL-11158 | 12291.8 | 12840.36 | -548.56 | -4.272% | 13142 | -850.2 | -6.469%
M025 | NY | SOL-10392 | 8862.375 | 13193.74 | -4331.365 | -32.83% | 12051 | -3188.625 | -26.46% | 1. Inverter 1 unit 1.5 was offline from 10/10 and it came back online on 11/10 2. Inverter 3 unit 3.1 was offline from 10/10 and it came back online on 11/10 | 1. SR110156 2. SR110155 | 1.Closed 2.Closed | SR110155
M028 | NY | SOL-10381 | 8206.2656 | 8228.234 | -21.9684 | -0.267% | 8255 | -48.7344 | -0.5904%
Q030 | NY | SOL-10878 | 9886.4844 | 10362.53 | -476.0456 | -4.594% | 10502 | -615.5156 | -5.861%
Q130 | NY | SOL-10877 | 5253.2034 | 6524.231 | -1271.0276 | -19.48% | 5411.849 | -158.6456 | -2.931% | 1. Inverter 1 unit 1.2 has heavy shading in the afternoon.
Q196 | NY | SOL-10879 | 6858.3906 | 8106.387 | -1247.9964 | -15.4% | 7155 | -296.6094 | -4.145% | 1. Inverter 3 has heavy shading in morning and evening.
Q220 | NY | SOL-10873 | 7129.8594 | 10711.88 | -3582.0206 | -33.44% | 7400 | -270.1406 | -3.651% | 1. The inverters are experiencing minor shading.
Q205 | NY | SOL-10922 | 10737.9219 | 13507.12 | -2769.1981 | -20.5% | 10532 | 205.9219 | 1.955% | 1. Inverter 3 has afternoon shading.
Q400 | NY | SOL-10871 | 9888.3125 | N/A |  |  | 15542 | -5653.6875 | -36.38% | 1. Inverter 2, unit 2.1 offline on 11/28 | 1.SR111819 | 1.Closed
R003 | NY | SOL-10416 | 16239.9062 | 15609.61 | 630.2962 | 4.038% | 15818 | 421.9062 | 2.667%
R007 | NY | SOL-10417 | 17423.4375 | 18500.07 | -1076.6325 | -5.82% | 22988.13 | -5564.6925 | -24.21% | 1. Actual vs Forcasted delta is showing 24% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
BK16 | NY | SOL-11093 | 16280.375 | 17315.66 | -1035.285 | -5.979% | 16902 | -621.625 | -3.678%
Trenton - Trenton East | IL | SOL-11060 | 253712 | 255632.3 | -1920.3 | -0.7512% | 220448 | 33264 | 15.09% | 1.Site was offline from 08:15 to 14:45 on 11/04 | 1.SR110598 | 1.Closed
Trenton - Trenton West | IL | SOL-11061 | 253189 | 224052 | 29137 | 13% | 229321 | 23868 | 10.41% | 1.Multiple trackers are stuck 2.Site was offline on 11/04 at 11:30 to 15:30 | 1.SR109332 2. SR110652 | 1.Pending 2.Closed | SR110652
Dakota - Dakota Solar 1 | IL | SOL-11113 | 206864 | 211766.3 | -4902.3 | -2.315% | 210384 | -3520 | -1.673%
X018 | NY | SOL-10418 | 7739.2812 | 7884.086 | -144.8048 | -1.837% | 9450 | -1710.7188 | -18.1% | 1.Inverter 3 having heavy shading issue in morning hours 2. Actual vs Forcasted delta is showing 18% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Janiak Solar | NY | SOL-10898 | 128714.6439 | 133336.8 | -4622.1561 | -3.467% | 206814 | -78099.3561 | -37.76% | 1.Site was offline on 10/31 at 11:00 and it came back online on 11/04 2.Site was offline on 11/11 and it came back online at 10:15 on 11/18 | 1.SR110484 2.SR110884 | 1.Closed 2.Closed | SR110884
County Route 11B | NY | SOL-10983 | 279722 | 273566.3 | 6155.7 | 2.25% | N/A
Barone | NY | SOL-11034 | 225837 | 221879 | 3958 | 1.784% | 297505 | -71668 | -24.09% | 1.Site came back online at 10:30 on 11/01 2.Site was offline on 11/06 and it came back online at 10:40 on 11/07 3.Site was offline at 10:00 on 11/20 at 10:10 on 11/21 | 1.SR110407 2. SR110728 3.SR111391 | 1.Closed 2.Closed 3.Closed | SR110728 | SR111391
Cedarville | IL | SOL-11069 | 143395 | 172391.8 | -28996.8 | -16.82% | 189071.5 | -45676.5 | -24.16% | 1.Site was tripped offline at 08:00 on 11/04 and it came back online on 11/06 | 1. SR110246 | 1.Closed
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | N/A |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | 1.Pending | SR098670
O'Brien Hill #2 | NY | SOL-11099 | 225729 | 225636 | 93 | 0.04122% | N/A |  |  | 1.Site was offline at 19:50 on 10/31 and it came back online at 10:40 on 11/02 2.Inverter 1 offline on 11/08 and it came back online at 12:50 on 11/09 3. All trackers are stuck between 51 and 55 DEG on 11/12. on 11/17 Technician was reset trackers, tracking properly tracking. | 1.SR110476 2. SR110703 3. SR110938 | 1.Closed 2.Closed 3.Closed | SR110703 | SR110938
Trinity - Freeport | IL | SOL-11057 | 188687 | 213822.2 | -25135.2 | -11.76% | 199856 | -11169 | -5.589% | 1.Site tripped offline from 13:30 to 16:00 on 11/21 | 1.SR111476 | 1.Closed
Ransom | NY | SOL-11157 | 315223 | 310457 | 0 | 0% | N/A |  |  | 1.Site was offline due to utility at 08:00 on 11/05 came back online at 16:20 on same day | 1. SR110669 | 1.Closed
Horseheads - Wedge | NY | SOL-11160 | 179848 | 177557 | 2291 | 1.29% | N/A |  |  | 1.Site tripped offline at 16:10 on 11/26 and it came back online at 10:40 on 11/28 | 1.SR111796 | 1.Completed
Otisville - Shoddy Hollow | NY | SOL-11185 | 395324 | 390173 | 5151 | 1.32% | N/A |  |  | 1.Site was offline from 12:45 to 13:00 on 11/08 2.The meter is missing comms but the inverters are communicating on 11/30 | 1. SR110776 2. SR111863 | 1.Closed 2.pendig | SR111863
Wellsville - Chenunda Creek | NY | SOL-11187 | 136191 | 133652 | 2539 | 1.9% | N/A |  |  | 1.Site tripped offline at 08:20 on 11/06 and it came back online at 12:10 on 11/07 2.Site took offline for some maintenance on the circuit from 07:00 until 18:00 on 11/12/25. | 1. SR110704 2.SR110882 | 1.Closed 2.Closed | SR110882
DC: Washington - Essex Condominium | DC | SOL-10036 | 1794 | 2351.456 | -557.456 | -23.71% | 2170.947 | -376.947 | -17.36% | 1. The site is performing as expected, but the expected and forecasted values are high. A similar event was observed over the past two years.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 5843 | 8892.015 | -3049.015 | -34.29% | 9803.471 | -3960.471 | -40.4% | 1. Inverter 2 was offline at 07:00 on 10/11. denied by customer 2. The meter has been communicating intermittently throughout the month. | 1. SR109524 2. SR100771 | 1.Closed 2.Pending | SR100771
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 10100 | 8112.219 | 1987.781 | 24.5% | 9798.225 | 301.775 | 3.08%
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 87025 | 159248.4 | -72223.4 | -45.35% | 219374.1 | -132349.1 | -60.33% | 1.Site tripped offline from 11:00 to 12:30 on 11/01 and again site tripped offline at 23:45 on 11/03 and it came back online at 09:45 on 11/06 2. All trackers are stuck from 10:25 am CST on 11/6. NCU is reporting a snow alarm. 3.Site was offline at 05:45 on 11/18 | 1. SR110361 2. SR110787 3.SR110863 | 1.Closed 2.Pending 3.Pending | SR110787 | SR110863
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 578038 | 580567.1 | -2529.1 | -0.4356% | 537280 | 40758 | 7.586%
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 198037 | 0 | 198037 |  | 218711.5 | -20674.5 | -9.453% | 1.Site was tripped offline at 12:30 on 11/05 and it came back online on 01:15 on 11/06 2.Site tripped offline from 06:15 to 07:15 on 11/07 3. Inverter 2 is constantly derating at 50kW from 08:30 on 11/10 and reporting "Temperature Sensor Fault - Warn0050". 4. Weather station stopped communicating on 9/22. | 1.SR110691 2. SR110755 3.SR110867 4.SR108392 | 1.Closed 2.Closed 3.Pending 4.Pending | SR110755 | SR110867 | SR108392
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 266440.5 | 386852.3 | -120411.8 | -31.13% | 472711 | -206270.5 | -43.64% | 1. Inverter 2 tripped offline at 09:45 on 11/03 and It came back online on 11/06 2. site tripped offline 08:31 on 11/13 it came back online on same day 3. Inverter 2 tripped offline at 11:00 on 11/15 it came back online on 11/16 | 1.SR110574 2. SR111001 3. SR111163 | 1.Closed 2.Closed 3.Pending | SR111001 | SR111163
NY: Whitesville - Independence North | NY | SOL-11186 | 262579 | N/A |  |  | N/A |  |  | 1. Site was taken off for utility maintenance on 11/12 from 07:00 to 18:00 | 1.SR110883 | 1.Closed
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 221021 | 231487.1 | -10466.1 | -4.521% | 235088 | -14067 | -5.984% | 1. Trackers TCU 41 Strucked on 10/07.Hold until 2026 per client | 1.SR109160 | 1.Denied
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 220208 | 284770.2 | -64562.2 | -22.67% | 220105 | 103 | 0.0468% | 1. Inverter 4 is underperforming by 10 kW from 10/07. Hold until 2026 per client | 1.SR109156 | 1.Denied
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 179121 | 360992.1 | -181871.1 | -50.38% | 186732 | -7611 | -4.076% | 1. Trackers TCU 39 Strucked on 10/07 and TCU 33 and 66 strucked on 10/14.Hold until 2026 per client | 1. SR109157 | 1.Denied
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 223333 | 254205.4 | -30872.4 | -12.14% | 193014.5 | 30318.5 | 15.71%
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 966585.6 | N/A |  |  | N/A
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 595868 | N/A |  |  | 609016.5 | -13148.5 | -2.159% | 1. Inverters 1.10, 2.05, and 2.11 have been intermittently derating to 50 kW during high-irradiance days since 11/10. | 1. SR112383 | 1. Pending
IL: Manhattan - Gougar (PW) | IL
Note on D89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter is reporting 0 we have taken total inverter energy as actual energy

## Dec
Generate Capital |  |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  |  | 46663079.3912 | 11738614.453 | 34924464.9382 | 297.5% | 17724983.202 | 28938096.1892 | 163.3%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
K026 | NY | SOL-10356 | 5816 | 13197.52 | -7381.52 | -55.93% | 9973.636 | -4157.636 | -41.69% | 1. Meter B phase currents dropped to Zero whole month. Need to replace CT's.On 12/30 CT's were removed | 1. SR107464 | 1. pending
K041 | NY | SOL-10357 | 7245.2812 | 9803.632 | -2558.3507 | -26.1% | 8296 | -1050.7188 | -12.67% | 1. Inverter 2 has afternoon shading.
K043 | NY | SOL-10358 | 9016.8125 | 11665.35 | -2648.5375 | -22.7% | 1930 | 7086.8125 | 367.2% | 1. Estimated values are low in AE we have also verified the file which was given by GC
K058 | NY | SOL-10360 | 6822.4375 | 9050.694 | -2228.2565 | -24.62% | 8335.429 | -1512.9915 | -18.15% | 1.Site production was low from 12/14 to 12/17 due to snow
K115 | NY | SOL-10361 | 3707.2236 | 6038.074 | -2330.8504 | -38.6% | 4765.995 | -1058.7714 | -22.22% | 1. Inverter 1 (middle unit) was offline on 11/25. After the technician replaced the defective optimizer, the inverter unit came back online at 10:30 on 12/09. | 1. SR111795 | 1. Closed
K152 | NY | SOL-10362 | 2494.0938 | 3397.701 | -903.6073 | -26.59% | 3295 | -800.9062 | -24.31% | 1.1 Optimizer was offline | 1.SR110236 | 1. pending
K166 | NY | SOL-10363 | 8880.875 | 12583.64 | -3702.765 | -29.43% | 11016.24 | -2135.365 | -19.38% | 1.3 optimizers are offline: 2.0.160, 3.0.17, 3.0.33 | 1.SR095666 | 1. pending
K206 | NY | SOL-10927 | 5535.375 | 5692.76 | -157.385 | -2.765% | 5754 | -218.625 | -3.8%
K251 | NY | SOL-10365 | 6436.1875 | 0 | 6436.1875 |  | 7861.315 | -1425.1275 | -18.13% | 1. Weather station stopped communicating on 11/22 at 07:00. replacement POA. | 1. SR093633 | 1. Closed
K269 | NY | SOL-10366 | 5704.1512 | 8521.731 | -2817.5798 | -33.06% | 6704.166 | -1000.0148 | -14.92% | 1. Inverter 2 started late for the production on 12/19 Inverters producing as expected and expected value and forecasted energy values difference. | 1.SR113179 | 1. Closed
K273 | NY | SOL-10367 | 5872.375 | 0 | 5872.375 |  | 8725 | -2852.625 | -32.69% | 1. 26 optimizers are down for roof repair. 2. Weather station stopped communicating since 06/14/24. | 1.SR093924 2. SR086842 | 1. Pending 2. Closed
K287 | NY | SOL-10919 | 4986.9688 | 5891.63 | -904.6613 | -15.36% | 6270 | -1283.0312 | -20.46% | 1.Site production was low from 12/14 to 12/17 due to snow
K298 | NY | SOL-10368 | 4314.5 | 7711.43 | -3396.93 | -44.05% | 4753 | -438.5 | -9.226% | 1.Site production was low from 12/14 to 12/17 due to snow
K335 | NY | SOL-10370 | 5102.8125 | 8062.69 | -2959.8775 | -36.71% | 7506 | -2403.1875 | -32.02% | 1. The site went offline at 07:00 on 12/08. Additionally, the inverters reported a ‘Grid Voltage’ fault, and the site came back online at 07:00 on 12/09. 2. Inverter 1 has minor shading issue. | 1. SR112395 | 1. Closed
K345 | NY | SOL-10920 | 6157.8438 | 5967.621 | 190.2227 | 3.188% | 4911 | 1246.8438 | 25.39%
K445 | NY | SOL-10373 | 5288.2812 | 8410.851 | -3122.5698 | -37.13% | 5564.289 | -276.0077 | -4.96% | 1.Site production was low from 12/14 to 12/17 due to snow
K495 | NY | SOL-10374 | 20475.875 | 30554.12 | -10078.245 | -32.98% | 42655.36 | -22179.485 | -52% | 1. Site tripped offline at 14:00 on 12/04 and back online at 09:00 on 12/08. 2. Inverter 4 was offline on 12/09 and reporting "critical temperature on AC terminal" and remained offline throughout the month. | 1. SR112247 2. SR112416 | 1. Closed 2. Pending
M020 | NY | SOL-10380 | 6297.8438 | 7431.936 | -1134.0922 | -15.26% | 7745 | -1447.1562 | -18.69% | 1.Site production was low from 12/14 to 12/17 due to snow
M092 | NY | SOL-10383 | 5798.3125 | 7960.239 | -2161.9265 | -27.16% | 6863.222 | -1064.9095 | -15.52% | 1.Site production was low from 12/14 to 12/17 due to snow
M143 | NY | SOL-10384 | 5774.875 | 7586.981 | -1812.106 | -23.88% | 7156.772 | -1381.897 | -19.31% | 1.Site production was low from 12/14 to 12/17 due to snow
M144 | NY | SOL-10385 | 9554.875 | 15307.98 | -5753.105 | -37.58% | 20169.15 | -10614.275 | -52.63% | 1. Inverter 2 has afternoon shading.
M167 | NY | SOL-10386 | 5510.2188 | 5916.079 | -405.8602 | -6.86% | 6666.668 | -1156.4492 | -17.35% | 1. Actual vs forcasted delta is showing 17% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).
M188 | NY | SOL-10387 | 5060.4198 | 7118.488 | -2058.0682 | -28.91% | 10141.11 | -5080.6902 | -50.1% | 1. Inverter 2 has morning shading.
EMHC | NY | SOL-10351 | 1537.9375 | 1491.1 | 46.8375 | 3.141% | 2006.482 | -468.5445 | -23.35% | 1.Module 1.0.90 (21772020-D8) No communication. 1.0.29 - 217E44D3-B6 - offline. | 1. SR093236 | 1. Pending
Q008 | NY | SOL-10397 | 8536.4375 | 11689.81 | -3153.3725 | -26.98% | 9163 | -626.5625 | -6.838% | 1.Site production was low from 12/14 to 12/17 due to snow
Q018 | NY | SOL-10398 | 5682.6875 | 7426.734 | -1744.0465 | -23.48% | 6115.039 | -432.3515 | -7.07% | 1.Site production was low from 12/14 to 12/17 due to snow
Q021 | NY | SOL-10399 | 4179.9375 | 6805.838 | -2625.9005 | -38.58% | 4714.944 | -535.0065 | -11.35% | 1.Site production was low from 12/14 to 12/17 due to snow
Q025 | NY | SOL-10400 | 7610 | 9334.553 | -1724.553 | -18.47% | 6321 | 1289 | 20.39% | 1. Actual vs Forcasted delta is showing 20% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Q074 | NY | SOL-10402 | 0 | 0 | 0 |  | 0 | 0 |  | 1. Home run Solar shut off the site at 08:30am on 09/22 to perform roof repairs. | 1. SR102529 | 1. Pending
Q115 | NY | SOL-10872 | 6076.6875 | 8566.134 | -2489.4465 | -29.06% | 7531.608 | -1454.9205 | -19.32% | 1. Inverter 1’s left unit went offline on 10/29 later back online at 10:45 on 12/01 2.1 broken modulefound during the PM | 1. SR110250 2.SR109181 | 1. Closed 2. Pending
Q139 | NY | SOL-10403 | 3706.0625 | 4979.367 | -1273.3045 | -25.57% | 4728 | -1021.9375 | -21.61% | 1. Inverter 2 has offline from 12/23 and offline for rest of the month 2.Some optimizers with production issues 1264FFBB-30 - Half production 12639DA9-BB - Half production | 1.SR113444 2.SR088282 | 1.Pending 2.Pending
Q157 | NY | SOL-10404 | 6762.625 | 11722.66 | -4960.035 | -42.31% | 8269.772 | -1507.147 | -18.22% | 1.Site production was low from 12/14 to 12/17 due to snow
Q192 | NY | SOL-10406 | 9020.125 | 14911.18 | -5891.055 | -39.51% | 12897.3 | -3877.175 | -30.06% | 1.Inverter 3 unit 3.1 tripped offline at 12:00 on 11/17 and remained rest of the month. | 1.SR112392 | 1.Pending
Q210 | NY | SOL-10407 | 8984.625 | 10179.04 | -1194.415 | -11.73% | 10755 | -1770.375 | -16.46% | 1.Site production was low from 12/14 to 12/17 due to snow
Q229 | NY | SOL-10408 | 3258.8125 | 5554.68 | -2295.8675 | -41.33% | 3222.47 | 36.3425 | 1.128% | 1. 8 optimizers are offline. GenC confirms that Amrc will handle, to be combined with PM. | 1. SR088813 | 1. Pending
Q231 | NY | SOL-10870 | 13776.375 | 23583.87 | -9807.495 | -41.59% | 13232 | 544.375 | 4.114% | 1.Inverter 1 has shading issue.
Q405 | NY | SOL-10409 | 16661.75 | 22389.42 | -5727.67 | -25.58% | 19284.85 | -2623.1 | -13.6% | 1. 4 Inverter modules are offline Module 1.0.64 Module 4.0.39 3.0.20 1.0.64 | 1. SR093324 | 1. Pending
Q435 | NY | SOL-10923 | 21476.375 | 17045.18 | 4431.195 | 26% | 21568 | -91.625 | -0.4248% | 1. Weather station has morning shading due to that expected values are low.
Q485 | NY | SOL-10869 | 17499.125 | 19172.91 | -1673.785 | -8.73% | 20417.86 | -2918.735 | -14.3% | 1.Inverter 1 right unit was offline on 10/30 and later back online at 10:45 on 12/05 | 1.SR111880 | 1.Closed
Q490 | NY | SOL-10411 | 13187.25 | 0 | 13187.25 |  | 15151.22 | -1963.97 | -12.96% | 1. Optimizers Module 1.2.4 , Module 2.2.18 , Module 2.3.11 , Module 3.1.16 , Module 6.1.5 , Module 7.1.4 , Module 7.3.17 , Module 9.1.16 ,Module 10.3.3 , 8.0.27 are offline. Pending troubleshooting. | 1. SR093326, SR110229 | 1. Pending
Q620 | NY | SOL-10867 | 20472.25 | 23803.15 | -3330.9 | -13.99% | 23059.82 | -2587.57 | -11.22% | 1.Inverter modules 3.0.144 and 5.0.100 are offline 4.0.66 - 30513B3F-FB - half production because split between 4 modules | 1. SR093327 | 1.Pending
QMOA | NY | SOL-10415 | 1980.9 | 0 | 1980.9 |  | 2545.934 | -565.034 | -22.19% | 1.Site production was low from 12/14 to 12/17 due to snow
X024 | NY | SOL-10419 | 6175.1562 | 8682.387 | -2507.2308 | -28.88% | 7933 | -1757.8438 | -22.16% | 1.Inverter 2 started late for the production on 12/16 and having heavy shading isuue in mid day hours | 1.SR112764 | 1.Closed
X026 | NY | SOL-10420 | 5641.4 | 8223.701 | -2582.301 | -31.4% | 9988.018 | -4346.618 | -43.52% | 1. Optimizer 1.0.124 is offline. Will investigate combinely with other modules. | 1.SR109950 | 1.Pending
X090 | NY | SOL-10925 | 5903.625 | 4677.65 | 1225.975 | 26.21% | 5824 | 79.625 | 1.367%
X117 | NY | SOL-10422 | 4096.3 | 7330.294 | -3233.994 | -44.12% | 5915.348 | -1819.048 | -30.75% | 1. Inverter 1 having morning shading issue.
X125 | NY | SOL-10423 | 8697.375 | 11976.89 | -3279.515 | -27.38% | 10041.16 | -1343.785 | -13.38% | 1.Inverter 1 unit 1.2 having evening shading issue
X134 | NY | SOL-10424 | 4076.375 | 13143.4 | -9067.025 | -68.99% | 7225 | -3148.625 | -43.58% | 1. 6 modules are offline: Module 1.2.1 Module 1.2.13 Module 1.2.14 Module 1.11.5 Module 2.1.12 Module 2.1.16 | 1.SR098241 | 1.Pending
X135 | NY | SOL-10425 | 6856.125 | 12152.03 | -5295.905 | -43.58% | 8283 | -1426.875 | -17.23% | 1.Inverter 1 unit 1.3 having morning shading issue and inverter 2 having evening shading issues
X139 JHS 222 | NY | SOL-10426 | 10130.5908 | 12793.92 | -2663.3292 | -20.82% | 10209 | -78.4092 | -0.768% | 1.Site production was low from 12/14 to 12/17 due to snow
X140 | NY | SOL-10926 | 6554.6738 | 6771.281 | -216.6072 | -3.199% | 6913 | -358.3262 | -5.183%
X166 | NY | SOL-10427 | 6157.4 | 10261.55 | -4104.15 | -40% | 5655 | 502.4 | 8.884% | 1. Inverter 2 has afternoon shading.
Murphy | MN | SOL-10094 | 118930 | 365553.7 | -246623.7 | -67.47% | 396855.8 | -277925.8 | -70.03% | 1.Inverter 1 tripped offline at 13:15 on 12/16 and later back online at 11:45 on 12/19 2.Site tripped offline at 16:00 on 12/25 and later back online at 11:40 on 12/30. 3.Inverter E is offline and Inverter A is producing at half of the capacity compared to peers from 11:30 on 12/30 after the site was re-energized. | 1.SR113149 2.SR113624 3.SR113912 | 1.Closed 2,Work in progress 3.Pending | SR113912
Terning | MN | SOL-10093 | 141339.4524 | 408204.2 | -266864.7476 | -65.38% | 358517 | -217177.5476 | -60.58% | 1.29 modules were damaged 2. inverter 2 derating by 150kW from 10/17/25, later PE has made repairs on 12/25 3.Inverter 5 is offline from 07:15 on 11/26 and back online at 08:00 on 12/03 4.Inverter 3 module was not communicating | 1.SR104556 2.SR109775 3.SR112024 4.SR113579 | 1.Pending 2.Closed 3.Closed 4.Pending | SR112024 | SR113579
Boas Road 04 | NY | SOL-10908 | 59333 | 59333 | 0 | 0% | 120930.845 | -61597.845 | -50.94% | 1.Site production was low on 12/02,12/10,12/23,12/24,12/25,12/26,12/27 &12/28 due to snow.
Kelly Bridge Farm | NY | SOL-10911 | 41508 | N/A |  |  | 119955.597 | -78447.597 | -65.4% | 1.Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher
Pool Brook Road | NY | SOL-10909 | 39393 | 39393 | 0 | 0% | 128062.968 | -88669.968 | -69.24% | 1.Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher
Sackett Lake | NY | SOL-10910 | 59433 | 0 | 59433 |  | 135943.766 | -76510.766 | -56.28% | 1.Inverter 1 was offline from 12/06 and back online at 11:00 on 12/10 2.Inverter 1 was offline from 12/13 and back online at 12:40 on 12/17 | 1.SR112418 2.SR112831 | 1.Closed 2.Closed
Burritt Road | NY | SOL-10913 | 76280 | 0 | 76280 |  | 100593.815 | -24313.815 | -24.17% | 1. The Production was low on 12/02, 12/07, 12/10, 12/15, 12/26 , 12/17 & 12/28 due to low irradiance/snow
Villa Roma 1 | NY | SOL-10914 | 45150 | 0 | 45150 |  | 102450.374 | -57300.374 | -55.93% | 1. The Production was low on 12/02, 12/03, 12/04, 12/05, 12/14 , 12/23 & 12/27 due to low irradiance/snow
Villa Roma 2 | NY | SOL-10915 | 31007 | 0 | 31007 |  | 100480.175 | -69473.175 | -69.14% | 1. The Production was low on 12/02, 12/03, 12/04, 12/05, 12/14 , 12/23 & 12/27 due to low irradiance/snow
Washington 1 | NY | SOL-10912 | 69990 | N/A |  |  | 96145.736 | -26155.736 | -27.2% | 1.Site tripped offline at 22:15 on 12/29 and back online at 12:35 on 12/30 2.Inverter 1 tripped offline at 12:15 on 12/27 and back online at 12:35 on 12/30 | 1.SR113825 | 1.Closed
Washington 3 | NY | SOL-10828 | 2434 | N/A |  |  | 117626.821 | -115192.821 | -97.93% | 1.Site was offline from 12:15 on 09/23 due to inverter to XFMR busbars had thermal damage and later back online at 15:30 on 12/23 and again offline from 10:30 on 12/24 and remained offline throughout the month due to oil leak in transformer. | 1.SR105816 ,SR113584 | 1.Closed, New
Washington 4 | NY | SOL-10829 | 101502 | N/A |  |  | 118024.801 | -16522.801 | -14% | 1.Inverter 1 tripped offline at 10:05 on 12/15 and later back online at 10:25 on 12/16 2.Site tripped offline at 22:15 on 12/29 and back online at 12:35 on 12/30 | 1.SR112838 2.SR113823 | 1.Closed 2.Closed
Big Tree | NY | SOL-10966 | 48720 | 48630 | 90 | 0.1851% | 106925.4 | -58205.4 | -54.44% | 1. The Production was low on 12/04, 12/13, 12/15, due to low irradiance.
Canoga | NY | SOL-10965 | 315150 | N/A |  |  | 299474.5 | 15675.5 | 5.234%
County Route 84 | NY | SOL-10967 | 198410 | 196910 | 1500 | 0.7618% | 372286.228 | -173876.228 | -46.7% | 1.Inverters 3&4 were kept offline from 11/21 and back online at 14:10 on 12/09 2.Site tripped offline at 09:30 and back online at 16:10 on 12/04, Inverter 2 was offline after site was back online on 12/04 and back online at 14:10 on 12/09 3.Site tripped offline at 11:05 on 12/16 and back online at 11:45 on 12/17 4.Site tripped offline at 12:05 on 12/21 and back online at 13:00 on 12/23 5.Site tripped offline from 10:10 to 14:30 on 12/31 and inverters 3&4 remained offline after site is back online. | 1.SR105508 2.SR112225 3.SR112950 4.SR113336 5.SR113456 | 1.Closed 2.Closed 3.Closed 4.Closed 5.Pending | SR112950 | SR113336 | SR113456
Donati | NY | SOL-10968 | 82800 | 79790 | 3010 | 3.772% | 118905.747 | -36105.747 | -30.37% | 1.Trackers: Group A tracker 1, 5, 6, 7, & 10 Group F tracker 22, 27, & 33 Group G tracker 13 & 14 are stuck | 1.SR113372 | 1.Pending
Henrietta | NY | SOL-10972 | 130420 | 127800 | 2620 | 2.05% | 223611.997 | -93191.997 | -41.68% | 1. Gateway 5 missing 3 trackers 6, 14 and 15 were strucked since 08/20.Gc to hold untill 2026 2.Inverter 4 tripped offline at 09:40 on 12/11 and back online at 10:30 on 12/17 3.8 trackers are stuck, previously requested to hold until 2026: T01.A.30; B.24; D.17; E.06, 13, 14, & 18; F.13 | 1.SR106622 2.SR112656 3.SR114038 | 1.Closed 2.Closed 3.Pending | SR114038
NY 70 | NY | SOL-10970 | 171540 | 168440 | 3100 | 1.84% | 352746.797 | -181206.797 | -51.37% | 1.Site tripped offline at 07:55 on 12/15 and back online at 23:00 on 12/17 | 1.SR112755 | 1.Closed
Reid | NY | SOL-10991 | 112622.0312 | 213407.4 | -100785.3688 | -47.23% | 252368 | -139745.9688 | -55.37% | 1.Inverters 1 - 20 started for production at 14:30 on 12/07 2.Inverter 9 has derated to 100kW from 08/31, tech has updated inverters 9 & 30 back to 100% on 12/07 3.Inverter 18 has derated at 50kW on 12/20 to 12/22 4.Weather station lost communication while technician was on site at 14:00 on 12/07 and came back online at 16:45 on 12/09 | 1.SR112331 2.SR107331, SR111325 4. SR112331 | 1.Closed 2.Closed 3.Closed | SR111325 | SR112331
Sangolqui | NY | SOL-10975 | 87810 | 85770 | 2040 | 2.378% | 115147.204 | -27337.204 | -23.74% | 1.10 trackers are stuck: T01.C.44, 45, 46, 48, & 50 T01.D.48 & 49 T01.E.37 & 43 Remaining trackers offline: C.44 - R280 C.45 - R240 C.46 - R263 C.48 - R257 C.50 - R241 D.49 - R243 2.POA pyranometer up reporting 0 from 12/30 | 1.SR108338 | 1.Denied
State Highway 17B | NY | SOL-10988 | 46330 | 45770 | 560 | 1.224% | 318438 | -272108 | -85.45% | 1.Site stopped communicating to GPM DAS From 02:00 on 12/17 and remained rest of the month but site is online and producing in Ingecon portal | 1.SR112948 | 1.Closed
State Route 14A | NY | SOL-10997 | 0 | 0 | 0 |  | 347688.048 | -347688.048 | -100% | 1. The site was offline since 04/03. On 05/14, USNE replaced the SEL relay and CAT5 cable, bringing the site back online at 12:55. It went offline again on 05/22. On 05/23, the site was re-energized but was subsequently shut down after Transformer 2 showed signs of internal arcing. Further medium-voltage (MV) troubleshooting is required. On 07/02 technician was after pulling event files from the SEL for analysis. The site remains offline. | 1. SR101820 | 1. Pending
West Creek | NY | SOL-10995 | 220610 | 217930 | 2680 | 1.23% | 299353.839 | -78743.839 | -26.3% | 1.Inverter 1-1 module and inverter 2-1 module was offline on 12/02,12/07 & 12/27 2.Inverter 1-2 module and inverter 2-2 module was offline on 12/02,12/10, 12/23 & 12/28
Wildflower | NY | SOL-10982 | 280878 | 0 | 280878 |  | 406181.2 | -125303.2 | -30.85% | 1. POA Pyranometer UP stopped communicating from 11/16 and POA Pyranometer DOWN stopped communicating since past years 2.Meter 1 is not capuring inverters data but production can be verified at inverter level from 11/16 3.Inverter 3 tripped offline at 15:05 on 12/29 and back online at 09:00 on 12/31 | 1.SR112202 2.SR113983 3.SR113857 | 1. Pending 2.Pending 3.Completed | SR113857
Glen Mary 1 | NY | SOL-10993 | 80100 | 78870 | 1230 | 1.56% | 382104.148 | -302004.148 | -79.04% | 1.The site went offline at 12:30 on 11/20 due to an MV issue and back online at 09:10 on 12/10 2.Site tripped offline at 14:45 on 12/19 and back online at 14:55 on 12/22, inverter 1 was offline on 12/23 and back online at 10:25 on 12/24 3.Site tripped offline at 15:20 on 12/28 and back online at 09:20 on 12/30 | 1.SR111271 2.SR113327 3.SR113700 | 1.Closed 2.Completed 3.Completed | SR113700
Glen Mary 2 | NY | SOL-10994 | 111020 | 0 | 111020 |  | 156963.37 | -45943.37 | -29.27% | 1.POA Pyranometer UP irradiance reporting 0W/m2 since 08/18. Due to this expected energy values in monthly reports has been affected. | 1.SR105649 | 1.Deined
Telegraph 1 | NY | SOL-11003 | 132800 | N/A |  |  | 261356.567 | -128556.567 | -49.19% | 1. The site tripped offline at 07:50 on 12/15 and back online at 12:05 on 12/15. 2. The site tripped offline at 13:40 on 12/17 and back online at 16:00 on 12/15. | 1. SR112750 2. SR113058 | 1. Closed 2. Closed
Telegraph 2 | NY | SOL-11004 | 77090 | N/A |  |  | 135359.611 | -58269.611 | -43.05% | 1. The site tripped offline at 07:50 on 12/15 and back online at 12:05 on 12/15. 2. The site tripped offline at 13:40 on 12/17 and back online at 16:00 on 12/15. | 1. SR112751 2. SR113059 | 1. Closed 2. Closed
Cafferty Hill | NY | SOL-10996 | 263110 | 265197.3 | -2087.3 | -0.7871% | 311672.715 | -48562.715 | -15.58% | 1. Site production was low on 12/24 due to snow
Dunkleman | NY | SOL-11008 | 187790 | 186570 | 1220 | 0.6539% | 325269.036 | -137479.036 | -42.27% | 1. site was offline at 13:00 on 12/29 and remained offline rest of the month. 2. 15 trackers are stuck from 11/11 Tracker 01 devices 11, 38, 44, 75, 92, 106, 119 Tracker 02 devices 21, 27, 36, 43, 52, 66, 88, 124 | 1. SR113860, SR113861 2. SR111019 | 1.Pending 2.Pending | SR111019
Route 19 1 | NY | SOL-11001 | 93868.4 | 91529 | 2339.4 | 2.556% | 131638.81 | -37770.41 | -28.69% | 1. The site tripped offline at 07:50 on 12/15 and back online at 12:05 on 12/15. 2. The site tripped offline at 13:40 on 12/17 and back online at 16:00 on 12/18. | 1. SR112748 2. SR113057 | 1. Closed 2. Closed
Route 19 2 | NY | SOL-11002 | 250180 | 245580 | 4600 | 1.873% | 356148.8 | -105968.8 | -29.75% | 1. The site tripped offline at 07:50 on 12/15 and back online at 12:05 on 12/15. 2. The site tripped offline at 13:40 on 12/17 and back online at 16:00 on 12/18. | 1. SR112749 2. SR113056 | 1. Closed 2. Closed
Yellow Mills 1 | NY | SOL-11006 | 90578 | 88314 | 2264 | 2.564% | 104452.889 | -13874.889 | -13.28% | 1. Inverter module 1-1 was offline whole day on 12/02,12/06 and 12/08 2. Inverter module 1-2 was offline whole day on 12/09,12/15,12/23 and 12/27 3. Modules startting late for the production most of the days during the month
Yellow Mills 2 | NY | SOL-11005 | 91022 | 0 | 91022 |  | 106574.691 | -15552.691 | -14.59% | 1. Inverter module 1-1 was offline whole day on 12/02,12/06,12/27 2. Inverter module 1-2 was offline whole day on 12/09,12/23 3. Modules startting late for the production most of the days during the month 4. Meter is intermittently lossing communication since 09/04, production can be verified at inverter level. 5. Weather station stopped communicating at 13:55 on 04/03/25. | 4. SR107667 | 4. Closed
Yellow Mills 3 | NY | SOL-11007 | 84202 | 81846 | 2356 | 2.879% | 95110.402 | -10908.402 | -11.47% | 1. Inverter module 1-2 was offline whole day on 12/02,12/23,12/27 and 12/28. 2. Inverter module 1-1 was offline whole day on 12/06,12/15 and 12/26. 3. Modules startting late for the production most of the days during the month
Catskill | NY | SOL-11021 | 101674 | 0 | 101674 |  | 233559.224 | -131885.224 | -56.47% | 1. Site tripped offline at 04:00 on 12/01 and back online at 13:15 on 12/01. 2. Site tripped offline at 09:55 on 12/19, After the technician closed the SEL, the site came back online at 11:35 on 12/21. 3. Site tripped offline at 00:30 on 12/30 and remained offline rest of the month. 4. Weather station is not communicating for whole month. | 1. SR111861 2. SR113323 3. SR113809 4. SR106739 | 1. Closed 2. Closed 3. Completed 4. Denied | SR113809 | SR106739
Eddy Ridge | NY | SOL-11054 | 68949 | 67138 | 1811 | 2.697% | 150483.8 | -81534.8 | -54.18% | 1. Trackers 1 through 49 have been stuck since 07/28. | 1. SR109604 | 1. Pending
Ridgeway #1 | NY | SOL-11018 | 235338 | 226458 | 8880 | 3.921% | 336087.4 | -100749.4 | -29.98% | 1. Modules started late for the production most of the days.
Rivard 1 | NY | SOL-11011 | 157421.0249 | 188934.4 | -31513.3751 | -16.68% | 206921.8 | -49500.7751 | -23.92% | 1.Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher
Rivard 2 | NY | SOL-11012 | 154141 | 153304.3 | 836.7 | 0.5458% | 196083 | -41942 | -21.39% | 1.Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher
Ridgeway #2 | NY | SOL-11027 | 112970 | 109702 | 3268 | 2.979% | 172285.7 | -59315.7 | -34.43% | 1.Site production was low most of the days due to snow due to that forcasted (theoretical) values appear higher
Spencer | NY | SOL-11017 | 243391.4 | 240258.3 | 3133.1 | 1.304% | 348250 | -104858.6 | -30.11% | 1. Site was tripped offline at 12:05 on 11/26 and site is back online at 12:00 on 12/03. | 1. SR111776, SR111964 | 1. Closed
Reisender | NY | SOL-10886 | 45230 | 44910 | 320 | 0.7125% | 109708.331 | -64478.331 | -58.77% | 1. Site production was low on 12/02,12/23,12/27 and 12/28 due to snow
Finney | NY | SOL-10999 | 352320 | 349830 | 2490 | 0.7118% | 310084.075 | 42235.925 | 13.62% | 1.MTR 1 - 4 tracker has stuck at -3.31 deg from 12:30 on 10/31. Impacting production during morning and evening hours and after technician recalibrated the tracker is back online on 12/08 and tracking as expected . | 1.SR112194 | 1. Closed
Davis Solar | NY | SOL-10958 | 95166 | 193916.5 | -98750.5 | -50.92% | 145289 | -50123 | -34.5% | 1. Inverter 1 tripped offline at 08:00 on 12/05. After a remote reset, the inverter came back online at 08:30 on 12/05. It tripped offline again at 11:30 on 12/15, reporting ‘contactor opened due to overvoltage.’ After a remote reset, the inverter came back online at 15:22 on 12/15. 2. Inverter 1 was offline at 07:00 on 12/30. After a remote reset, the inverter came back online at 10:15 on 12/30. 3. Inverter 1 was offline at 13:00 on 12/31. After a remote reset, the inverter came back online at 15:45 on 12/31. | 1. SR112253 2. SR113837 3. SR113924 | 1. Closed 2. Closed 3. New | SR113924
Genesee | NY | SOL-10951 | 38403.1 | 37622.9 | 780.2 | 2.074% | 184500.573 | -146097.473 | -79.19% | 1. Both inverters tripped offline at 11:35 and reported the AC breaker in an ‘open state.’ After the technician closed the SEL, both inverters came back online at 12:45 on 12/01. 2. NCU 1 trackers 21 & 53 are strucked since 12/03. 3. The site tripped offline at 11:10 on 12/04. After the technician closed the SEL, the site came back online at 09:10 on 12/05. 4. The site tripped offline at 12:20 on 12/08 while a technician was onsite working on the trackers and came back online at 14:00 on 12/09. 5. The site tripped offline at 09:50 on 12/11 while a technician was onsite working on the trackers and came back online at 11:35 on 12/17. 6.Site tripped offline at 10:30 on 12/18 and remained offline rest of the month. | 1. SR111825 2. SR112035, SR113433 3. SR112217 4. SR112035 5. SR111825, SR112892 6. SR113201 | 1. Closed 2. Pending 3. Closed 4. Closed 5. Closed 6. Pending | SR113433 | SR112217 | SR112035 | SR111825 | SR112892 | SR113201
Landau I | NY | SOL-10891 | 56160 | N/A |  |  | 157892.43 | -101732.43 | -64.43% | 1.CB 1.11 strings 14, 15 and string 5 & 6 were isolated due to ground faults | 1.SR112199 | 1.Pending
Landau II | NY | SOL-10895 | 165430 | N/A |  |  | N/A |  |  | 1. Inverter 1 tripped offline at 10:40 on 12/10. After a remote reset, the inverter came back online at 12:10 on 12/10. | 1. SR112502 | 1. Closed
New Beginnings | NY | SOL-10890 | 93960 | 93950 | 10 | 0.01064% | 167415.358 | -73455.358 | -43.88% | 1.Site production was low on 12/02, 12/03, 12/27 & 12/28 due to snow.
Bullitt Farm Solar, LLC | NY | SOL-10998 | 182335 | 293104.9 | -110769.9 | -37.79% | 277348.6 | -95013.6 | -34.26% | 1.Site production was low on 12/07 & 12/10 due to snow.
Brodhead Solar, LLC | NY | SOL-10899 | 157506 | 183916.4 | -26410.4 | -14.36% | 179686.1 | -22180.1 | -12.34% | 1.Site production was low on 12/02 due to snow
Svenski | NY | SOL-10894 | 84210 | N/A |  |  | 130508.786 | -46298.786 | -35.48% | 1. Inverter 1 was offline at 07:00 on 12/08, reporting a “ground fault.” After a remote breaker reset, the inverter returned online at 12:35 on 12/08. It went offline again at 07:00 on 12/12, reporting a “ground fault,” and after a remote breaker reset, it returned online at 10:20 on 12/13. Once again, the inverter went offline at 07:00 on 12/18 with a “ground fault,” and after a remote breaker reset, it returned online at 11:00 on 12/18. | 1. SR112379 | 1. Closed
Bantam | NY | SOL-10986 | 121510 | 173910 | -52400 | -30.13% | 290202.008 | -168692.008 | -58.13% | 1. Site tripped offline at 07:30 on 12/29 and remained offline rest of the month. 2. The meter is missing phase A throughout the month, resulting in incomplete production data for both inverters. GC will review in 2026 3. NCU 1 is missing communications and tracker angles cannot be confirmed, NCU 4 SPC 1015 is stuck. Pending replacement slew drive needed. 4. All trackers were stuck on 12/04 and reporting “stow mode.” After the technician power-cycled the TCUs, all trackers came back online on 12/05. | 1. SR113716 2. SR108248 3. SR108120 4. SR112191 | 1. New 2. Closed 3. Pending 5. Closed | SR108120 | SR112191
Bogart | NY | SOL-10887 | 97510 | 95740 | 1770 | 1.849% | 134640.576 | -37130.576 | -27.58% | 1. Actual vs Forcasted delta is showing 28% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Dubois | NY | SOL-10892 | 480 | 384.5 | 95.5 | 24.84% | 0 | 480 |  | 1. The site has been offline since 06:20 on 08/10 due to a transformer failure. After the technician replaced the SIM card, the site came back online at 13:31 on 12/30. | 1. SR106921, SR112759 | 1. Work in Progress
Salt Point | NY | SOL-10888 | 117970 | 117970 | 0 | 0% | 120639.812 | -2669.812 | -2.213%
Wheatland 2A | NY | SOL-10971 | 187690 | 186040 | 1650 | 0.8869% | 221839.974 | -34149.974 | -15.39% | 1.25 trackers are currently stuck: NCU 1 SPC 101, 106, 111, 112, 116, 118, 201, 204, 301, 302, 305, 307, 309, 310 NCU 2 SPC 125, 126, 136, 141, 223, 234, 242, 324, 327, 338, 341 | 1. SR110135, SR113865 | 1. Pending
Wheatland 2B | NY | SOL-10961 | 194200 | 0 | 194200 |  | 218721.805 | -24521.805 | -11.21% | 1.15 trackers are stuck: NCU 1 SPC 101, 206, 218, & 314 NCU 2 SPC 118, 128, 230, 234, 321, 323, 333, 334, 336, 337, & 343 2.POA pyranometer stopped communicating from 14:05 on 11/07. Additionally, POA pyranometer is not communicating since past years | 1. SR098860, SR099264, SR113864 2. SR112216 | 1. Pending 2 .Pending | SR113864 | SR112216
Brickchurch | NY | SOL-10889 | 42520 | 44110 | -1590 | -3.605% | 67734.372 | -25214.372 | -37.23% | 1. Site tripped offline at 22:15 on 12/09 and back online at 09:10 on 12/11. 2. Site tripped offline at 01:20 on 12/19 After the technician closed the relay, the site came back online at 11:10 on 12/21. 3. The site went offline at 12:55 on 12/29 and remained offline for the rest of the month. 4. 7 trackers 119,216,220,329, 338, 143, and 240 have seized slew drives. | 1. SR112506 2. SR113322 3. SR113815 4. SR109998 | 1. Closed 2. Closed 3. New 4. Pending | SR113815 | SR109998
McCarthy Solar | NY | SOL-10992 | 148710 | 0 | 148710 |  | 166526.9 | -17816.9 | -10.7% | 1. Weather station is not communicating through out the month. | 1. SR109079, SR110746 | 1.Deined
Costanza | NY | SOL-10907 | 75900 | 75926.5 | -26.5 | -0.0349% | 127106.447 | -51206.447 | -40.29% | 1. The site tripped offline at 08:15 AM on 12/19. After the technician closed the relay, the site came back online at 14:27 on 12/21. 2. The site tripped offline at 07:53 on 12/23. After the recloser was closed remotely, the site came back online at 09:00 on 12/23. 3.Site tripped offline at 06:50 on 12/30 and remained offline rest of the month | 1. SR113325 2. SR113414 3.SR113817 | 1. Closed 2. Closed 3.Completed | SR113817
Lockenhurst Pond | NY | SOL-11000 | 141612 | 168989.2 | -27377.2 | -16.2% | 128868 | 12744 | 9.889% | 1.Site production was low on 12/02,12/14,12/23 & 12/27 due to snow
Drinkwater | NY | SOL-10896 | 81840 | 78980 | 2860 | 3.621% | 128946.605 | -47106.605 | -36.53% | 1. Inverters and weather station stopped communicating at 03:00 on 12/29
Altamont | NY | SOL-11085 | 30296 | 64866.6 | -34570.6 | -53.29% | 273615.1 | -243319.1 | -88.93% | 1. The site went offline at 04:00 on 12/05. After the technician replaced the cable, the site came back online at 10:30 on 12/29. | 1. SR112261, SR113150 | 1. Pending
Krumkill North | NY | SOL-11086 | 163209 | 256168.9 | -92959.9 | -36.29% | 383916.3 | -220707.3 | -57.49% | 1.Inverter 2 having heavy shading isuue from afternoon to evening hours
Krumkill South | NY | SOL-11087 | 106985 | 265875 | -158890 | -59.76% | 300979.4 | -193994.4 | -64.45% | 1. Inverter S.1 was offline from 12/16 and remained offline for the rest of the month. | 1. SR113089 | 1. Pending
X092 | NY | SOL-11189 | 4696.9 | 5921.084 | -1224.184 | -20.67% | 6635 | -1938.1 | -29.21% | 1.Inverters 1,2 are having morning shading issue
X093 | NY | SOL-10932 | 3329.7422 | 4282.94 | -953.1978 | -22.26% | 3954 | -624.2578 | -15.79% | 1. Inverter 2 is derating by 25 kW during peak hours on 12/01 (peak production) due to all three units temperature fluctuation. Isue resolved on 12/11 | 1.SR111884 | 1.closed
X095 | NY | SOL-10929 | 4273.5469 | 8699.849 | -4426.3021 | -50.88% | 5832 | -1558.4531 | -26.72% | 1. inverter 3 unit 3.3 was offline on 11/25 and later back online at 12:00 on 12/26 | 1.SR112553 | 1.closed
X181 | NY | SOL-10428 | 8965.0938 | 11252.82 | -2287.7262 | -20.33% | 9717 | -751.9062 | -7.738% | 1.Site production was low on 12/14 to 12/17 due to snow
X415 | NY | SOL-10429 | 5558.3125 | 6071.741 | -513.4285 | -8.456% | 5186 | 372.3125 | 7.179%
K198 | NY | SOL-10930 | 4270.2969 | 5982.414 | -1712.1171 | -28.62% | 4992 | -721.7031 | -14.46% | 1.Site production was low on 12/14 to 12/17 due to snow
K203 | NY | SOL-11190 | 5351.7 | 6294.818 | -943.118 | -14.98% | 7803 | -2451.3 | -31.41% | 1. Actual vs Forcasted delta is showing 31% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
K213 | NY | SOL-11191 | 6110.5 | 8539.809 | -2429.309 | -28.45% | 7786 | -1675.5 | -21.52% | 1. Inverters 3 and 4 had heavy shading in morning.
K217 | NY | SOL-10933 | 2214.4609 | 4567.027 | -2352.5661 | -51.51% | 3192 | -977.5391 | -30.62% | 1.Inverter unit 1.2 was offline on 12/15 and reporting a low voltage fault. | 1. SR113437 | 1.pending
K307 | NY | SOL-10876 | 7091.7344 | 14454.82 | -7363.0856 | -50.94% | 6146 | 945.7344 | 15.39% | 1. Inverter 2 experiencing minor shading issue
K610 | NY | SOL-11158 | 8623.5 | 10192.45 | -1568.95 | -15.39% | 10624 | -2000.5 | -18.83% | 1.Site production was low on 12/14 to 12/17 due to snow
M025 | NY | SOL-10392 | 5254.7656 | 11372.49 | -6117.7244 | -53.79% | 8251 | -2996.2344 | -36.31% | 1. Inverter 3 unit 3.1 was offline on 12/08 | 1. SR112389 | 1.pending
M028 | NY | SOL-10381 | 5680.1719 | 6915.794 | -1235.6221 | -17.87% | 5563 | 117.1719 | 2.106% | 1.Site production was low on 12/14 to 12/17 due to snow
Q030 | NY | SOL-10878 | 4173.3125 | 5837.938 | -1664.6255 | -28.51% | 7259 | -3085.6875 | -42.51% | 1.Site was offline at 07:30 on 12/19 throuth the month | 1. SR113237 | 1.pending
Q130 | NY | SOL-10877 | 3524.3903 | 5714.432 | -2190.0417 | -38.32% | 3544.817 | -20.4267 | -0.5762% | 1. Inverter 1 unit 1.2 has heavy shading in the afternoon.
Q196 | NY | SOL-10879 | 4590.2188 | 6576.159 | -1985.9402 | -30.2% | 4888 | -297.7812 | -6.092% | 1. Inverter 3 has heavy shading in morning and evening.
Q220 | NY | SOL-10873 | 4845.125 | 9077.747 | -4232.622 | -46.63% | 4864 | -18.875 | -0.3881% | 1. Inverter 1 unit 1.2 was offline on 09/29 at 14:30 | 1.SR112357 | 1.pending
Q205 | NY | SOL-10922 | 7392.8438 | 11645.19 | -4252.3463 | -36.52% | 7369 | 23.8438 | 0.3236% | 1. Inverter 3 has afternoon shading.
Q400 | NY | SOL-10871 | 10540.6225 | N/A |  |  | 10708 | -167.3775 | -1.563%
R003 | NY | SOL-10416 | 11311.75 | 13028.53 | -1716.78 | -13.18% | 11215 | 96.75 | 0.8627% | 1.Site production was low on 12/14 to 12/17 due to snow
R007 | NY | SOL-10417 | 12050.2812 | 15472.87 | -3422.5888 | -22.12% | 20876.16 | -8825.8787 | -42.28% | 1. Actual vs Forcasted delta is showing 42% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
BK16 | NY | SOL-11093 | 11471.375 | 14489.33 | -3017.955 | -20.83% | 11566 | -94.625 | -0.8181% | 1.Site production was low on 12/14 to 12/17 due to snow
Trenton - Trenton East | IL | SOL-11060 | 191540 | 194250.5 | -2710.5 | -1.395% | 175446 | 16094 | 9.173%
Trenton - Trenton West | IL | SOL-11061 | 189455 | 171848.8 | 17606.2 | 10.25% | 177808 | 11647 | 6.55% | 1.Multiple trackers are stuck | 1.SR109332 | 1.pending
Dakota - Dakota Solar 1 | IL | SOL-11113 | 145562 | 152502.3 | -6940.3 | -4.551% | 201696 | -56134 | -27.83% | 1. Inverter 4 is derating on 12/04 at 50kw, reporting temperature sensor fault. inverter was producing at expected rates around 14:00 on 12/19. | 1.SR112210 | 1.completed
X018 | NY | SOL-10418 | 5345.3438 | 6330.121 | -984.7773 | -15.56% | 6480 | -1134.6562 | -17.51% | 1.Inverter 3 having heavy shading issue in morning hours 2. Actual vs Forcasted delta is showing 18% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
Janiak Solar | NY | SOL-10898 | 170216 | 220439 | -50223 | -22.78% | 161233 | 8983 | 5.571% | 1.Site was offline from 10:30 to 13:30 on 12/26 | 1.SR113649 | 1.closed
County Route 11B | NY | SOL-10983 | 185800.5 | 178803 | 6997.5 | 3.914% | N/A |  |  | 1.Inverter 1 tripped offline at 09:40 on 12/06 and back online at 16:05 on 12/08.tech noted that CB 10 was offline and later back online on 12/09 | 1.SR113247 | 1.pending
Barone | NY | SOL-11034 | 230635 | 227015 | 3620 | 1.595% | 244770 | -14135 | -5.775% | 1.Site tripped offline at 12:20 on 12/07 and it came back online at 14:25 on 12/08 2.Inverters tripped offline at 12:25 on 12/27 and it came back online on 12/29 | 1. SR112334 2.SR113692 | 1.Closed 2.pending
Cedarville | IL | SOL-11069 | 127432 | 130623.6 | -3191.6 | -2.443% | 151431.7 | -23999.7 | -15.85% | 1. Actual vs Forcasted delta is showing 16% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
O'Brien Hill #1 | NY | SOL-11098 | 0 | 0 | 0 |  | N/A |  |  | 1. The site has been offline since 03/07. The site will likely remain de-energized until late this year. | 1. SR098278, SR098670 | 1.Pending
O'Brien Hill #2 | NY | SOL-11099 | 222530 | 222410 | 120 | 0.05395% | N/A |  |  | 1. Site tripped offline at 09:05 on 12/10 and it came back online on 12/11 at 08:40 2.All trackers are now stuck on 12/04, approximately a quarter inch of snow fall residual reported nearby. | 1. SR112499 2. SR112060 | 1.Closed 2.closed
Trinity - Freeport | IL | SOL-11057 | 147183 | 133129 | 14054 | 10.56% | 149552 | -2369 | -1.584% | 1.All trackers are now stuck, approximately a quarter inch of snow fall residual reported nearby on 12/04 and selfresolved on 12/05 | 1. SR112060 | 1.Closed
Ransom | NY | SOL-11157 | 232868 | 229038 | 3830 | 1.672% | N/A
Horseheads - Wedge | NY | SOL-11160 | 148532 | 146292 | 2240 | 1.531% | N/A |  |  | 1. Both inverters tripped offline at 12:30 on 12/27 and came back online on 12/29 | 1. SR113693 | 1.Closed
Otisville - Shoddy Hollow | NY | SOL-11185 | 362787 | 343004 | 19783 | 5.768% | N/A |  |  | 1.The meter is missing comms but the inverters are communicating on 11/30 2.Inverters tripped offline at 12:30 on 12/27 and back online on 12/29 2.Inverter 2 is offline on 12/31 | 1.SR111863 2.SR113693 3.SR113917 | 1.Closed 2.closed 3.Closed | SR113917
Wellsville - Chenunda Creek | NY | SOL-11187 | 129912 | 127362 | 2550 | 2.002% | N/A |  |  | 1.31 trackers are currently stuck: #2, 4, 6, 9-13, 32-47, 49, 50, 52, 78-84. - These trackers have a low battery auto stow warning, several are charging, this may be related to the recent snowfall. Issue self resolved on 12/17 | 1. SR112440 | 1.Closed
DC: Washington - Essex Condominium | DC | SOL-10036 | 1114 | 1598.154 | -484.154 | -30.29% | 1998.707 | -884.707 | -44.26% | 1. The site is performing as expected, but the expected and forecasted values are high. A similar event was observed over the past two years.
HI: Waipahu - 94-246 Leoku St - E.F.G. | HI | SOL-10071 | 7154.029 | 7399.643 | -245.614 | -3.319% | 9454.063 | -2300.034 | -24.33% | 1. Inverter 2 was offline at 07:00 on 10/11. denied by customer 2. The meter has been communicating intermittently throughout the month. | 1. SR109524 2. SR100771 | 1.Closed 2.Pending
HI: Waipahu - 94-099 Waipahu St - PV | HI | SOL-10068 | 8335 | 6771.217 | 1563.783 | 23.09% | 9449.005 | -1114.005 | -11.79% | 1.Actual vs Forcasted delta is showing 12% due to Forcasted energy recording low possibly due to data glitch (similar event observe last 2 years).
IL: Prophetstown - 5170 Yager Road (PW) | IL | SOL-11149 | 0 | 45408.39 | -45408.39 | -100% | 168273.8 | -168273.8 | -100% | 1. Site was offline for whole month. | 1. SR110863 | 1. Pending
IL: Viola - Goldenrod - (PW) | IL | SOL-11132 | 340154 | 383746 | -43592 | -11.36% | 444000 | -103846 | -23.39% | 1. All trackers on site were not tracking properly for whole month. 2. Inverters 1.14, 2.04, 2.13, 2.15 and 2.20 were derating at 47kw from 12/01 to 12/15 | 1. SR113569 2. SR112384 | 1. Pending 2. completed
IL: Marengo - Grant - (PW) | IL | SOL-11147 | 160718 | 0 | 160718 |  | 166718.7 | -6000.7 | -3.599% | 1. Inverter 2 was derated to 50kW from 11/10 to 11:15 on 12/19. 2. Weather station was not communicated for whole month. | 1. SR110867 2. SR108392 | 1. Completed 2. Pending
NY: Cambridge - Cambridge (PW) | NY | SOL-11126 | 101010.3292 | 326811.6 | -225801.2708 | -69.09% | 402501 | -301490.6708 | -74.9% | 1. Site has tripped offline at 00:15 on 12/26 and later back online at 12:00 on 12/26. 2. Site was offline from 08:45 on 12/19 to 12:00 on 12/20. 3. Inverter 2 was underproducing by 500kW for whole month. 4. Inverter 2 was offline from 11/29 to 08:00 on 12/02. 5. POA and BPO was not communicated from 07:15 on 12/23. | 1. SR113626 2. SR113177 3. SR113003 4. SR111163 5. SR113452 | 1. Closed 2. Closed 3. Pending 4. Pending 5. Pending | SR113003 | SR111163 | SR113452
NY: Whitesville - Independence North | NY | SOL-11186 | 239295 | N/A |  |  | N/A
IL: Beecher - Cottage Grove North (PW) | IL | SOL-11114 | 135129 | 154715.1 | -19586.1 | -12.66% | 171136 | -36007 | -21.04% | 1. Site was offline from 07:00 on 12/19 to 10:00 on 12/22. 2. Inverter 2 was offline from 10:00 on 12/22 to end of the month. | 1. SR113185 2. SR113455 | 1. Completed 2. Pending
IL: Beecher - Cottage Grove South (PW) | IL | SOL-11115 | 160374 | 227052.3 | -66678.3 | -29.37% | 160390 | -16 | -0.009976% | 1.Site production was low on 12/18 ,12/26 to 12/28 due to snow
IL: Harvard - 9618 US HWY 14 (PW) | IL | SOL-11110 | 144730 | 309259.2 | -164529.2 | -53.2% | 133149 | 11581 | 8.698% | 1.Site production was low on 12/09 , 12/10 , 12/11 ,12/13 , 12/18, 12/22 , 12/26, 12/27, 12/28 due to snow
IL: Beecher - 701 E Goodenow Rd (PW) | IL | SOL-11112 | 147218 | 185050.2 | -37832.2 | -20.44% | 144976 | 2242 | 1.546% | 1. Site was offline from 07:00 on 12/29 to end of the month. | 1. SR113743 | 1. Pending
NY: Stormville - Green Haven - (IRA) | NY | SOL-11151 | 33903314 | N/A |  |  | N/A |  |  | 1. Inverter 23 was offline from 07:00 on 12/05 to end of the month. | 1. SR112320 | 1. Pending
IL: Hillsboro - Anacott (PW) | IL | SOL-11134 | 403700 | N/A |  |  | 476680 | -72980 | -15.31% | 1. Site was de-energised from 16:00 to 18:00 on 12/19. 2. Inverters 1.10, 2.05 and 2.11 are intermittently derating at 50kw during high irradiance from 11/10 to 12/17. | 1. SR113222 2. SR112383 | 1. Closed 2. Completed
IL: Manhattan - Gougar (PW) | IL | SOL-11148 | 94776.515 | 121981.2 | -27204.685 | -22.3% | 178632.9 | -83856.385 | -46.94% | 1.Site tripped offline at 08:45 on 12/06 and it came back online at 14:15 on 12/17 2.Site tripped offline at 15:00 on 12/28 and it came back online at 14:15 12/29 | 1.SR112318 2. SR113699 | 1.Closed 2.Closed
.
Note on D89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter is reporting 0 we have taken total inverter energy as actual energy

## Sites
Portfolio: | Generate Capital
Site DAS Name | Site | State | Update | DAS | SOL#
K026 | K026 | NY |  | PowerTrack | SOL-10356
K041 | K041 | NY |  | PowerTrack | SOL-10357
K043 Brooklyn | K043 | NY |  | PowerTrack | SOL-10358
K058 | K058 | NY |  | PowerTrack | SOL-10360
K115 | K115 | NY |  | PowerTrack | SOL-10361
K152 | K152 | NY |  | PowerTrack | SOL-10362
K166 | K166 | NY |  | PowerTrack | SOL-10363
K206 | K206 | NY |  | PowerTrack | SOL-10927
K251 | K251 | NY |  | PowerTrack | SOL-10365
K269 | K269 | NY |  | PowerTrack | SOL-10366
K273 | K273 | NY |  | PowerTrack | SOL-10367
K287 | K287 | NY |  | PowerTrack | SOL-10919
K298 | K298 | NY |  | PowerTrack | SOL-10368
K335 | K335 | NY |  | PowerTrack | SOL-10370
K345 | K345 | NY |  | PowerTrack | SOL-10920
K445 | K445 | NY |  | PowerTrack | SOL-10373
K495 | K495 | NY |  | PowerTrack | SOL-10374
M020 | M020 | NY |  | PowerTrack | SOL-10380
M092 | M092 | NY |  | PowerTrack | SOL-10383
M143 | M143 | NY |  | PowerTrack | SOL-10384
M144 | M144 | NY |  | PowerTrack | SOL-10385
M167 | M167 | NY |  | PowerTrack | SOL-10386
M188 | M188 | NY |  | PowerTrack | SOL-10387
Elmhurst Hospital | EMHC | NY |  | PowerTrack | SOL-10351
Q008 | Q008 | NY |  | PowerTrack | SOL-10397
Q018 | Q018 | NY |  | PowerTrack | SOL-10398
Q021 | Q021 | NY |  | PowerTrack | SOL-10399
Q025 | Q025 | NY |  | PowerTrack | SOL-10400
Q074 | Q074 | NY |  | PowerTrack | SOL-10402
Q115 | Q115 | NY |  | PowerTrack | SOL-10872
Q139 | Q139 | NY |  | PowerTrack | SOL-10403
Q157 | Q157 | NY |  | PowerTrack | SOL-10404
Q192 | Q192 | NY |  | PowerTrack | SOL-10406
Q210 | Q210 | NY |  | PowerTrack | SOL-10407
Q229 | Q229 | NY |  | PowerTrack | SOL-10408
Q231 | Q231 | NY |  | PowerTrack | SOL-10870
Q405 | Q405 | NY |  | PowerTrack | SOL-10409
Q435 | Q435 | NY |  | PowerTrack | SOL-10923
Q485 | Q485 | NY |  | PowerTrack | SOL-10869
Q490 | Q490 | NY |  | PowerTrack | SOL-10411
Q620 | Q620 | NY |  | PowerTrack | SOL-10867
Queens Museum of Art | QMOA | NY |  | PowerTrack | SOL-10415
X024 | X024 | NY |  | PowerTrack | SOL-10419
38 | X026 | NY |  | PowerTrack | SOL-10420
144 | X090 | NY |  | PowerTrack | SOL-10925
279 | X117 | NY |  | PowerTrack | SOL-10422
293 | X125 | NY |  | PowerTrack | SOL-10423
308 | X134 | NY |  | PowerTrack | SOL-10424
309 | X135 | NY |  | PowerTrack | SOL-10425
X-139 JHS 222 | X139 JHS 222 | NY |  | PowerTrack | SOL-10426
X140 | X140 | NY |  | PowerTrack | SOL-10926
358 | X166 | NY |  | PowerTrack | SOL-10427
Murphy (WaveSun) | Murphy | MN |  | PowerTrack | SOL-10094
Terning (MontSun) | Terning | MN |  | PowerTrack | SOL-10093
Boas Road 04 | Boas Road 04 | NY | FA | Green Power Monitor | SOL-10908
Kelly Bridge Farm | Kelly Bridge Farm | NY | FA | Green Power Monitor | SOL-10911
Pool Brook Farm | Pool Brook Road | NY | FA | Green Power Monitor | SOL-10909
Sackett Lake Farm 1 | Sackett Lake | NY | FA | Green Power Monitor | SOL-10910
Burritt Road | Burritt Road | NY | FA | Green Power Monitor | SOL-10913
Villa Roma 1 | Villa Roma 1 | NY | FA | Green Power Monitor | SOL-10914
Villa Roma 2 | Villa Roma 2 | NY | FA | Green Power Monitor | SOL-10915
Washington 1 | Washington 1 | NY | FA | Green Power Monitor | SOL-10912
Washington 3 | Washington 3 | NY | FA | Green Power Monitor | SOL-10828
Washington 4 | Washington 4 | NY | FA | Green Power Monitor | SOL-10829
Big Tree | Big Tree | NY | FA | Green Power Monitor | SOL-10966
Canoga | Canoga | NY | A | Green Power Monitor | SOL-10965
County Route 84 | County Route 84 | NY | FA | Green Power Monitor | SOL-10967
Donati | Donati | NY | FA | Green Power Monitor | SOL-10968
Henrietta | Henrietta | NY | FA | Green Power Monitor | SOL-10972
NY 70 | NY 70 | NY | FA | Green Power Monitor | SOL-10970
Reid (FFP) | Reid | NY |  | PowerTrack | SOL-10991
Sangolqui | Sangolqui | NY | FA | Green Power Monitor | SOL-10975
State Highway 17B | State Highway 17B | NY | A | Green Power Monitor | SOL-10988
State Route 14A | State Route 14A | NY | FA | Green Power Monitor | SOL-10997
West Creek | West Creek | NY | FA | Green Power Monitor | SOL-10995
Wildflower | Wildflower | NY |  | Green Power Monitor | SOL-10982
Glen Mary 1 | Glen Mary 1 | NY | FA | Green Power Monitor | SOL-10993
Glen Mary 2 | Glen Mary 2 | NY | FA | Green Power Monitor | SOL-10994
Telegraph 1 | Telegraph 1 | NY | FA | Green Power Monitor | SOL-11003
Telegraph 2 | Telegraph 2 | NY | FA | Green Power Monitor | SOL-11004
Cafferty Hill | Cafferty Hill | NY | FA | Green Power Monitor | SOL-10996
Dunkleman | Dunkleman | NY | FA | Green Power Monitor | SOL-11008
Route 19 #1 | Route 19 1 | NY | FA | Green Power Monitor | SOL-11001
Route 19 #2 | Route 19 2 | NY | FA | Green Power Monitor | SOL-11002
Yellow Mills 1 | Yellow Mills 1 | NY | FA | Green Power Monitor | SOL-11006
Yellow Mills 2 | Yellow Mills 2 | NY | FA | Green Power Monitor | SOL-11005
Yellow Mills 3 | Yellow Mills 3 | NY | FA | Green Power Monitor | SOL-11007
Catskill | Catskill | NY | FA | Green Power Monitor | SOL-11021
Eddy Ridge | Eddy Ridge | NY | FA | Green Power Monitor | SOL-11054
Ridgeway #1 | Ridgeway #1 | NY |  | Green Power Monitor | SOL-11018
Rivard 1 | Rivard 1 | NY |  | PowerTrack | SOL-11011
Rivard 2 | Rivard 2 | NY |  | PowerTrack | SOL-11012
Ridgeway #1 | Ridgeway #2 | NY |  | Green Power Monitor | SOL-11027
Spencer | Spencer | NY | FA | Green Power Monitor | SOL-11017
Reisender | Reisender | NY | FA | Green Power Monitor | SOL-10886
Finney | Finney | NY | FA | Green Power Monitor | SOL-10999
Davis Solar | Davis Solar | NY |  | Also Energy API | SOL-10958
Genesee | Genesee | NY | FA | Green Power Monitor | SOL-10951
Landau I | Landau I | NY | FA | Green Power Monitor | SOL-10891
Landau II | Landau II | NY |  | Green Power Monitor | SOL-10895
New Beginnings | New Beginnings | NY | FA | Green Power Monitor | SOL-10890
Guilin Farm Solar | Bullitt Farm Solar, LLC | NY |  | PowerTrack | SOL-10998
Brodhead Solar | Brodhead Solar, LLC | NY |  | PowerTrack | SOL-10899
Svenski | Svenski | NY | FA | Green Power Monitor | SOL-10894
Bantam | Bantam | NY | FA | Green Power Monitor | SOL-10986
Bogart | Bogart | NY | FA | Green Power Monitor | SOL-10887
Dubois | Dubois | NY | F | Green Power Monitor | SOL-10892
Salt Point | Salt Point | NY | FA | Green Power Monitor | SOL-10888
Wheatland 2A | Wheatland 2A | NY | FA | Green Power Monitor | SOL-10971
Wheatland 2B | Wheatland 2B | NY | FA | Green Power Monitor | SOL-10961
Brickchurch | Brickchurch | NY | FA | Green Power Monitor | SOL-10889
McCarthy Solar | McCarthy Solar | NY |  | Green Power Monitor | SOL-10992
Costanza | Costanza | NY | FA | Green Power Monitor | SOL-10907
Lockenhurst Pond | Lockenhurst Pond | NY |  | PowerTrack | SOL-11000
Drinkwater | Drinkwater | NY | FA | Green Power Monitor | SOL-10896
Altamont | Altamont | NY |  | PowerTrack | SOL-11085
Krumkill North | Krumkill North | NY |  | PowerTrack | SOL-11086
Krumkill South | Krumkill South | NY |  | PowerTrack | SOL-11087
X092 | X092 | NY |  | PowerTrack | SOL-11189
X093 | X093 | NY |  | PowerTrack | SOL-10932
X095 | X095 | NY |  | PowerTrack | SOL-10929
X181 | X181 | NY |  | PowerTrack | SOL-10428
X415 | X415 | NY |  | PowerTrack | SOL-10429
K198 | K198 | NY |  | PowerTrack | SOL-10930
K203 | K203 | NY |  | PowerTrack | SOL-11190
K213 | K213 | NY |  | PowerTrack | SOL-11191
K217 | K217 | NY |  | PowerTrack | SOL-10933
K307 | K307 | NY |  | PowerTrack | SOL-10876
K610 | K610 | NY |  | PowerTrack | SOL-11158
M025 | M025 | NY |  | PowerTrack | SOL-10392
M028 | M028 | NY |  | PowerTrack | SOL-10381
Q030 | Q030 | NY |  | PowerTrack | SOL-10878
Q130 | Q130 | NY |  | PowerTrack | SOL-10877
Q196 | Q196 | NY |  | PowerTrack | SOL-10879
Q220 | Q220 | NY |  | PowerTrack | SOL-10873
Q205 | Q205 | NY |  | PowerTrack | SOL-10922
Q400 | Q400 | NY |  | PowerTrack | SOL-10871
R003 | R003 | NY |  | PowerTrack | SOL-10416
R007 | R007 | NY |  | PowerTrack | SOL-10417
BK16 | BK16 | NY |  | PowerTrack | SOL-11093
Trenton East | Trenton - Trenton East | IL |  | PowerTrack | SOL-11060
Trenton West | Trenton - Trenton West | IL |  | PowerTrack | SOL-11061
6274 N Dakota Rd - Stephenson | Dakota - Dakota Solar 1 | IL |  | PowerTrack | SOL-11113
X018 | X018 | NY |  | PowerTrack | SOL-10418
Janiak Solar | Janiak Solar | NY |  | PowerTrack | SOL-10898
County Route 11B | County Route 11B | NY | FA | Green Power Monitor | SOL-10983
Barone | Barone | NY | FA | Green Power Monitor | SOL-11034
Cedarville | Cedarville | IL |  | PowerTrack | SOL-11069
O'Brien Hill #1 | O'Brien Hill #1 | NY |  | Green Power Monitor | SOL-11098
O'Brien Hill #2 | O'Brien Hill #2 | NY |  | Green Power Monitor | SOL-11099
Trinity Freeport | Trinity - Freeport | IL |  | PowerTrack | SOL-11057
Binghamton - Ransom | Ransom | NY |  | Green Power Monitor | SOL-11157
Wedge | Horseheads - Wedge | NY | FA | Green Power Monitor | SOL-11160
hoddy Hollow | Otisville - Shoddy Hollow | NY |  | Green Power Monitor | SOL-11185
Chenunda Creek | Wellsville - Chenunda Creek | NY | FA | Green Power Monitor | SOL-11187
The Essex - DC | DC: Washington - Essex Condominium | DC |  | PowerTrack | SOL-10036
Leoku | HI: Waipahu - 94-246 Leoku St - E.F.G. | HI |  | PowerTrack | SOL-10071
Waipahu | HI: Waipahu - 94-099 Waipahu St - PV | HI |  | PowerTrack | SOL-10068
Yager Road Whiteside Solar 1, LLC | IL: Prophetstown - 5170 Yager Road (PW) | IL |  | PowerTrack | SOL-11149
Goldenrod Solar Project, LLC | IL: Viola - Goldenrod - (PW) | IL |  | PowerTrack | SOL-11132
Grant Highway Solar 1, LLC | IL: Marengo - Grant - (PW) | IL |  | PowerTrack | SOL-11147
Cambridge - Cambridge (PW) | NY: Cambridge - Cambridge (PW) | NY |  | PowerTrack | SOL-11126
Whitesville - Independence North | NY: Whitesville - Independence North | NY |  | Green Power Monitor | SOL-11186
S Cottage Grove Ave - North | IL: Beecher - Cottage Grove North (PW) | IL |  | PowerTrack | SOL-11114
S Cottage Grove Ave - South | IL: Beecher - Cottage Grove South (PW) | IL |  | PowerTrack | SOL-11115
9521 US 14 - McHenry | IL: Harvard - 9618 US HWY 14 (PW) | IL |  | PowerTrack | SOL-11110
Goodenow West | IL: Beecher - 701 E Goodenow Rd (PW) | IL |  | PowerTrack | SOL-11112
NY: Stormville - Green Haven - (IRA) | NY: Stormville - Green Haven - (IRA) | NY |  | Power factors | SOL-11151
Anacott Solar, LLC | IL: Hillsboro - Anacott (PW) | IL |  | PowerTrack | SOL-11134
Gougar Road Solar 1, LLC | IL: Manhattan - Gougar (PW) | IL |  | PowerTrack | SOL-11148