## Year to Date
GoodFinch |  |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  |  | 7290209.9071 | 6742493.3712 | 547716.5359 | 8.123% | 9580238.781 | -2290028.8739 | -23.9%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 66668.5585 | 45601.906 | 21066.6525 | 46.2% | 72559.273 | -5890.7145 | -8.118%
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 210242.5 | 268259.38 | -58016.88 | -21.63% | 297860.68 | -87618.18 | -29.42%
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 80329.7564 | 0 | 80329.7564 |  | 105253.21 | -24923.4536 | -23.68%
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 62367.66 | 77035.77 | -14668.11 | -19.04% | 63917.132 | -1549.472 | -2.424%
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 159465.725 | 147363.06 | 12102.665 | 8.213% | 165877.15 | -6411.425 | -3.865%
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 148322.2159 | 109248.05 | 39074.1659 | 35.77% | 189378.74 | -41056.5241 | -21.68%
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 58479.7743 | 44978.214 | 13501.5603 | 30.02% | 82421.05 | -23941.2757 | -29.05%
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 34278.8934 | 5400.422 | 28878.4714 | 534.7% | 45896.73 | -11617.8366 | -25.31%
AZ: Yuma Airport | AZ | SOL-10754 | 348200 | 498435.7 | -150235.7 | -30.14% | 398037 | -49837 | -12.52%
AZ: Globe - Gila CC | AZ | SOL-10751 | 92163.9128 | 48253.127 | 43910.7858 | 91% | 88236.048 | 3927.8648 | 4.452%
AZ: Payson - Gila CC | AZ | SOL-10748 | 64301.7514 | 28664.282 | 35637.4694 | 124.3% | 58786 | 5515.7514 | 9.383%
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 132565.5 | 26614.73 | 105950.77 | 398.1% | 220819.4 | -88253.9 | -39.97%
AZ: Tempe - SCNM | AZ | SOL-10760 | 378469.38 | 206518.5 | 171950.88 | 83.26% | 417248.57 | -38779.19 | -9.294%
DE: Newark - Clayton Hall | DE | SOL-10820 | 87624 | 93939.015 | -6315.015 | -6.722% | 93474.5 | -5850.5 | -6.259%
DE: Newark - UOD Field House | DE | SOL-10821 | 253874 | 31622.79 | 222251.21 | 702.8% | 229713.163 | 24160.837 | 10.52%
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 51562 | 146154.79 | -94592.79 | -64.72% | 169432.965 | -80287.965 | -47.39%
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 812589 | 830167.866 | -17578.866 | -2.118% | 805286.081 | 7302.919 | 0.9069%
MD: Easton - Shortall | MD | SOL-10091 | 860064 | 716912.34 | 143151.66 | 19.97% | 835721.723 | 24342.277 | 2.913%
MA: Boston - Seaport Solar | MA | SOL-10772 | 327252.5 | 83573.136 | 243679.364 | 291.6% | 388615.09 | -61362.59 | -15.79%
MA: Dedham - Sprague Street | MA | SOL-10773 | 723575 | 0 | 723575 |  | 715281.952 | 8293.048 | 1.159%
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 394414.066 | -394414.066 | -100% | 1461312.08 | -1052088.08 | -72%
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 252927.5 | 304858.77 | -51931.27 | -17.03% | 223788.765 | 29138.735 | 13.02%
MA: Braintree - RCAB | MA | SOL-10838 | 547338 | 627246.671 | -79908.671 | -12.74% | 533838.214 | 13499.786 | 2.529%
NH: Rochester - Portland Street | NH | SOL-10771 | 40966.048 | 34386.583 | 6579.465 | 19.13% | 50366.275 | -9400.227 | -18.66%
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 169143.375 | 62706.34 | 106437.035 | 169.7% | 148612.884 | 20530.491 | 13.81%
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 60755.5 | 76636.51 | -15881.01 | -20.72% | 81287.633 | -20532.133 | -25.26%
NH: Rochester - Rochester MS | NH | SOL-10765 | 149064.6287 | 180150.57 | -31085.9413 | -17.26% | 129519.29 | 19545.3387 | 15.09%
NH Rochester - Spaulding HS | NH | SOL-10767 | 73381.8174 | 66660.673 | 6721.1444 | 10.08% | 63515.391 | 9866.4264 | 15.53%
NH: Rochester - McClelland ES | NH | SOL-10766 | 50123.3118 | 58225.032 | -8101.7202 | -13.91% | 43161.762 | 6961.5498 | 16.13%
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 65477.4473 | 68044.475 | -2567.0277 | -3.773% | 54767.024 | 10710.4233 | 19.56%
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 313523.5312 | 601512.53 | -287988.9988 | -47.88% | 536871 | -223347.4688 | -41.6%
OH: Cleveland - CV Wooster | OH | SOL-10763 | 92953.25 | 0 | 92953.25 |  | 116356.698 | -23403.448 | -20.11%
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 76363 | 96185.008 | -19822.008 | -20.61% | 97246.873 | -20883.873 | -21.48%
PR: Bayamon - Coca Cola | PR | SOL-10073 | 285472 | 420563.696 | -135091.696 | -32.12% | 360933.784 | -75461.784 | -20.91%
PR: Carolina - St. Francis | PR | SOL-10034 | 97107.75 | 257340.815 | -160233.065 | -62.26% | 163499.588 | -66391.838 | -40.61%
DC: Chevy Chase -Sinai | DC | SOL-10028 | 41113.62 | 62917.635 | -21804.015 | -34.65% | 48058.496 | -6944.876 | -14.45%
DC: Washington - Weinberg 1 | DC | SOL-10039 | 7110 | 7202.5987 | -92.5987 | -1.286% | 7601.4122 | -491.4122 | -6.465%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 6866 | 6924.6238 | -58.6238 | -0.8466% | 7392.2508 | -526.2508 | -7.119%
DC: Washington - Weinberg 3 | DC | SOL-10042 | 8127 | 7773.6967 | 353.3033 | 4.545% | 8292.904 | -165.904 | -2.001%

## 1st Qtr
GoodFinch |  |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 0 | 0 | 0 |  | 0 | 0
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 0 | 0 | 0 |  | 0 | 0
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 0 | 0 | 0 |  | 0 | 0
AZ: Yuma Airport | AZ | SOL-10754 | 0 | 0 | 0 |  | 0 | 0
AZ: Globe - Gila CC | AZ | SOL-10751 | 0 | 0 | 0 |  | 0 | 0
AZ: Payson - Gila CC | AZ | SOL-10748 | 0 | 0 | 0 |  | 0 | 0
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - SCNM | AZ | SOL-10760 | 0 | 0 | 0 |  | 0 | 0
DE: Newark - Clayton Hall | DE | SOL-10820 | 0 | 0 | 0 |  | 0 | 0
DE: Newark - UOD Field House | DE | SOL-10821 | 0 | 0 | 0 |  | 0 | 0
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 0 | 0 | 0 |  | 0 | 0
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 0 | 0 | 0 |  | 0 | 0
MD: Easton - Shortall | MD | SOL-10091 | 0 | 0 | 0 |  | 0 | 0
MA: Boston - Seaport Solar | MA | SOL-10772 | 0 | 0 | 0 |  | 0 | 0
MA: Dedham - Sprague Street | MA | SOL-10773 | 0 | 0 | 0 |  | 0 | 0
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 0 | 0 |  | 0 | 0
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 0 | 0 | 0 |  | 0 | 0
MA: Braintree - RCAB | MA | SOL-10838 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - Portland Street | NH | SOL-10771 | 0 | 0 | 0 |  | 0 | 0
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 0 | 0 | 0 |  | 0 | 0
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - Rochester MS | NH | SOL-10765 | 0 | 0 | 0 |  | 0 | 0
NH Rochester - Spaulding HS | NH | SOL-10767 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - McClelland ES | NH | SOL-10766 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 0 | 0 | 0 |  | 0 | 0
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 0 | 0 | 0 |  | 0 | 0
OH: Cleveland - CV Wooster | OH | SOL-10763 | 0 | 0 | 0 |  | 0 | 0
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 0 | 0 | 0 |  | 0 | 0
PR: Bayamon - Coca Cola | PR | SOL-10073 | 0 | 0 | 0 |  | 0 | 0
PR: Carolina - St. Francis | PR | SOL-10034 | 0 | 0 | 0 |  | 0 | 0
DC: Chevy Chase -Sinai | DC | SOL-10028 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Weinberg 1 | DC | SOL-10039 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Weinberg 2 | DC | SOL-10045 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Weinberg 3 | DC | SOL-10042 | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
GoodFinch |  |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  |  | #REF! | #REF! | #REF! | 0% | #REF! | #REF! | 0%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 0 | 0 | 0 |  | 0 | 0
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 0 | 0 | 0 |  | 0 | 0
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 0 | 0 | 0 |  | 0 | 0
AZ: Yuma Airport | AZ | SOL-10754 | 0 | 0 | 0 |  | 0 | 0
AZ: Globe - Gila CC | AZ | SOL-10751 | 0 | 0 | 0 |  | 0 | 0
AZ: Payson - Gila CC | AZ | SOL-10748 | 0 | 0 | 0 |  | 0 | 0
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 0 | 0 | 0 |  | 0 | 0
AZ: Tempe - SCNM | AZ | SOL-10760 | 0 | 0 | 0 |  | 0 | 0
DE: Newark - Clayton Hall | DE | SOL-10820 | 0 | 0 | 0 |  | 0 | 0
DE: Newark - UOD Field House | DE | SOL-10821 | 0 | 0 | 0 |  | 0 | 0
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 0 | 0 | 0 |  | 0 | 0
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 0 | 0 | 0 |  | 0 | 0
MD: Easton - Shortall | MD | SOL-10091 | 0 | 0 | 0 |  | 0 | 0
MA: Boston - Seaport Solar | MA | SOL-10772 | 0 | 0 | 0 |  | 0 | 0
MA: Dedham - Sprague Street | MA | SOL-10773 | 0 | 0 | 0 |  | 0 | 0
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 0 | 0 |  | 0 | 0
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 0 | 0 | 0 |  | 0 | 0
MA: Braintree - RCAB | MA | SOL-10838 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - Portland Street | NH | SOL-10771 | 0 | 0 | 0 |  | 0 | 0
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 0 | 0 | 0 |  | 0 | 0
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - Rochester MS | NH | SOL-10765 | 0 | 0 | 0 |  | 0 | 0
NH Rochester - Spaulding HS | NH | SOL-10767 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - McClelland ES | NH | SOL-10766 | 0 | 0 | 0 |  | 0 | 0
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 0 | 0 | 0 |  | 0 | 0
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 0 | 0 | 0 |  | 0 | 0
OH: Cleveland - CV Wooster | OH | SOL-10763 | 0 | 0 | 0 |  | 0 | 0
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 0 | 0 | 0 |  | 0 | 0
PR: Bayamon - Coca Cola | PR | SOL-10073 | 0 | 0 | 0 |  | 0 | 0
PR: Carolina - St. Francis | PR | SOL-10034 | 0 | 0 | 0 |  | 0 | 0
DC: Chevy Chase -Sinai | DC | SOL-10028 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Weinberg 1 | DC | SOL-10039 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Weinberg 2 | DC | SOL-10045 | 0 | 0 | 0 |  | 0 | 0
DC: Washington - Weinberg 3 | DC | SOL-10042 | 0 | 0 | 0 |  | 0 | 0
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!
|  | #VALUE! | #REF! | #REF! |  |  | #REF! | #REF!

## 3rd Qtr
GoodFinch |  |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  |  | 4552224.5721 | 4128083.687 | 424140.8851 | 10.27% | 6074920.682 | -1522696.1099 | -25.07%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 38700.2121 | 24795.159 | 13905.0531 | 56.08% | 39775.16 | -1074.9479 | -2.703%
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 132403 | 162791.66 | -30388.66 | -18.67% | 189224.45 | -56821.45 | -30.03%
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 49165.3794 | 0 | 49165.3794 |  | 56457.74 | -7292.3606 | -12.92%
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 35641.2692 | 42048.56 | -6407.2908 | -15.24% | 40386.94 | -4745.6708 | -11.75%
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 88185.55 | 94126.23 | -5940.68 | -6.311% | 94413.2 | -6227.65 | -6.596%
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 85195.6661 | 68542.1 | 16653.5661 | 24.3% | 93559.31 | -8363.6439 | -8.939%
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 34665.0096 | 28219.264 | 6445.7456 | 22.84% | 41521.52 | -6856.5104 | -16.51%
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 17824.3096 | 0 | 17824.3096 |  | 29012.578 | -11188.2684 | -38.56%
AZ: Yuma Airport | AZ | SOL-10754 | 181747 | 266025.68 | -84278.68 | -31.68% | 224061 | -42314 | -18.89%
AZ: Globe - Gila CC | AZ | SOL-10751 | 54507.0764 | 23486.82 | 31020.2564 | 132.1% | 51509.5 | 2997.5764 | 5.819%
AZ: Payson - Gila CC | AZ | SOL-10748 | 37246.0788 | 17334.666 | 19911.4128 | 114.9% | 38124 | -877.9212 | -2.303%
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 86754.7 | 0 | 86754.7 |  | 139347.41 | -52592.71 | -37.74%
AZ: Tempe - SCNM | AZ | SOL-10760 | 209268 | 127773.75 | 81494.25 | 63.78% | 250842.95 | -41574.95 | -16.57%
DE: Newark - Clayton Hall | DE | SOL-10820 | 58239 | 62809.022 | -4570.022 | -7.276% | 54137.888 | 4101.112 | 7.575%
DE: Newark - UOD Field House | DE | SOL-10821 | 155312 | 0 | 155312 |  | 134604.393 | 20707.607 | 15.38%
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 14362 | 96729.296 | -82367.296 | -85.15% | 102169.337 | -50224.337 | -49.16%
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 461497 | 459534.486 | 1962.514 | 0.4271% | 472980.281 | -11483.281 | -2.428%
MD: Easton - Shortall | MD | SOL-10091 | 513232 | 491705.99 | 21526.01 | 4.378% | 469954.773 | 43277.227 | 9.209%
MA: Boston - Seaport Solar | MA | SOL-10772 | 234036.5 | 43678.348 | 190358.152 | 435.8% | 217087.45 | 16949.05 | 7.807%
MA: Dedham - Sprague Street | MA | SOL-10773 | 503914 | 0 | 503914 |  | 484083.522 | 19830.478 | 4.096%
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 195335.436 | -195335.436 | -100% | 1033753.29 | -624529.29 | -60.41%
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 213326.375 | 249325.24 | -35998.865 | -14.44% | 188907.554 | 24418.821 | 12.93%
MA: Braintree - RCAB | MA | SOL-10838 | 395726.5 | 468500.2 | -72773.7 | -15.53% | 373966.05 | 21760.45 | 5.819%
NH: Rochester - Portland Street | NH | SOL-10771 | 31120.752 | 23135.202 | 7985.55 | 34.52% | 26479.246 | 4641.506 | 17.53%
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 124214.625 | 12514.94 | 111699.685 | 892.5% | 98432.599 | 25782.026 | 26.19%
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 13129 | 14176.25 | -1047.25 | -7.387% | 30672 | -17543 | -57.2%
NH: Rochester - Rochester MS | NH | SOL-10765 | 108342.1215 | 116658.16 | -8316.0385 | -7.129% | 85816.61 | 22525.5114 | 26.25%
NH Rochester - Spaulding HS | NH | SOL-10767 | 54721.1862 | 46019.406 | 8701.7802 | 18.91% | 43005.701 | 11715.4852 | 27.24%
NH: Rochester - McClelland ES | NH | SOL-10766 | 36952.3746 | 39607.794 | -2655.4194 | -6.704% | 28592.626 | 8359.7486 | 29.24%
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 49977.0711 | 48284.52 | 1692.5511 | 3.505% | 36441.56 | 13535.5111 | 37.14%
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 198170.1953 | 409439.9 | -211269.7047 | -51.6% | 362873 | -164702.8047 | -45.39%
OH: Cleveland - CV Wooster | OH | SOL-10763 | 62873 | 0 | 62873 |  | 82314.56 | -19441.56 | -23.62%
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 39747 | 52433.288 | -12686.288 | -24.2% | 63433.986 | -23686.986 | -37.34%
PR: Bayamon - Coca Cola | PR | SOL-10073 | 139785 | 230557.806 | -90772.806 | -39.37% | 239482.764 | -99697.764 | -41.63%
PR: Carolina - St. Francis | PR | SOL-10034 | 51529.5 | 158682.105 | -107152.605 | -67.53% | 110532.028 | -59002.528 | -53.38%
DC: Chevy Chase -Sinai | DC | SOL-10028 | 26516.12 | 39967.95 | -13451.83 | -33.66% | 32059.843 | -5543.723 | -17.29%
DC: Washington - Weinberg 1 | DC | SOL-10039 | 4665 | 4724.671 | -59.671 | -1.263% | 4870.585 | -205.585 | -4.221%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 4324 | 4227.74 | 96.26 | 2.277% | 4816.788 | -492.788 | -10.23%
DC: Washington - Weinberg 3 | DC | SOL-10042 | 5209 | 4892.048 | 316.952 | 6.479% | 5216.49 | -7.49 | -0.1436%

## 4th Qtr
GoodFinch |  |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  |  | 2737985.335 | 2614409.6842 | 123575.6508 | 4.727% | 3505318.099 | -767332.764 | -21.89%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 27968.3464 | 20806.747 | 7161.5994 | 34.42% | 32784.113 | -4815.7666 | -14.69%
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 77839.5 | 105467.72 | -27628.22 | -26.2% | 108636.23 | -30796.73 | -28.35%
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 31164.377 | 0 | 31164.377 |  | 48795.47 | -17631.093 | -36.13%
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 26726.3908 | 34987.21 | -8260.8192 | -23.61% | 23530.192 | 3196.1988 | 13.58%
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 71280.175 | 53236.83 | 18043.345 | 33.89% | 71463.95 | -183.775 | -0.2572%
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 63126.5497 | 40705.95 | 22420.5997 | 55.08% | 95819.43 | -32692.8803 | -34.12%
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 23814.7647 | 16758.95 | 7055.8147 | 42.1% | 40899.53 | -17084.7653 | -41.77%
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 16454.5838 | 5400.422 | 11054.1618 | 204.7% | 16884.152 | -429.5682 | -2.544%
AZ: Yuma Airport | AZ | SOL-10754 | 166453 | 232410.02 | -65957.02 | -28.38% | 173976 | -7523 | -4.324%
AZ: Globe - Gila CC | AZ | SOL-10751 | 37656.8364 | 24766.307 | 12890.5294 | 52.05% | 36726.548 | 930.2884 | 2.533%
AZ: Payson - Gila CC | AZ | SOL-10748 | 27055.6726 | 11329.616 | 15726.0566 | 138.8% | 20662 | 6393.6726 | 30.94%
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 45810.8 | 26614.73 | 19196.07 | 72.13% | 81471.99 | -35661.19 | -43.77%
AZ: Tempe - SCNM | AZ | SOL-10760 | 169201.38 | 78744.75 | 90456.63 | 114.9% | 166405.62 | 2795.76 | 1.68%
DE: Newark - Clayton Hall | DE | SOL-10820 | 29385 | 31129.993 | -1744.993 | -5.606% | 39336.612 | -9951.612 | -25.3%
DE: Newark - UOD Field House | DE | SOL-10821 | 98562 | 31622.79 | 66939.21 | 211.7% | 95108.77 | 3453.23 | 3.631%
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 37200 | 49425.494 | -12225.494 | -24.74% | 67263.628 | -30063.628 | -44.7%
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 351092 | 370633.38 | -19541.38 | -5.272% | 332305.8 | 18786.2 | 5.653%
MD: Easton - Shortall | MD | SOL-10091 | 346832 | 225206.35 | 121625.65 | 54.01% | 365766.95 | -18934.95 | -5.177%
MA: Boston - Seaport Solar | MA | SOL-10772 | 93216 | 39894.788 | 53321.212 | 133.7% | 171527.64 | -78311.64 | -45.66%
MA: Dedham - Sprague Street | MA | SOL-10773 | 219661 | 0 | 219661 |  | 231198.43 | -11537.43 | -4.99%
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 199078.63 | -199078.63 | -100% | 427558.79 | -427558.79 | -100%
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 39601.125 | 55533.53 | -15932.405 | -28.69% | 34881.211 | 4719.914 | 13.53%
MA: Braintree - RCAB | MA | SOL-10838 | 151611.5 | 158746.471 | -7134.971 | -4.495% | 159872.164 | -8260.664 | -5.167%
NH: Rochester - Portland Street | NH | SOL-10771 | 9845.296 | 11251.381 | -1406.085 | -12.5% | 23887.029 | -14041.733 | -58.78%
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 44928.75 | 50191.4 | -5262.65 | -10.49% | 50180.285 | -5251.535 | -10.47%
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 47626.5 | 62460.26 | -14833.76 | -23.75% | 50615.633 | -2989.133 | -5.906%
NH: Rochester - Rochester MS | NH | SOL-10765 | 40722.5073 | 63492.41 | -22769.9027 | -35.86% | 43702.68 | -2980.1727 | -6.819%
NH Rochester - Spaulding HS | NH | SOL-10767 | 18660.6311 | 20641.267 | -1980.6359 | -9.596% | 20509.69 | -1849.0589 | -9.016%
NH: Rochester - McClelland ES | NH | SOL-10766 | 13170.9372 | 18617.238 | -5446.3008 | -29.25% | 14569.136 | -1398.1988 | -9.597%
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 15500.3762 | 19759.955 | -4259.5788 | -21.56% | 18325.464 | -2825.0878 | -15.42%
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 115353.3359 | 192072.63 | -76719.2941 | -39.94% | 173998 | -58644.6641 | -33.7%
OH: Cleveland - CV Wooster | OH | SOL-10763 | 30080.25 | 0 | 30080.25 |  | 34042.138 | -3961.888 | -11.64%
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 36616 | 43751.72 | -7135.72 | -16.31% | 33812.887 | 2803.113 | 8.29%
PR: Bayamon - Coca Cola | PR | SOL-10073 | 145687 | 190005.89 | -44318.89 | -23.33% | 121451.02 | 24235.98 | 19.96%
PR: Carolina - St. Francis | PR | SOL-10034 | 45578.25 | 98658.71 | -53080.46 | -53.8% | 52967.56 | -7389.31 | -13.95%
DC: Chevy Chase -Sinai | DC | SOL-10028 | 14597.5 | 22949.685 | -8352.185 | -36.39% | 15998.653 | -1401.153 | -8.758%
DC: Washington - Weinberg 1 | DC | SOL-10039 | 2445 | 2477.9277 | -32.9277 | -1.329% | 2730.8272 | -285.8272 | -10.47%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 2542 | 2696.8838 | -154.8838 | -5.743% | 2575.4628 | -33.4628 | -1.299%
DC: Washington - Weinberg 3 | DC | SOL-10042 | 2918 | 2881.6487 | 36.3513 | 1.261% | 3076.414 | -158.414 | -5.149%

## Jan
GoodFinch |  |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748
AZ: Tempe - ASU - Fulton | AZ | SOL-10749
AZ: Superior - JFK Elementary | AZ | SOL-10758
AZ: Tempe - ASU - Noble | AZ | SOL-10750
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751
AZ: Tempe - ASU - PE East | AZ | SOL-10752
AZ: Tempe - ASU - Schwada | AZ | SOL-10753
AZ: Phoenix - Starshine Academy | AZ | SOL-10757
AZ: Yuma Airport | AZ | SOL-10754
AZ: Globe - Gila CC | AZ | SOL-10751
AZ: Payson - Gila CC | AZ | SOL-10748
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759
AZ: Tempe - SCNM | AZ | SOL-10760
DE: Newark - Clayton Hall | DE | SOL-10820
DE: Newark - UOD Field House | DE | SOL-10821
DE: Newark - UOD 461 Wyoming | DE | SOL-10819
MD: Presston - Bird-in-Hand | MD | SOL-10092
MD: Easton - Shortall | MD | SOL-10091
MA: Boston - Seaport Solar | MA | SOL-10772
MA: Dedham - Sprague Street | MA | SOL-10773
MA: Boston - Summer Street | MA | SOL-10764
MA: Leominster - Spectro Coatings | MA | SOL-10074
MA: Braintree - RCAB | MA | SOL-10838
NH: Rochester - Portland Street | NH | SOL-10771
NH: Portsmouth - Portsmouth HS | NH | SOL-10769
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770
NH: Rochester - Rochester MS | NH | SOL-10765
NH Rochester - Spaulding HS | NH | SOL-10767
NH: Rochester - McClelland ES | NH | SOL-10766
NH: Rochester - Brock St Vocational | NH | SOL-10768
OH: Cleveland - CV Kinsman | OH | SOL-10762
OH: Cleveland - CV Wooster | OH | SOL-10763
PR: Aguadilla - Coca Cola | PR | SOL-10072
PR: Bayamon - Coca Cola | PR | SOL-10073
PR: Carolina - St. Francis | PR | SOL-10034
DC: Chevy Chase -Sinai | DC | SOL-10028
DC: Washington - Weinberg 1 | DC | SOL-10039
DC: Washington - Weinberg 2 | DC | SOL-10045
DC: Washington - Weinberg 3 | DC | SOL-10042

## Feb
GoodFinch |  |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748
AZ: Tempe - ASU - Fulton | AZ | SOL-10749
AZ: Superior - JFK Elementary | AZ | SOL-10758
AZ: Tempe - ASU - Noble | AZ | SOL-10750
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751
AZ: Tempe - ASU - PE East | AZ | SOL-10752
AZ: Tempe - ASU - Schwada | AZ | SOL-10753
AZ: Phoenix - Starshine Academy | AZ | SOL-10757
AZ: Yuma Airport | AZ | SOL-10754
AZ: Globe - Gila CC | AZ | SOL-10751
AZ: Payson - Gila CC | AZ | SOL-10748
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759
AZ: Tempe - SCNM | AZ | SOL-10760
DE: Newark - Clayton Hall | DE | SOL-10820
DE: Newark - UOD Field House | DE | SOL-10821
DE: Newark - UOD 461 Wyoming | DE | SOL-10819
MD: Presston - Bird-in-Hand | MD | SOL-10092
MD: Easton - Shortall | MD | SOL-10091
MA: Boston - Seaport Solar | MA | SOL-10772
MA: Dedham - Sprague Street | MA | SOL-10773
MA: Boston - Summer Street | MA | SOL-10764
MA: Leominster - Spectro Coatings | MA | SOL-10074
MA: Braintree - RCAB | MA | SOL-10838
NH: Rochester - Portland Street | NH | SOL-10771
NH: Portsmouth - Portsmouth HS | NH | SOL-10769
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770
NH: Rochester - Rochester MS | NH | SOL-10765
NH Rochester - Spaulding HS | NH | SOL-10767
NH: Rochester - McClelland ES | NH | SOL-10766
NH: Rochester - Brock St Vocational | NH | SOL-10768
OH: Cleveland - CV Kinsman | OH | SOL-10762
OH: Cleveland - CV Wooster | OH | SOL-10763
PR: Aguadilla - Coca Cola | PR | SOL-10072
PR: Bayamon - Coca Cola | PR | SOL-10073
PR: Carolina - St. Francis | PR | SOL-10034
DC: Chevy Chase -Sinai | DC | SOL-10028
DC: Washington - Weinberg 1 | DC | SOL-10039
DC: Washington - Weinberg 2 | DC | SOL-10045
DC: Washington - Weinberg 3 | DC | SOL-10042

## Mar
GoodFinch |  |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748
AZ: Tempe - ASU - Fulton | AZ | SOL-10749
AZ: Superior - JFK Elementary | AZ | SOL-10758
AZ: Tempe - ASU - Noble | AZ | SOL-10750
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751
AZ: Tempe - ASU - PE East | AZ | SOL-10752
AZ: Tempe - ASU - Schwada | AZ | SOL-10753
AZ: Phoenix - Starshine Academy | AZ | SOL-10757
AZ: Yuma Airport | AZ | SOL-10754
AZ: Globe - Gila CC | AZ | SOL-10751
AZ: Payson - Gila CC | AZ | SOL-10748
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759
AZ: Tempe - SCNM | AZ | SOL-10760
DE: Newark - Clayton Hall | DE | SOL-10820
DE: Newark - UOD Field House | DE | SOL-10821
DE: Newark - UOD 461 Wyoming | DE | SOL-10819
MD: Presston - Bird-in-Hand | MD | SOL-10092
MD: Easton - Shortall | MD | SOL-10091
MA: Boston - Seaport Solar | MA | SOL-10772
MA: Dedham - Sprague Street | MA | SOL-10773
MA: Boston - Summer Street | MA | SOL-10764
MA: Leominster - Spectro Coatings | MA | SOL-10074
MA: Braintree - RCAB | MA | SOL-10838
NH: Rochester - Portland Street | NH | SOL-10771
NH: Portsmouth - Portsmouth HS | NH | SOL-10769
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770
NH: Rochester - Rochester MS | NH | SOL-10765
NH Rochester - Spaulding HS | NH | SOL-10767
NH: Rochester - McClelland ES | NH | SOL-10766
NH: Rochester - Brock St Vocational | NH | SOL-10768
OH: Cleveland - CV Kinsman | OH | SOL-10762
OH: Cleveland - CV Wooster | OH | SOL-10763
PR: Aguadilla - Coca Cola | PR | SOL-10072
PR: Bayamon - Coca Cola | PR | SOL-10073
PR: Carolina - St. Francis | PR | SOL-10034
DC: Chevy Chase -Sinai | DC | SOL-10028
DC: Washington - Weinberg 1 | DC | SOL-10039
DC: Washington - Weinberg 2 | DC | SOL-10045
DC: Washington - Weinberg 3 | DC | SOL-10042
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
|  | #VALUE! | [9 empty] | SR098594 | SR098779 | SR098902
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!

## Apr
GoodFinch |  |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748
AZ: Tempe - ASU - Fulton | AZ | SOL-10749
AZ: Superior - JFK Elementary | AZ | SOL-10758
AZ: Tempe - ASU - Noble | AZ | SOL-10750
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751
AZ: Tempe - ASU - PE East | AZ | SOL-10752
AZ: Tempe - ASU - Schwada | AZ | SOL-10753
AZ: Phoenix - Starshine Academy | AZ | SOL-10757
AZ: Yuma Airport | AZ | SOL-10754
AZ: Globe - Gila CC | AZ | SOL-10751
AZ: Payson - Gila CC | AZ | SOL-10748
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759
AZ: Tempe - SCNM | AZ | SOL-10760
DE: Newark - Clayton Hall | DE | SOL-10820
DE: Newark - UOD Field House | DE | SOL-10821
DE: Newark - UOD 461 Wyoming | DE | SOL-10819
MD: Presston - Bird-in-Hand | MD | SOL-10092
MD: Easton - Shortall | MD | SOL-10091
MA: Boston - Seaport Solar | MA | SOL-10772
MA: Dedham - Sprague Street | MA | SOL-10773
MA: Boston - Summer Street | MA | SOL-10764
MA: Leominster - Spectro Coatings | MA | SOL-10074
MA: Braintree - RCAB | MA | SOL-10838
NH: Rochester - Portland Street | NH | SOL-10771
NH: Portsmouth - Portsmouth HS | NH | SOL-10769
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770
NH: Rochester - Rochester MS | NH | SOL-10765
NH Rochester - Spaulding HS | NH | SOL-10767
NH: Rochester - McClelland ES | NH | SOL-10766
NH: Rochester - Brock St Vocational | NH | SOL-10768
OH: Cleveland - CV Kinsman | OH | SOL-10762
OH: Cleveland - CV Wooster | OH | SOL-10763
PR: Aguadilla - Coca Cola | PR | SOL-10072
PR: Bayamon - Coca Cola | PR | SOL-10073
PR: Carolina - St. Francis | PR | SOL-10034
DC: Chevy Chase -Sinai | DC | SOL-10028
DC: Washington - Weinberg 1 | DC | SOL-10039
DC: Washington - Weinberg 2 | DC | SOL-10045
DC: Washington - Weinberg 3 | DC | SOL-10042

## May
GoodFinch |  |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748
AZ: Tempe - ASU - Fulton | AZ | SOL-10749
AZ: Superior - JFK Elementary | AZ | SOL-10758
AZ: Tempe - ASU - Noble | AZ | SOL-10750
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751
AZ: Tempe - ASU - PE East | AZ | SOL-10752
AZ: Tempe - ASU - Schwada | AZ | SOL-10753
AZ: Phoenix - Starshine Academy | AZ | SOL-10757
AZ: Yuma Airport | AZ | SOL-10754
AZ: Globe - Gila CC | AZ | SOL-10751
AZ: Payson - Gila CC | AZ | SOL-10748
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759
AZ: Tempe - SCNM | AZ | SOL-10760
DE: Newark - Clayton Hall | DE | SOL-10820
DE: Newark - UOD Field House | DE | SOL-10821
DE: Newark - UOD 461 Wyoming | DE | SOL-10819
MD: Presston - Bird-in-Hand | MD | SOL-10092
MD: Easton - Shortall | MD | SOL-10091
MA: Boston - Seaport Solar | MA | SOL-10772
MA: Dedham - Sprague Street | MA | SOL-10773
MA: Boston - Summer Street | MA | SOL-10764
MA: Leominster - Spectro Coatings | MA | SOL-10074
MA: Braintree - RCAB | MA | SOL-10838
NH: Rochester - Portland Street | NH | SOL-10771
NH: Portsmouth - Portsmouth HS | NH | SOL-10769
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770
NH: Rochester - Rochester MS | NH | SOL-10765
NH Rochester - Spaulding HS | NH | SOL-10767
NH: Rochester - McClelland ES | NH | SOL-10766
NH: Rochester - Brock St Vocational | NH | SOL-10768
OH: Cleveland - CV Kinsman | OH | SOL-10762
OH: Cleveland - CV Wooster | OH | SOL-10763
PR: Aguadilla - Coca Cola | PR | SOL-10072
PR: Bayamon - Coca Cola | PR | SOL-10073
PR: Carolina - St. Francis | PR | SOL-10034
DC: Chevy Chase -Sinai | DC | SOL-10028
DC: Washington - Weinberg 1 | DC | SOL-10039
DC: Washington - Weinberg 2 | DC | SOL-10045
DC: Washington - Weinberg 3 | DC | SOL-10042

## Jun
GoodFinch |  |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748
AZ: Tempe - ASU - Fulton | AZ | SOL-10749
AZ: Superior - JFK Elementary | AZ | SOL-10758
AZ: Tempe - ASU - Noble | AZ | SOL-10750
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751
AZ: Tempe - ASU - PE East | AZ | SOL-10752
AZ: Tempe - ASU - Schwada | AZ | SOL-10753
AZ: Phoenix - Starshine Academy | AZ | SOL-10757
AZ: Yuma Airport | AZ | SOL-10754
AZ: Globe - Gila CC | AZ | SOL-10751
AZ: Payson - Gila CC | AZ | SOL-10748
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759
AZ: Tempe - SCNM | AZ | SOL-10760
DE: Newark - Clayton Hall | DE | SOL-10820
DE: Newark - UOD Field House | DE | SOL-10821
DE: Newark - UOD 461 Wyoming | DE | SOL-10819
MD: Presston - Bird-in-Hand | MD | SOL-10092
MD: Easton - Shortall | MD | SOL-10091
MA: Boston - Seaport Solar | MA | SOL-10772
MA: Dedham - Sprague Street | MA | SOL-10773
MA: Boston - Summer Street | MA | SOL-10764
MA: Leominster - Spectro Coatings | MA | SOL-10074
MA: Braintree - RCAB | MA | SOL-10838
NH: Rochester - Portland Street | NH | SOL-10771
NH: Portsmouth - Portsmouth HS | NH | SOL-10769
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770
NH: Rochester - Rochester MS | NH | SOL-10765
NH Rochester - Spaulding HS | NH | SOL-10767
NH: Rochester - McClelland ES | NH | SOL-10766
NH: Rochester - Brock St Vocational | NH | SOL-10768
OH: Cleveland - CV Kinsman | OH | SOL-10762
OH: Cleveland - CV Wooster | OH | SOL-10763
PR: Aguadilla - Coca Cola | PR | SOL-10072
PR: Bayamon - Coca Cola | PR | SOL-10073
PR: Carolina - St. Francis | PR | SOL-10034
DC: Chevy Chase -Sinai | DC | SOL-10028
DC: Washington - Weinberg 1 | DC | SOL-10039
DC: Washington - Weinberg 2 | DC | SOL-10045
DC: Washington - Weinberg 3 | DC | SOL-10042

## Jul
GoodFinch |  |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  |  | 1510344 | 1434979.737 | 75364.263 | 5.252% | 2234725 | -724381 | -32.41% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 13735 | 8817 | 4918 | 55.78% | 13565 | 170 | 1.253%
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 51105 | 60590 | -9485 | -15.65% | 68756 | -17651 | -25.67% | 1. The weather station has been reporting erroneous values during evening hours, showing readings around 600–800 W/m², while nearby sites are reporting approximately 300 W/m². | 1. SR101016
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 12132 | N/A |  |  | 18696 | -6564 | -35.11% | 1. Meter 1 did not communicate from 07/02 and production of inverter 1 cannot be confirmed. Upon arrival technician found dead squirrels on meter enclosure and also a blown fuse on phase B at utility disconnect later it came back online at 11:00AM on 07/31 | 1. SR103955
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 12583 | 15025 | -2442 | -16.25% | 15254 | -2671 | -17.51% | 1. Low production/generation due to low irradiance on 07/20
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 34338 | 35478 | -1140 | -3.213% | 31619 | 2719 | 8.599% | 1. Inverter 2 underperforming by 10 kW (2 strings) for whole month | 1. SR104268
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 30212 | 25953 | 4259 | 16.41% | 31935 | -1723 | -5.395%
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 9177 | 10685 | -1508 | -14.11% | 13894 | -4717 | -33.95% | 1.Site has been repeatedly tripping offline since it was reenergized on 7/22, and was online with occasional spikes in production | 1. SR105035 ,SR104591
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 6048 | N/A |  |  | 11002 | -4954 | -45.03% | 1.Meter production dropping to zero on Multiple days throughout the month, but not consistently.Replacement is still inprogress for meter and 12 broken modules replacement. | 1.SR099666
AZ: Yuma Airport | AZ | SOL-10754 | 66601 | 94130 | -27529 | -29.25% | 82137 | -15536 | -18.91% | 2. Site trips offline in the afternoon. Some inverter(s) trip offline mid morning as well. (site does not have inverter communications in PowerTrack). | 2. SR105159
AZ: Globe - Gila CC | AZ | SOL-10751 | 20373 | 8836.737 | 11536.263 | 130.5% | 18652 | 1721 | 9.227% | 1.Inverters 1 & 2 are operational but not communicating. Further troubleshooting is needed to resolve both the underperformance and communication issues of Inverter 1&2. | 1. SR101037
AZ: Payson - Gila CC | AZ | SOL-10748 | 15206 | 6559 | 8647 | 131.8% | 15449 | -243 | -1.573%
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 32820 | N/A |  |  | 52037 | -19217 | -36.93% | 1. Expected values are too low observed during monthly reports. The weather station at site is virtual weather station. | 1.SR093028
AZ: Tempe - SCNM | AZ | SOL-10760 | 67508 | 49080 | 18428 | 37.55% | 91007 | -23499 | -25.82% | 1.Meter build 5 & 6 is dropping by 20 kW on most days, possibly two inverters tripping offline | 1.SR103804
DE: Newark - Clayton Hall | DE | SOL-10820 | 21726 | 23827 | -2101 | -8.818% | 20228 | 1498 | 7.406% | 2.Meter Build 8 & 9 contiously tripping and self-resolving through out the month | 2.SR105439
DE: Newark - UOD Field House | DE | SOL-10821 | 55764 | N/A |  |  | 49697 | 6067 | 12.21% | 1.Inverter 2 has been sporadically derating during high irradiance days. | 1.SR091894
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | - | 36217 |  |  | 37583 |  |  | 1.Inverter was offline since 06/17.Technician checked in and found that line 3 AC bus bar in inverter is corroded with thermal marks and 5A ground fault fuse was blown.He mentioned that the inverter will be de-energized until the parts are replaced. | 1. SR103078
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 145779 | 144639 | 1140 | 0.7882% | 179659 | -33880 | -18.86% | 1. Inverter 4 is derating at 20kW from 06/23and reporting "Fans are defective Sensor defect". On 07/18 technician was Installed the new fan and producing as expected with peer inverters. 2.The site was de-energized on 07/09 at 06:49 for a transformer replacement. After the replacement, the site came back online at 08:15 on 07/16 3. Inverter 1 derated to 20 kW starting at 14:00 on 07/18. A technician found one failed fan, which is currently under RMA. The inverter will continue to derate until the fan is replaced | 1.SR103354 2. SR104105 3. SR104590
MD: Easton - Shortall | MD | SOL-10091 | 188462 | 193997 | -5535 | -2.853% | 158876 | 29586 | 18.62% | 1.Inverter 3 dropped a string from 4/28 2. Inverter A13 is derating from 07/28 at 20.10kW and reporting "fan fault". | 1. SR103711 2. SR105203
MA: Boston - Seaport Solar | MA | SOL-10772 | 85398 | 14366 | 71032 | 494.4% | 86009 | -611 | -0.7104% | 1.Weather station is barely reporting from 12/06 at 08:30. This issue will be troubleshooting next time onsite | 1.SR095305
MA: Dedham - Sprague Street | MA | SOL-10773 | 185825 | 0 | 185825 |  | 193251 | -7426 | -3.843% | 1.The weather station stopped communicating on 05/04. The communication issue will persist until further repairs are completed. | 1.SR1010110
MA: Boston - Summer Street | MA | SOL-10764 | - | 64248 |  |  | 409224
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 38127 | 39200 | -1073 | -2.737% | 38211 | -84 | -0.2198%
MA: Braintree - RCAB | MA | SOL-10838 | 147058 | 182019 | -34961 | -19.21% | 146483 | 575 | 0.3925% | 1. Inverters 4&11 are experiencing heavy shading due to surrounding trees throughout the day from 11/07/2024. | 1.SR093047
NH: Rochester - Portland Street | NH | SOL-10771 | 11536 | 8216 | 3320 | 40.41% | 9369 | 2167 | 23.13%
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 44412 | N/A |  |  | 35518 | 8894 | 25.04% | 1. Inverter 6 is down a string since 07/07 | 1.SR105784
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | - | 0 |  |  | 0
NH: Rochester - Rochester MS | NH | SOL-10765 | 38048 | 40396 | -2348 | -5.812% | 30355 | 7693 | 25.34%
NH Rochester - Spaulding HS | NH | SOL-10767 | 19595 | 16446 | 3149 | 19.15% | 15033 | 4562 | 30.35%
NH: Rochester - McClelland ES | NH | SOL-10766 | 13247 | 13989 | -742 | -5.304% | 9804 | 3443 | 35.12%
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 17978 | 17518 | 460 | 2.626% | 13220 | 4758 | 35.99%
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 714 | 138037 | -137323 | -99.48% | 133750 | -133036 | -99.47% | 1.Site tripped offline at 16:00 on 06/28 and inverters are reporting at constant value through out the month and site came back online on 07/22 2. Inverter 2 failed to start for production from 07/22 after site re-energization. | 1.SR103721 2. SR104748
OH: Cleveland - CV Wooster | OH | SOL-10763 | 21528 | N/A |  |  | 32092 | -10564 | -32.92% | 1. 8 inverters are offline from 09/05/24 according to the SMA Sunny Portal and need to be replaced. Gen Cap will work directly with Rural Solar. | SR092556
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 15714 | 20086 | -4372 | -21.77% | 23213 | -7499 | -32.31% | 1. Inverter 2 was offline for whole month due to fault current. 2. Inverter 3 was offline for whole month due to Interference device fault | 1.SR099268 2.SR093354
PR: Bayamon - Coca Cola | PR | SOL-10073 | 53577 | 82117 | -28540 | -34.76% | 86974 | -33397 | -38.4% | 1. Inverter 11 was offline for whole month. 2. Inverter 14 was offline for whole month. 3. Inverter 15 was offline for whole month. 4. Inverter 16 was offline for whole month. 5. Inverter 25 was offline for whole month. 6. Inverter 26 was offline for whole month. 7.Inverter 17 offline from 07/10 | 1. SR101102 2. SR101744 3. SR100464 4. SR098883 5. SR092332 6. SR095649 7. SR101102
PR: Carolina - St. Francis | PR | SOL-10034 | 18667 | 64279 | -45612 | -70.96% | 44155 | -25488 | -57.72% | 1. Inverter 1 was offline for whole month 2. Inverter 4 was offline for whole month 3. Inverter 7 was offline for whole month 4. Inverter 10 was offline for whole month 5. Inverter 16 was offline for whole month 6. Inverter 17 was offline for whole month 7. Inverter 15 was offline for most of the days in month 8. Inverter 2 was offline from 06/04 through out the month. 9. Inverter 5 was offline from 06/12 through out the month. 10.Site tripped offline at 10:30 from 07/09 and it came back online on 07/11 11.Inverter 6 offline from 07/10" | 1. SR102198 2. SR101942, SR088869 3. SR092209 4. SR101998 5. SR092255 6. SR092751 7. SR092095 8. SR101997 9. SR103021 10. SR104199 11. SR104453
DC: Chevy Chase -Sinai | DC | SOL-10028 | 10029 | 14969 | -4940 | -33% | 12371 | -2342 | -18.93% | 1.Inverter 9 offline from 07/09 | 1. SR104194
DC: Washington - Weinberg 1 | DC | SOL-10039 | 1770 | 1824 | -54 | -2.961% | 1844 | -74 | -4.013%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 1604 | 1600 | 4 | 0.25% | 1861 | -257 | -13.81% | 1.Low production/generation due to low irradiance on 07/10
DC: Washington - Weinberg 3 | DC | SOL-10042 | 1948 | 1836 | 112 | 6.1% | 1942 | 6 | 0.309%

## Aug
GoodFinch |  |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  |  | 1713881.4446 | 1550150.411 | 163731.0336 | 10.56% | 2191029.338 | -477147.8934 | -21.78%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 13453.4608 | 8419.71 | 5033.7508 | 59.79% | 13509.58 | -56.1192 | -0.4154%
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 43846.5 | 55652.46 | -11805.96 | -21.21% | 65198.07 | -21351.57 | -32.75% | 1. Inverter was offline from 06:00 on 08/19 to 10:30 on 08/21. | 1. SR106525
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 19620.9865 | N/A |  |  | 19123 | 497.9865 | 2.604% | 1. Meter 2 was offline from 05:15 on 08/14 to 10:15 on 08/18. | 1. SR106306
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 12185.0834 | 14256.47 | -2071.3866 | -14.53% | 15176.2 | -2991.1166 | -19.71% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 32020.8375 | 32669.12 | -648.2825 | -1.984% | 32554.21 | -533.3725 | -1.638% | 1. Inverter 2 was offline from 06:00 on 08/26 to 13:00 on 08/27. | 1. SR106940
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 29607.6649 | 23582.18 | 6025.4849 | 25.55% | 29931.18 | -323.5151 | -1.081%
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 13603.3017 | 9708.966 | 3894.3357 | 40.11% | 13115 | 488.3017 | 3.723%
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 4902.1035 | N/A |  |  | 9502 | -4599.8965 | -48.41% | 1. Site was offline for half a day from 08/01 to 08/17, and was producing at half of its capacity. It was tripped offline again on 08/20 at 16:00 and brought back online on 08/21 at 06:00. The site was tripped offline again on 08/21 at 13:00 and came back online on 08/22 at 06:00. Production dropped to half of its rating again from 08/25 at 06:00. | 1. SR106366, SR105842, SR105159 | SR105842 | SR105159
AZ: Yuma Airport | AZ | SOL-10754 | 59016 | 88791.13 | -29775.13 | -33.53% | 74541 | -15525 | -20.83% | 1. Inverter 3 was offline for whole month. | 1. SR105838, SR099310 | SR099310
AZ: Globe - Gila CC | AZ | SOL-10751 | 18359.0784 | 7005.122 | 11353.9564 | 162.1% | 18272 | 87.0784 | 0.4766% | 1.Inverters 1 & 2 are operational but not communicating. Further troubleshooting is needed to resolve both the underperformance and communication issues of Inverter 1&2. | 1. SR101037
AZ: Payson - Gila CC | AZ | SOL-10748 | 10693.8869 | 5876.605 | 4817.2819 | 81.97% | 13721 | -3027.1131 | -22.06% | 1. Inverters 2 and 3 were tripping on and off from 08/11 to end of the month. | 1. SR106134
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 29948.01 | N/A |  |  | 50610 | -20661.99 | -40.83% | 1. Meter build 5 & 6 is dropping by 20 kW on most days, possibly two inverters tripping offline.Technician was advised that equipment is beyond legacy date, and repair parts are no longer quotable or available. Complete replacement is only option going forward. | 1. SR103804
AZ: Tempe - SCNM | AZ | SOL-10760 | 66706.5 | 43347.96 | 23358.54 | 53.89% | 83780 | -17073.5 | -20.38% | 1. Inverter 1 was underperforming by 150kW from 07:45 on 04/17 to 15:15 on 08/20. Inverter 2 is derating in the afternoon by 100kW 08/10 to 08/27 | 1. SR105841, SR106733 | SR106733
DE: Newark - Clayton Hall | DE | SOL-10820 | 20330 | 21883.226 | -1553.226 | -7.098% | 18905 | 1425 | 7.538%
DE: Newark - UOD Field House | DE | SOL-10821 | 53343 | N/A |  |  | 48292 | 5051 | 10.46%
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 0 | 33703.362 | -33703.362 | -100% | 36430 | -36430 | -100% | 1. Site was offline for whole month. | 1. SR106006, SR103078 | SR103078
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 178144 | 177085.386 | 1058.614 | 0.5978% | 167217.481 | 10926.519 | 6.534%
MD: Easton - Shortall | MD | SOL-10091 | 183791 | 172267.59 | 11523.41 | 6.689% | 172138.873 | 11652.127 | 6.769% | 1. Inverter 3 was underperforming 5kW down from 04/28 to 08/25. | 1. SR103711
MA: Boston - Seaport Solar | MA | SOL-10772 | 85433 | 16867.238 | 68565.762 | 406.5% | 78282.81 | 7150.19 | 9.134% | 1. Weather station was reporting low values (upto 200w/m2) even on good sunny day for whole month. | 1. SR095305
MA: Dedham - Sprague Street | MA | SOL-10773 | 188559 | 0 | 188559 |  | 171041.622 | 17517.378 | 10.24%
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 75812.516 | -75812.516 | -100% | 366886.89 | -366886.89 | -100% | 1. Site was offline for whole month. | 1. SR105609
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 144747.5 | 179328.21 | -34580.71 | -19.28% | 127995.384 | 16752.116 | 13.09% | 1. Inverter 3 was offline from 11:15 on 08/08 to 07:45 on 08/11. 2. Inverter 2 was offline from 17:15 to 20:15 o 08/12. | 1. SR105910 2. SR106165 | SR106165
MA: Braintree - RCAB | MA | SOL-10838 | 144747.5 | 179332.6 | -34585.1 | -19.29% | 129127.6 | 15619.9 | 12.1% | 1. Weather station was reporting erroneous value (0w/m2) for whole month. | 1. SR106696
NH: Rochester - Portland Street | NH | SOL-10771 | 11197.531 | 8246.57 | 2950.961 | 35.78% | 8679.6 | 2517.931 | 29.01%
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 44509 | 0 | 44509 |  | 31822.459 | 12686.541 | 39.87% | 1. Inverter 6 was underproducing by 5kW compared to peer inverters for whole month. | 1. SR104785
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month. | 1. SR106017
NH: Rochester - Rochester MS | NH | SOL-10765 | 38689.5 | 41629.52 | -2940.02 | -7.062% | 28169.78 | 10519.72 | 37.34% | 1. Inverter 5 was underproducing 5kW for whole month. | 1. SR103898
NH Rochester - Spaulding HS | NH | SOL-10767 | 19684.122 | 16540.346 | 3143.776 | 19.01% | 13854.861 | 5829.261 | 42.07%
NH: Rochester - McClelland ES | NH | SOL-10766 | 13213.872 | 14178.234 | -964.362 | -6.802% | 9061.12 | 4152.752 | 45.83%
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 18102.1307 | 17306.58 | 795.5507 | 4.597% | 12184.97 | 5917.1607 | 48.56%
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 101319.1953 | 138778.2 | -37459.0047 | -26.99% | 128225 | -26905.8047 | -20.98% | 1. Inverter 2 failed to start for production from 07/22 after site re-energization. | 1. SR104748
OH: Cleveland - CV Wooster | OH | SOL-10763 | 21737.5 |  |  |  | 30332 | -8594.5 | -28.33% | 1. 8 inverters are offline from 09/05/24 according to the SMA Sunny Portal and need to be replaced. Gen Cap will work directly with Rural Solar. | 1. SR092556
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 12965 | 17397.658 | -4432.658 | -25.48% | 22936.726 | -9971.726 | -43.47% | 1. Inverter 1 was intermittently derating by 5kW for whole month 2. Inverter 5 was underproducing by 5kW for whole month. 3. Inverter 2 was offline for whole month. 4. Inverter 3 was offline for whole month. | 1. SR106775 2. SR106303 3. SR099268 4. SR093354 | SR106303 | SR099268 | SR093354
PR: Bayamon - Coca Cola | PR | SOL-10073 | 47380 | 79425.636 | -32045.636 | -40.35% | 90261.694 | -42881.694 | -47.51% | 1. Inverter 11 was offline for whole month. 2. Inverter 14 was offline for whole month. 3. Inverter 17 was offline for whole month. 4. Inverter 15 was offline for whole month. 5. Inverter 16 was offline for whole month. 6. Inverter 26 was offline for whole month. 7. Inverter 25 was offline for whole month. 8. Inverters 1 and 13 are underperforming by about 18 kW each for whole month and Inverter 19 was derated by 5 kW intermittently for whole month | 1. SR101102 2. SR101744 3. SR104348 4. SR100464 5. SR098883 6. SR095649 7. SR092332 8. SR098311 9. | SR101744 | SR104348 | SR100464 | SR098883 | SR095649 | SR092332 | SR098311
PR: Carolina - St. Francis | PR | SOL-10034 | 17876.75 | 52391.865 | -34515.115 | -65.88% | 43455.598 | -25578.848 | -58.86% | 1. Inverter 16 was offline for whole month. 2. Inverter 7 was offline for whole month. 3. Inverter 15 was offline for whole month. 4. Inverter 5 was offline for whole month. 5. Inverter 1 was offline for whole month. 6. Inverter 2 was offline for whole month. 7. Inverter 10 was offline for whole month. 8. Inverter 17 was offline for whole month. 9. Weather station was not communicated from 19:00 on 08/21 to 15:00 on 08/23. | 1. SR092255 2. SR092209 3. SR092095 4. SR103021 5. SR102198 6. SR101997 7. SR101998 8. SR092751 9. SR106747 | SR092209 | SR092095 | SR103021 | SR102198 | SR101997 | SR101998 | SR092751 | SR106747
DC: Chevy Chase -Sinai | DC | SOL-10028 | 9264.43 | 13922.36 | -4657.93 | -33.46% | 11511.16 | -2246.73 | -19.52% | 1. Inverter 9 was offline from 06:00 on 07/09 to 10:15 on 08/27. | 1. SR104194
DC: Washington - Weinberg 1 | DC | SOL-10039 | 1604 | 1618.032 | -14.032 | -0.8672% | 1700.016 | -96.016 | -5.648%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 1482 | 1436.4 | 45.6 | 3.175% | 1703.97 | -221.97 | -13.03% | 1.Low production on 08/01 and 08/18 to 08/21 due to rain
DC: Washington - Weinberg 3 | DC | SOL-10042 | 1798 | 1689.159 | 108.841 | 6.444% | 1779.484 | 18.516 | 1.041%

## Sep
GoodFinch |  |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  |  | 1327999.1275 | 1142953.539 | 185045.5885 | 16.19% | 1649166.344 | -321167.2165 | -19.47%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 11511.7513 | 7558.449 | 3953.3023 | 52.3% | 12700.58 | -1188.8287 | -9.36%
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 37451.5 | 46549.2 | -9097.7 | -19.54% | 55270.38 | -17818.88 | -32.24% | 1. The weather station has been reporting erroneous values during evening hours, showing readings around 600–800 W/m², while nearby sites are reporting approximately 300 W/m².
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 17412.3929 | N/A |  |  | 18638.74 | -1226.3471 | -6.58% | 1. Meter 1 was offline from 09/26 at 14:45 and being LOTO | 1.SR108802
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 10873.1859 | 12767.09 | -1893.9041 | -14.83% | 9956.74 | 916.4459 | 9.204% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 21826.7125 | 25979.11 | -4152.3975 | -15.98% | 30239.99 | -8413.2775 | -27.82% | 1. Inverter 2 is back online at 17:00 on 09/11 2. Inverter 1 tripped offline at 15:00 on 09/09 and back online at 17:00 on 09/11 | 1.SR106940 2.SR107729 | SR107729
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 25376.0012 | 19006.92 | 6369.0812 | 33.51% | 31693.13 | -6317.1288 | -19.93%
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 11884.7079 | 7825.298 | 4059.4099 | 51.88% | 14512.52 | -2627.8121 | -18.11%
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 6874.2061 | N/A |  |  | 8508.578 | -1634.3719 | -19.21% | 1. One of the inverter is offline 2. The site has dropped production to 7 kW on 08/29. Based on historical data, this appears to be a recurring issue. The site’s capacity is 116 kW, but it is currently only producing 40 kW it's possible that a few inverters are offline. on 09/02 technicin was After increasing inverter voltage thresholds, 2 of 2 inverters were online but 1 tripped off. thermals taken of transformer. | 1.SR107222
AZ: Yuma Airport | AZ | SOL-10754 | 56130 | 83104.55 | -26974.55 | -32.46% | 67383 | -11253 | -16.7% | 1. Inverter 3 was offline for whole month. 2.Inverters 1 & 2 are operational but not communicating. Further troubleshooting is needed to resolve both the underperformance and communication issues of Inverter 1&2. | 1.SR099310 2.SR101037 | SR101037
AZ: Globe - Gila CC | AZ | SOL-10751 | 15774.998 | 7644.961 | 8130.037 | 106.3% | 14585.5 | 1189.498 | 8.155% | 1.Inverters 1 & 2 are operational but not communicating. Further troubleshooting is needed to resolve both the underperformance and communication issues of Inverter 1&2. | 1.SR101037
AZ: Payson - Gila CC | AZ | SOL-10748 | 11346.1919 | 4899.061 | 6447.1309 | 131.6% | 8954 | 2392.1919 | 26.72% | 1. Inverters 2 and 3 were tripping on and off from 08/11 to end of the month. | 1.SR106134
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 23986.69 | N/A |  |  | 36700.41 | -12713.72 | -34.64% | 1.Meter 8 & 9 tripped offline around 12:45 on 09/04. They were originally heavily derated 2. Meter building 5 & 6 intermittently underperforming by 20kW historically. meter building 8 & 9 underperforming by 70kW historically. These inverters may need repowers | 1.SR107481 2.SR107139, SR108009 | SR107139 | SR108009
AZ: Tempe - SCNM | AZ | SOL-10760 | 75053.5 | 35345.79 | 39707.71 | 112.3% | 76055.95 | -1002.45 | -1.318% | 1. Inverter 1 was underperforming by 150kW from 07:45 on 04/17 to 15:15 on 08/20. Inverter 2 is derating in the afternoon by 100kW 08/10 to 08/27 | 1.SR105841,SR106733 | SR106733
DE: Newark - Clayton Hall | DE | SOL-10820 | 16183 | 17098.796 | -915.796 | -5.356% | 15004.888 | 1178.112 | 7.852%
DE: Newark - UOD Field House | DE | SOL-10821 | 46205 | N/A |  |  | 36615.393 | 9589.607 | 26.19%
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 14362 | 26808.934 | -12446.934 | -46.43% | 28156.337 | -13794.337 | -48.99% | 1. Site is back online at 11:00 on 09/12 2.CB 5 string 12 and 15 left isolated from 09/08. | 1.SR106006 2.SR107629 | SR107629
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 137574 | 137810.1 | -236.1 | -0.1713% | 126103.8 | 11470.2 | 9.096% | 1. Inverter is offline foe whole day on 09/17. | 1.SR108036
MD: Easton - Shortall | MD | SOL-10091 | 140979 | 125441.4 | 15537.6 | 12.39% | 138939.9 | 2039.1 | 1.468%
MA: Boston - Seaport Solar | MA | SOL-10772 | 63205.5 | 12445.11 | 50760.39 | 407.9% | 52795.64 | 10409.86 | 19.72% | 1. Weather station was reporting low values (upto 200w/m2) even on good sunny day for whole month. | 1.SR095305
MA: Dedham - Sprague Street | MA | SOL-10773 | 129530 | 0 | 129530 |  | 119790.9 | 9739.1 | 8.13% | 1. Site tripped offline at 10:15 on 09/08 and back online at 11:15 on 09/09 2. Site tripped offline at 20:00 on 09/19 and back online at 18:45 on 09/20 | 1.SR107632 2.SR108300 | SR108300
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 55274.92 | -55274.92 | -100% | 257642.4 | -257642.4 | -100% | 1. Site was offline for whole month. | 1.SR105609
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 30451.875 | 30797.03 | -345.155 | -1.121% | 22701.17 | 7750.705 | 34.14% | 1. Inverter 2 is offline on 09/07 and back online at 08:30 on 09/08 | 1.SR106165
MA: Braintree - RCAB | MA | SOL-10838 | 103921 | 107148.6 | -3227.6 | -3.012% | 98355.45 | 5565.55 | 5.659% | 1. Weather station was reporting erroneous value (0w/m2) for whole month. | 1.SR106696
NH: Rochester - Portland Street | NH | SOL-10771 | 8387.221 | 6672.632 | 1714.589 | 25.7% | 8430.646 | -43.425 | -0.5151%
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 35293.625 | 12514.94 | 22778.685 | 182% | 31092.14 | 4201.485 | 13.51% | 1. Inverter 6 is producing with its peers from 09/02. 2.Weather station started communication on 09/18 at 12:30 | 1.SR104785 2.SR095643 | SR095643
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 13129 | 14176.25 | -1047.25 | -7.387% | 30672 | -17543 | -57.2% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
NH: Rochester - Rochester MS | NH | SOL-10765 | 31604.6214 | 34632.64 | -3028.0186 | -8.743% | 27291.83 | 4312.7914 | 15.8% | 1. Inverter 5 is producing with its peers from 09/06 | 1.SR103898
NH Rochester - Spaulding HS | NH | SOL-10767 | 15442.0642 | 13033.06 | 2409.0042 | 18.48% | 14117.84 | 1324.2242 | 9.38%
NH: Rochester - McClelland ES | NH | SOL-10766 | 10491.5026 | 11440.56 | -949.0574 | -8.296% | 9727.506 | 763.9966 | 7.854%
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 13896.9405 | 13459.94 | 437.0005 | 3.247% | 11036.59 | 2860.3505 | 25.92% | 1. Inverter 3 is offline on 09/09 and back online at 09/10 | 1.SR107718
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 96137 | 132624.7 | -36487.7 | -27.51% | 100898 | -4761 | -4.719% | 1.45 modules shattered on site 2. Inverter 2 is offline for the whole month | 1.SR091707 2.SR092555 | SR092555
OH: Cleveland - CV Wooster | OH | SOL-10763 | 19607.5 |  |  |  | 19890.56 | -283.06 | -1.423% | 1. 8 inverters are offline from 09/05/24 according to the SMA Sunny Portal and need to be replaced. Gen Cap will work directly with Rural Solar. | 1.SR092556
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 11068 | 14949.63 | -3881.63 | -25.96% | 17284.26 | -6216.26 | -35.96% | 1. Inverter 1 was intermittently derating by 5kW for whole month 2. Inverter 5 was underproducing by 5kW for whole month. 3. Inverter 2 was offline for whole month. 4. Inverter 3 was offline for whole month. | 1. SR106775 2. SR106303 3. SR099268 4. SR093354 | SR106303 | SR099268 | SR093354
PR: Bayamon - Coca Cola | PR | SOL-10073 | 38828 | 69015.17 | -30187.17 | -43.74% | 62247.07 | -23419.07 | -37.62% | 1. Inverter 11 was offline for whole month. 2. Inverter 14 was offline for whole month. 3. Inverter 17 was offline for whole month. 4. Inverter 15 was offline for whole month. 5. Inverter 16 was offline for whole month. 6. Inverter 26 was offline for whole month. 7. Inverter 25 was offline for whole month. 8. Inverters 1 and 13 are underperforming by about 18 kW each for whole month and Inverter 19 was derated by 5 kW intermittently for whole month 9. Site was taken offline due to fire at 11:00 on 09/25 | 1. SR101102 2. SR101744 3. SR104348 4. SR100464 5. SR098883 6. SR095649 7. SR092332 8. SR098311 9.SR108548 | SR101744 | SR104348 | SR100464 | SR098883 | SR095649 | SR092332 | SR098311 | SR108548
PR: Carolina - St. Francis | PR | SOL-10034 | 14985.75 | 42011.24 | -27025.49 | -64.33% | 22921.43 | -7935.68 | -34.62% | 1. Inverter 16 was offline for whole month. 2. Inverter 7 was offline for whole month. 3. Inverter 15 was offline for whole month. 4. Inverter 5 was offline for whole month. 5. Inverter 1 was offline for whole month. 6. Inverter 2 was offline for whole month. 7. Inverter 10 was offline for whole month. 8. Inverter 17 was offline for whole month. 9. Weather station was not communicated from 05:00 on 09/18 to 18:00 on 09/19. | 1. SR092255 2. SR092209 3. SR092095 4. SR103021 5. SR102198 6. SR101997 7. SR101998 8. SR092751 9. SR108270 | SR092209 | SR092095 | SR103021 | SR102198 | SR101997 | SR101998 | SR092751 | SR108270
DC: Chevy Chase -Sinai | DC | SOL-10028 | 7222.69 | 11076.59 | -3853.9 | -34.79% | 8177.683 | -954.993 | -11.68% | 1.inverter 09 tripped offline at 06:00am on 09/03 | 1.SR107355
DC: Washington - Weinberg 1 | DC | SOL-10039 | 1291 | 1282.639 | 8.361 | 0.6519% | 1326.569 | -35.569 | -2.681%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 1238 | 1191.34 | 46.66 | 3.917% | 1251.818 | -13.818 | -1.104%
DC: Washington - Weinberg 3 | DC | SOL-10042 | 1463 | 1366.889 | 96.111 | 7.031% | 1495.006 | -32.006 | -2.141%

## Oct
GoodFinch |  |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  |  | 1235037.3648 | 1040145.804 | 194891.5608 | 18.74% | 1469875.886 | -234838.5212 | -15.98%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 11060.8396 | 7598.541 | 3462.2986 | 45.57% | 12242.05 | -1181.2104 | -9.649%
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 32651.75 | 42655.48 | -10003.73 | -23.45% | 44927.36 | -12275.61 | -27.32% | 1. Inverter has heavy evening shading for whole month.
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 10572.0841 | N/A |  |  | 17925.71 | -7353.6259 | -41.02% | 1. Meter 1 was offline for whole month. | 1. SR108802 | 1. Pending
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 10860.2126 | 12802.69 | -1942.4774 | -15.17% | 8347.666 | 2512.5466 | 30.1% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 25855.825 | 22031.49 | 3824.335 | 17.36% | 25352.84 | 502.985 | 1.984% | 1. Inverter 2 was offline from 10/01 to 15:00 on 10/02. | 1. SR106940 | 1. Closed
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 24849.1621 | 16524.94 | 8324.2221 | 50.37% | 32826.78 | -7977.6179 | -24.3%
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 11436.3902 | 6803.443 | 4632.9472 | 68.1% | 13903.81 | -2467.4198 | -17.75%
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 6981.8939 | N/A |  |  | 6908.07 | 73.8239 | 1.069% | 1. Production at meter frequently dropped to 20kW for whole month. | 1. SR109065 | 1. Closed
AZ: Yuma Airport | AZ | SOL-10754 | 65053 | 87950.03 | -22897.03 | -26.03% | 63291 | 1762 | 2.784% | 1. Inverter 3 was offline from 10/01 to 10/16. | 1. SR108280 | 1. Closed
AZ: Globe - Gila CC | AZ | SOL-10751 | 15272.354 | 8479.68 | 6792.674 | 80.11% | 14577 | 695.354 | 4.77% | 1. Production meter is underperforming by 20kW intermittently. Possible indication 1 of 4 inverters intermittently offline. | 1.SR110537 | 1.Pending
AZ: Payson - Gila CC | AZ | SOL-10748 | 11317.2816 | 4458.1 | 6859.1816 | 153.9% | 8601 | 2716.2816 | 31.58% | 1. Inverters 2 and 3 were tripping on and off from 08/11 to end of the month. | 1. SR106134 | 1.Closed
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 20010.06 | N/A |  |  | 30334.14 | -10324.08 | -34.03% | 1. Building 8 & 9 are offline mostly for whole month. 2. Meter building 5 & 6 intermittently underperforming by 20kW historically. meter building 8 & 9 underperforming by 70kW historically. These inverters may need repowers | 1. SR108009, SR108679 2. SR108009 | 1. Pending, Closed 2.Pending | SR108679 | SR108009
AZ: Tempe - SCNM | AZ | SOL-10760 | 68084.38 | 31435.85 | 36648.53 | 116.6% | 63211.73 | 4872.65 | 7.708% | 1. Inverter 2 was offline from 10:30 to 15:15 on 10/21. | 1. SR106733 | 1. Closed
DE: Newark - Clayton Hall | DE | SOL-10820 | 14256 | 14610.278 | -354.278 | -2.425% | 14535.864 | -279.864 | -1.925%
DE: Newark - UOD Field House | DE | SOL-10821 | 43708 | N/A |  |  | 35490.78 | 8217.22 | 23.15%
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 20490 | 22998.967 | -2508.967 | -10.91% | 27256.043 | -6766.043 | -24.82% | 1. Inverter 1 tripped offline at 09:00 to 11:15 on 10/16.
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 151327 | 154968.6 | -3641.6 | -2.35% | 119840.2 | 31486.8 | 26.27% | 1. Inverter 17 derated to 4kW from 09:00 to 19:00 on 10/06 and was offline from 06:00 to 18:00 on 10/07. | 1. SR109129 | 1. Pending
MD: Easton - Shortall | MD | SOL-10091 | 160866 | 107393.8 | 53472.2 | 49.79% | 132045.4 | 28820.6 | 21.83%
MA: Boston - Seaport Solar | MA | SOL-10772 | 44746 | 8277.318 | 36468.682 | 440.6% | 90296.07 | -45550.07 | -50.45% | 1. Weather station was reporting low values (upto 200w/m2) even on good sunny day for whole month. | 1.SR095305
MA: Dedham - Sprague Street | MA | SOL-10773 | 102240 | 0 | 102240 |  | 109896.5 | -7656.5 | -6.967%
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 35721.51 | -35721.51 | -100% | 196945.8 | -196945.8 | -100% | 1. Site was offline for whole month. | 1. SR105609 | 1. Pending
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 23125.625 | 24471.27 | -1345.645 | -5.499% | 16391.47 | 6734.155 | 41.08%
MA: Braintree - RCAB | MA | SOL-10838 | 71319 | 73301.71 | -1982.71 | -2.705% | 70778.33 | 540.67 | 0.7639% | 1. Inverter 4, 11, 12 had heavy evening shading.
NH: Rochester - Portland Street | NH | SOL-10771 | 5991.685 | 5247.822 | 743.863 | 14.17% | 8872.158 | -2880.473 | -32.47% | 1.Inverter expericing shading issue
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 25458.875 | 24485.56 | 973.315 | 3.975% | 27755.82 | -2296.945 | -8.276%
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 26595.5 | 29301.37 | -2705.87 | -9.235% | 26306.26 | 289.24 | 1.1%
NH: Rochester - Rochester MS | NH | SOL-10765 | 24189.6286 | 28461.55 | -4271.9214 | -15.01% | 23962.06 | 227.5685 | 0.9497% | 1. Inverter 3 was offline from 12:00 to 18:00 on 10/16. | 1. SR109608 | 1. Closed
NH Rochester - Spaulding HS | NH | SOL-10767 | 11409.2539 | 10062.44 | 1346.8139 | 13.38% | 11880.41 | -471.1561 | -3.966%
NH: Rochester - McClelland ES | NH | SOL-10766 | 7978.4375 | 8740.015 | -761.5775 | -8.714% | 8220.146 | -241.7085 | -2.94%
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 9825.4393 | 9861.6 | -36.1607 | -0.3667% | 8208.713 | 1616.7263 | 19.7%
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 77686.9375 | 108516.4 | -30829.4625 | -28.41% | 78248 | -561.0625 | -0.717% | 1. Inverter 2 was offline for whole month. | 1. SR092555 | 1. Pending
OH: Cleveland - CV Wooster | OH | SOL-10763 | 16704.25 | N/A |  |  | 15652.25 | 1052 | 6.721%
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 11837 | 14656.49 | -2819.49 | -19.24% | 15917.25 | -4080.25 | -25.63% | 1. Inverter 3 was offline for whole month. | 1. SR106775
PR: Bayamon - Coca Cola | PR | SOL-10073 | 47700 | 67075.12 | -19375.12 | -28.89% | 57323.83 | -9623.83 | -16.79% | 1. Inverter 15 and 22 were offline for whole month and inverter 13 was underproducing by 18kW. inverters 16, 17 were underproducing due to a few strings down, and inverter 19 was overheating | 1. SR108732 | 1. Pending
PR: Carolina - St. Francis | PR | SOL-10034 | 12924.25 | 36924.46 | -24000.21 | -65% | 20197.19 | -7272.94 | -36.01% | 1. Inverter 16 was offline for whole month. 2. Inverter 7 was offline for whole month. 3. Inverter 15 was offline for whole month. 4. Inverter 5 was offline for whole month. 5. Inverter 1 was offline for whole month. 6. Inverter 2 was offline for whole month. 7. Inverter 10 was offline for whole month. 8. Inverter 17 was offline for whole month. 9. Site was offline from 01:00 to 17:00 on 10/26. | 1. SR092255 2. SR092209 3. SR092095 4. SR103021 5. SR102198 6. SR101997 7. SR101998 8. SR092751 9. SR109991 | 1. Pending 2. Pending 3. Pending 4. Pending 5. Pending 6. Pending 7. Pending 8. Pending 9. Closed | SR092209 | SR092095 | SR103021 | SR102198 | SR101997 | SR101998 | SR092751 | SR109991
DC: Chevy Chase -Sinai | DC | SOL-10028 | 6838.25 | 10596.94 | -3758.69 | -35.47% | 7530.733 | -692.483 | -9.195% | 1. Inverter 4,5 9,11, 10 are experiencing shading issues. 2.Inverters tripping on and off online due to technician was on site to replace inverter 9 and reinstalled a dislodged module | 1.PM9922 | 1.Completed
DC: Washington - Weinberg 1 | DC | SOL-10039 | 1196 | 1184.675 | 11.325 | 0.956% | 1262.262 | -66.262 | -5.249%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 1217 | 1215.376 | 1.624 | 0.1336% | 1190.531 | 26.469 | 2.223%
DC: Washington - Weinberg 3 | DC | SOL-10042 | 1402 | 1332.289 | 69.711 | 5.232% | 1422.66 | -20.66 | -1.452%

## Nov
GoodFinch |  |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  |  | 868782.3406 | 871540.417 | -2758.0764 | -0.3165% | 1158193.1221 | -289410.7815 | -24.99%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 8591.5743 | 6519.536 | 2072.0383 | 31.78% | 10726.16 | -2134.5857 | -19.9% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 23597.5 | 32228.03 | -8630.53 | -26.78% | 35197.85 | -11600.35 | -32.96% | 1. Inverter has heavy evening shading for whole month.
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 9046.6012 |  |  |  | 15934.38 | -6887.7788 | -43.23% | 1.Meter 1 was offline whole month | 1. SR108802 | 1.Pending
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 7269.0478 | 10958.56 | -3689.5122 | -33.67% | 7926.86 | -657.8122 | -8.299% | 1.Inverter 1 offline from 13:45 on 11/21 | 1.SR111477 | 1.Pending
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 22856.35 | 16205.65 | 6650.7 | 41.04% | 24075.35 | -1219 | -5.063%
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 19296.7486 | 12452.7 | 6844.0486 | 54.96% | 31553.09 | -12256.3414 | -38.84% | 1. Inverter 2 has shading in the afternoon
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 5083.3918 | 5126.871 | -43.4792 | -0.8481% | 13886.94 | -8803.5482 | -63.39% | 1.Inverter 2 tripped offline at 08:15 on 11/05 and it came back online at 12:30 on 11/07 2.Inverter 2 was offline on 11/10 | 1. SR110730 2. SR110939 | 1.Closed 2.Pending | SR110939
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 4951.3925 | 5400.422 | -449.0295 | -8.315% | 5423 | -471.6075 | -8.696%
AZ: Yuma Airport | AZ | SOL-10754 | 54060 | 72251.47 | -18191.47 | -25.18% | 57082 | -3022 | -5.294% | 1. Inverter 3 stopped communicating on 11/19 but production was captured on 11/20. From 11/23, meter capturing the production of inverter 1 and 2 only and inverter 3 production cannot be confirmed as per the difference between meter and inverter 2 production. Currently inverter 3 is offline. | 1.SR111411 | 1. Pending
AZ: Globe - Gila CC | AZ | SOL-10751 | 10993.1064 | 8108.72 | 2884.3864 | 35.57% | 11611 | -617.8936 | -5.322% | 1. production meter is underperforming by 20kW intermittently: 11/01 Possible indication 1 of 4 inverters intermittently offline. Issue resolved on 11/24 | 1. SR110537 ,SR111101 | 1.Closed , Completed | SR111101
AZ: Payson - Gila CC | AZ | SOL-10748 | 8029.4033 | 3495.601 | 4533.8023 | 129.7% | 6575 | 1454.4033 | 22.12% | 1. Inverters 2 and 3 were tripping on and off from 08/11 to end of the month. | 1. SR106134 | 1.Closed
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 13603.5 | 26614.73 | -13011.23 | -48.89% | 26726 | -13122.5 | -49.1% | 1. Building 8 & 9 are offline mostly for whole month. 2. Meter building 5 & 6 intermittently underperforming by 20kW historically. meter building 8 & 9 underperforming by 70kW historically. These inverters may need repowers | 1. SR108009, SR108679 2. SR108009 | 1.pending , closed 2.Pending | SR108679 | SR108009
AZ: Tempe - SCNM | AZ | SOL-10760 | 51124.88 | 24194.14 | 26930.74 | 111.3% | 53172.7 | -2047.82 | -3.851%
DE: Newark - Clayton Hall | DE | SOL-10820 | 8991 | 9308.1 | -317.1 | -3.407% | 13027 | -4036 | -30.98% | 1. Inverter has a minor evening shading 2. Site has low production from 11/20 to 11/22 due to bad weather.
DE: Newark - UOD Field House | DE | SOL-10821 | 30439 | 31622.79 | -1183.79 | -3.743% | 31755 | -1316 | -4.144%
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 12930 | 14955.3 | -2025.3 | -13.54% | 17920.5 | -4990.5 | -27.85% | 1. Inverter has shading in the morning 2. Site has low production from 11/20 to 11/22 and from 11/25 to 11/27 due to bad weather.
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 115185 | 123024.9 | -7839.9 | -6.373% | 134715.8 | -19530.8 | -14.5% | 1. Inverter 17 derated to 4kW from 09:00 to 19:00 on 10/06 and was offline on 11/06 at 09:30 and it came back online on 11/19 | 1. SR109129 | 1.Closed
MD: Easton - Shortall | MD | SOL-10091 | 124330 | 77789.46 | 46540.54 | 59.83% | 148255.2 | -23925.2 | -16.14%
MA: Boston - Seaport Solar | MA | SOL-10772 | 26894 | 16437.11 | 10456.89 | 63.62% | 30863.97 | -3969.97 | -12.86% | 1.Site was offline on 11/04 at 09:45 and it came back online at 14:00 on 11/05 | 1. SR110622 | 1.Closed
MA: Dedham - Sprague Street | MA | SOL-10773 | 66809 | 0 | 66809 |  | 73074.5 | -6265.5 | -8.574%
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 83111.3 | -83111.3 | -100% | 143741.1 | -143741.1 | -100% | 1. Site was offline for whole month. | 1.SR105609 | 1.Closed
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 13634.75 | 15595.22 | -1960.47 | -12.57% | 10815 | 2819.75 | 26.07% | 1.Site was offline on 11/21 and it came back online on 11/24 | 1.SR111484 | 1.Closed
MA: Braintree - RCAB | MA | SOL-10838 | 45840 | 47044.98 | -1204.98 | -2.561% | 45985.75 | -145.75 | -0.3169% | 1.Site was offline on 11/23 at 18:30 and it came back online at 10:30 on 11/24 | 1.SR111508 | 1.closed
NH: Rochester - Portland Street | NH | SOL-10771 | 3330.8 | 3147.3 | 183.5 | 5.83% | 8339 | -5008.2 | -60.06% | 1. Site production was low from 11/09 to 11/11 and on 11/30 due to snow.
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 15465.625 | 13547.88 | 1917.745 | 14.16% | 18098.34 | -2632.715 | -14.55% | 1. Inverter 3 has heavy shading in the morning and afternoon and inverter 4 has minor shading in the afternoon and all other inverters are experiencing a heavy shading in the evening.
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 14826.5 | 17054.69 | -2228.19 | -13.06% | 17072.62 | -2246.12 | -13.16% | 1. Inveters 5 and 7 have heavy shading in the morning. 2. Inverter 3 has heavy shading in afternoon and evening. 3. All inverters have a minor shading in the morning.
NH: Rochester - Rochester MS | NH | SOL-10765 | 14042.1287 | 17884.54 | -3842.4113 | -21.48% | 15263.19 | -1221.0613 | -8% | 1. All inverters have heavy shading in the morning and inverter 3 has shading in the afternoon.
NH Rochester - Spaulding HS | NH | SOL-10767 | 6106.5636 | 5593.597 | 512.9666 | 9.171% | 7071.437 | -964.8734 | -13.64% | 1. Inverters have shading in the morning and inverter 1 has heavy shading in morning and during the peak hours.
NH: Rochester - McClelland ES | NH | SOL-10766 | 4380.2533 | 5202.471 | -822.2177 | -15.8% | 5218.185 | -837.9317 | -16.06% | 1.Inverter 2 tripped offline at 10:30 on 11/15 and it came back online at 12:15 on 11/19 | 1. SR111281 | 1.Closed
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 4911.5 | 5142.9 | -231.4 | -4.499% | 4755 | 156.5 | 3.291%
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 30035.5625 | 47622.23 | -17586.6675 | -36.93% | 55597 | -25561.4375 | -45.98% | 1. Inverter 2 was offline for whole month. | 1.SR092555 | 1.pending
OH: Cleveland - CV Wooster | OH | SOL-10763 | 9044.5 | N/A |  |  | 10570.81 | -1526.31 | -14.44% | 1. 8 inverters are offline from 09/05/24 according to the SMA Sunny Portal and need to be replaced. Gen Cap will work directly with Rural Solar. | 1. SR092556 | 1.pending
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 12217.7215 | 14227.94 | -2010.2185 | -14.13% | 9317.049 | 2900.6725 | 31.13% | 1. Inverter 3 was offline for whole month. 2. Inverter 2 & 3 are offline, reporting "Interference device." | 1.SR106775 2. SR111264 | 1.Closed 2.pending | SR111264
PR: Bayamon - Coca Cola | PR | SOL-10073 | 48838 | 61017.9 | -12179.9 | -19.96% | 33386.42 | 15451.58 | 46.28% | 1. Inverter 15 and 22 were offline for whole month and inverter 13 was underproducing by 18kW. inverters 16, 17 were underproducing due to a few strings down, and inverter 19 was overheating 2. Inverter 11 was offline on 11/17, reporting "Interference device." | 1. SR108732 2. SR111265 | 1.Closed 2.Pending | SR111265
PR: Carolina - St. Francis | PR | SOL-10034 | 14795.75 | 28958.93 | -14163.18 | -48.91% | 16734.04 | -1938.29 | -11.58% | 1. Inverter 16 was offline for whole month. 2. Inverter 7 was offline for whole month. 3. Inverter 15 was offline for whole month. 4. Inverter 5 was offline for whole month. 5. Inverter 1 was offline for whole month. 6. Inverter 2 was offline for whole month. 7. Inverter 10 was offline for whole month. 8. Inverter 17 was offline for whole month. | 1. SR092255 2. SR092209 3. SR092095 4. SR103021 5. SR102198 6. SR101997 7. SR101998 8. SR092751 | 1. Pending 2. Pending 3. Pending 4. Pending 5. Pending 6. Pending 7. Pending 8. Pending | SR092209 | SR092095 | SR103021 | SR102198 | SR101997 | SR101998 | SR092751
DC: Chevy Chase -Sinai | DC | SOL-10028 | 4720.19 | 7172.047 | -2451.857 | -34.19% | 4408.569 | 311.621 | 7.069% | 1. There are two trees that seem to shade one array for whole month. | 1. SR110504 | 1. Pending
DC: Washington - Weinberg 1 | DC | SOL-10039 | 771 | 758.5012 | 12.4988 | 1.648% | 754.8442 | 16.1558 | 2.14%
DC: Washington - Weinberg 2 | DC | SOL-10045 | 812 | 864.8707 | -52.8707 | -6.113% | 712.0233 | 99.9767 | 14.04% | 1. Site is producing as expected
DC: Washington - Weinberg 3 | DC | SOL-10042 | 928 | 899.0301 | 28.9699 | 3.222% | 850.4446 | 77.5554 | 9.119%

## Dec
GoodFinch |  |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  |  | 634165.6296 | 702723.4632 | -68557.8336 | -9.756% | 877249.0909 | -243083.4613 | -27.71%
Site | State | SOL# | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | status
AZ: Tempe - ASU - Farmer | AZ | SOL-10748 | 8315.9326 | 6688.67 | 1627.2626 | 24.33% | 9815.903 | -1499.9704 | -15.28% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: Tempe - ASU - Fulton | AZ | SOL-10749 | 21590.25 | 30584.21 | -8993.96 | -29.41% | 28511.02 | -6920.77 | -24.27% | 1. Inverter has heavy evening shading for whole month.
AZ: Superior - JFK Elementary | AZ | SOL-10758 | 11545.6917 | N/A |  |  | 14935.38 | -3389.6883 | -22.7% | 1.Meter 1 was back online on 12/18 | 1.SR108802 | 1.Closed
AZ: Tempe - ASU - Noble | AZ | SOL-10750 | 8597.1304 | 11225.96 | -2628.8296 | -23.42% | 7255.666 | 1341.4644 | 18.49% | 1. Although the expected values and last year’s expected data were high, the site is producing as expected.
AZ: Tempe - ASU - Parking #3 | AZ | SOL-10751 | 22568 | 14999.69 | 7568.31 | 50.46% | 22035.76 | 532.24 | 2.415% | 1. Inverter 2 has shading in the afternoon
AZ: Tempe - ASU - PE East | AZ | SOL-10752 | 18980.6391 | 11728.31 | 7252.3291 | 61.84% | 31439.56 | -12458.9209 | -39.63% | 1. Inverter 2 has shading in the afternoon
AZ: Tempe - ASU - Schwada | AZ | SOL-10753 | 7294.9827 | 4828.636 | 2466.3467 | 51.08% | 13108.78 | -5813.7973 | -44.35% | 1.Inverter 2 was back online on 12/08 at 12:15 | 1. SR110939 | 1.Closed
AZ: Phoenix - Starshine Academy | AZ | SOL-10757 | 4521.2974 | N/A |  |  | 4553.082 | -31.7846 | -0.6981%
AZ: Yuma Airport | AZ | SOL-10754 | 47340 | 72208.52 | -24868.52 | -34.44% | 53603 | -6263 | -11.68% | 1. Inverter 3 was offline from 11/23 to 12:15 on 12/19. | 1. SR111411 | 1. Closed
AZ: Globe - Gila CC | AZ | SOL-10751 | 11391.376 | 8177.907 | 3213.469 | 39.29% | 10538.548 | 852.828 | 8.092%
AZ: Payson - Gila CC | AZ | SOL-10748 | 7708.9876 | 3375.915 | 4333.0726 | 128.4% | 5486 | 2222.9876 | 40.52% | 1. The Expected value at the site was taken from a virtual weather station.
AZ: Mesa - Sequoia Charter School | AZ | SOL-10759 | 12197.24 | N/A |  |  | 24411.85 | -12214.61 | -50.04% | 1. Building 8 & 9 are offline mostly for whole month. 2. Meter building 5 & 6 intermittently underperforming by 20kW historically. meter building 8 & 9 underperforming by 70kW historically. These inverters may need repowers | 1. SR108009, SR108679 2. SR108009 | 1.pending , closed 2.Pending | SR108009
AZ: Tempe - SCNM | AZ | SOL-10760 | 49992.12 | 23114.76 | 26877.36 | 116.3% | 50021.19 | -29.07 | -0.05812% | 1. The Expected value at the site was taken from a virtual weather station.
DE: Newark - Clayton Hall | DE | SOL-10820 | 6138 | 7211.615 | -1073.615 | -14.89% | 11773.748 | -5635.748 | -47.87% | 1. Inverter has a minor evening shading
DE: Newark - UOD Field House | DE | SOL-10821 | 24415 | N/A |  |  | 27862.99 | -3447.99 | -12.37% | 1. Site production was low on 12/21, 12/23, 12/28, 12/29 due to snow.
DE: Newark - UOD 461 Wyoming | DE | SOL-10819 | 3780 | 11471.227 | -7691.227 | -67.05% | 22087.085 | -18307.085 | -82.89% | 1.Inverter was offline on 12/03 and it came back online on 12/22 | 1.SR112055 | 1.Completed
MD: Presston - Bird-in-Hand | MD | SOL-10092 | 84580 | 92639.88 | -8059.88 | -8.7% | 77749.8 | 6830.2 | 8.785%
MD: Easton - Shortall | MD | SOL-10091 | 61636 | 40023.09 | 21612.91 | 54% | 85466.35 | -23830.35 | -27.88% | 1.Site was offline at 10:45 on 12/08 and it came back online at 12:15 on 12/18 | 1.SR112401 , SR113249 | 1.Closed
MA: Boston - Seaport Solar | MA | SOL-10772 | 21576 | 15180.36 | 6395.64 | 42.13% | 50367.6 | -28791.6 | -57.16% | 1. Site production was low on 12/14, 12/27 to 12/29 due to snow.
MA: Dedham - Sprague Street | MA | SOL-10773 | 50612 | N/A |  |  | 48227.43 | 2384.57 | 4.944%
MA: Boston - Summer Street | MA | SOL-10764 | 0 | 80245.82 | -80245.82 | -100% | 86871.89 | -86871.89 | -100% | 1. Site was offline for whole month. | 1. SR105609 | 1.Workin progress
MA: Leominster - Spectro Coatings | MA | SOL-10074 | 2840.75 | 15467.04 | -12626.29 | -81.63% | 7674.741 | -4833.991 | -62.99% | 1. Inverter 1 is experiencing multiple tripping's need to replace DMGI | 1. SR111835 | 1.Pending
MA: Braintree - RCAB | MA | SOL-10838 | 34452.5 | 38399.781 | -3947.281 | -10.28% | 43108.084 | -8655.584 | -20.08% | 1. All inverters have heavy shading.
NH: Rochester - Portland Street | NH | SOL-10771 | 522.811 | 2856.259 | -2333.448 | -81.7% | 6675.871 | -6153.06 | -92.17% | 1. Site produced barely from 12/03 to 12/19 due to snow.
NH: Portsmouth - Portsmouth HS | NH | SOL-10769 | 4004.25 | 12157.96 | -8153.71 | -67.06% | 4326.125 | -321.875 | -7.44% | 1. Inverter 3 has heavy shading in the morning and afternoon and inverter 4 has minor shading in the afternoon and all other inverters are experiencing a heavy shading in the evening. 2. Site production was low due to snow.
NH: Portsmouth - Portsmouth WTP | NH | SOL-10770 | 6204.5 | 16104.2 | -9899.7 | -61.47% | 7236.753 | -1032.253 | -14.26% | 1. Inveters 5 and 7 have heavy shading in the morning. 2. Inverter 3 has heavy shading in afternoon and evening. 3. All inverters have a minor shading in the morning.
NH: Rochester - Rochester MS | NH | SOL-10765 | 2490.75 | 17146.32 | -14655.57 | -85.47% | 4477.43 | -1986.68 | -44.37% | 1. All inverters have heavy shading in the morning and inverter 3 has shading in the afternoon.
NH Rochester - Spaulding HS | NH | SOL-10767 | 1144.8136 | 4985.23 | -3840.4164 | -77.04% | 1557.843 | -413.0294 | -26.51% | 1. Inverters have shading in the morning and inverter 1 has heavy shading in morning and during the peak hours.
NH: Rochester - McClelland ES | NH | SOL-10766 | 812.2464 | 4674.752 | -3862.5056 | -82.62% | 1130.805 | -318.5586 | -28.17% | 1. Site produced barely from 12/03 to 12/19 due to snow.
NH: Rochester - Brock St Vocational | NH | SOL-10768 | 763.4368 | 4755.455 | -3992.0182 | -83.95% | 5361.751 | -4598.3142 | -85.76% | 1. Site produced barely from 12/03 to 12/19 due to snow.
OH: Cleveland - CV Kinsman | OH | SOL-10762 | 7630.8359 | 35934 | -28303.1641 | -78.76% | 40153 | -32522.1641 | -81% | 1. Inverter B was offline for whole month. 2.Inverter A offline on 12/11 , 12/12 , 12/14 to 12/24, 12/30, 12/31. On 12/24 technician confirmed Inverter B is kept offline to prevent constant cycling. Additional troubleshooting is required 3.Inverter C offline on 12/11 , 12/12 , 12 /14 to 12/17 , 12/19 , 12/20, 12/30, 12/31. 4. Site was offline from 07:00 on 12/19 to 18:00 on 12/19 5. Inverter D was offline from 12/30, 12/31. | 1.SR092555 2. SR113092 3. SR113314 5. SR113836 | 1.Pending 2.Pending 3.Pending 5. pending | SR113314 | SR113836
OH: Cleveland - CV Wooster | OH | SOL-10763 | 4331.5 | N/A |  |  | 7819.078 | -3487.578 | -44.6% | 1. 8 inverters are offline from 09/05/24 according to the SMA Sunny Portal and need to be replaced. Gen Cap will work directly with Rural Solar. | 1.SR092556 | 1.Pending
PR: Aguadilla - Coca Cola | PR | SOL-10072 | 12561.2785 | 14867.29 | -2306.0115 | -15.51% | 8578.588 | 3982.6905 | 46.43% | 1. Inverter 3 was offline for whole month. 2. Inverter 2 & 3 are offline, reporting "Interference device." | 1.SR106775 2. SR111264 | 1.Closed 2.pending
PR: Bayamon - Coca Cola | PR | SOL-10073 | 49149 | 61912.87 | -12763.87 | -20.62% | 30740.77 | 18408.23 | 59.88% | 1. Inverter 14, 15 and 22 were offline for whole month and inverter 13 was underproducing by 18kW. inverters 16, 17 were underproducing due to a few strings down, and inverter 19 was overheating 2. Inverter 11 was offline on 11/17, reporting "Interference device." | 1. SR108732 2. SR111265 | 1.Closed 2.Pending
PR: Carolina - St. Francis | PR | SOL-10034 | 17858.25 | 32775.32 | -14917.07 | -45.51% | 16036.33 | 1821.92 | 11.36% | 1. Inverter 16 was offline for whole month. 2. Inverter 7 was offline for whole month. 3. Inverter 15 was offline for whole month. 4. Inverter 5 was offline for whole month. 5. Inverter 1 was offline for whole month. 6. Inverter 2 was offline for whole month. 7. Inverter 10 was offline for whole month. 8. Inverter 17 was offline for whole month. | 1. SR092255 2. SR092209 3. SR092095 4. SR103021 5. SR102198 6. SR101997 7. SR101998 8. SR092751 | 1. Pending 2. Pending 3. Pending 4. Pending 5. Pending 6. Pending 7. Pending 8. Pending | SR092095 | SR103021 | SR102198 | SR101997 | SR101998 | SR092751
DC: Chevy Chase -Sinai | DC | SOL-10028 | 3039.06 | 5180.698 | -2141.638 | -41.34% | 4059.351 | -1020.291 | -25.13% | 1. There are two trees that seem to shade one array for whole month. | 1. SR110504 | 1.Pending
DC: Washington - Weinberg 1 | DC | SOL-10039 | 478 | 534.7515 | -56.7515 | -10.61% | 713.721 | -235.721 | -33.03% | 1.site production was low due to snow.
DC: Washington - Weinberg 2 | DC | SOL-10045 | 513 | 616.6371 | -103.6371 | -16.81% | 672.9085 | -159.9085 | -23.76% | 1. Site production was low due to sow.
DC: Washington - Weinberg 3 | DC | SOL-10042 | 588 | 650.3296 | -62.3296 | -9.584% | 803.3094 | -215.3094 | -26.8% | 1. Site is producing as expected

## Sites
Portfolio: | GoodFinch
Site DAS Name | Site | State | Update | DAS | SOL#
ASU - Farmer | AZ: Tempe - ASU - Farmer | AZ |  | PowerTrack | SOL-10748
ASU - Fulton | AZ: Tempe - ASU - Fulton | AZ | AEF | PowerTrack | SOL-10749
JFK Elementary | AZ: Superior - JFK Elementary | AZ | AF | PowerTrack | SOL-10758
ASU - Noble | AZ: Tempe - ASU - Noble | AZ | AEF | PowerTrack | SOL-10750
ASU - Parking #3 | AZ: Tempe - ASU - Parking #3 | AZ | AEF | PowerTrack | SOL-10751
ASU - PE East | AZ: Tempe - ASU - PE East | AZ | AEF | PowerTrack | SOL-10752
ASU - Schwada | AZ: Tempe - ASU - Schwada | AZ | AEF | PowerTrack | SOL-10753
Starshine | AZ: Phoenix - Starshine Academy | AZ |  | PowerTrack | SOL-10757
Yuma Airport | AZ: Yuma Airport | AZ | AEF | PowerTrack | SOL-10754
GCC Globe Solar PV | AZ: Globe - Gila CC | AZ |  | PowerTrack | SOL-10751
GCC Payson Solar PV | AZ: Payson - Gila CC | AZ |  | PowerTrack | SOL-10748
Sequoia Charter School | AZ: Mesa - Sequoia Charter School | AZ |  | PowerTrack | SOL-10759
Southwest College Naturopathic Medicine | AZ: Tempe - SCNM | AZ |  | PowerTrack | SOL-10760
Clayton Hall | DE: Newark - Clayton Hall | DE |  | PowerTrack | SOL-10820
Field House | DE: Newark - UOD Field House | DE |  | PowerTrack | SOL-10821
Wyoming Road | DE: Newark - UOD 461 Wyoming | DE |  | PowerTrack | SOL-10819
Bird in Hand | MD: Presston - Bird-in-Hand | MD |  | PowerTrack | SOL-10092
Shortal | MD: Easton - Shortall | MD |  | PowerTrack | SOL-10091
Seaport | MA: Boston - Seaport Solar | MA |  | PowerTrack | SOL-10772
Sprague St | MA: Dedham - Sprague Street | MA |  | PowerTrack | SOL-10773
Summer St | MA: Boston - Summer Street | MA |  | PowerTrack | SOL-10764
Claremont Flock | MA: Leominster - Spectro Coatings | MA |  | PowerTrack | SOL-10074
RCAB - Pastoral Center | MA: Braintree - RCAB | MA |  | PowerTrack | SOL-10838
Portland St | NH: Rochester - Portland Street | NH |  | PowerTrack | SOL-10771
Portsmouth HS | NH: Portsmouth - Portsmouth HS | NH |  | PowerTrack | SOL-10769
Portsmouth WTP | NH: Portsmouth - Portsmouth WTP | NH |  | PowerTrack | SOL-10770
Rochester Middle School (Brock Street) | NH: Rochester - Rochester MS | NH |  | PowerTrack | SOL-10765
Spaulding HS | NH Rochester - Spaulding HS | NH |  | PowerTrack | SOL-10767
McClelland ES | NH: Rochester - McClelland ES | NH |  | PowerTrack | SOL-10766
Rochester Technical School (Wakefield Street) | NH: Rochester - Brock St Vocational | NH |  | PowerTrack | SOL-10768
CV Kinsman | OH: Cleveland - CV Kinsman | OH | AEF | PowerTrack | SOL-10762
CV Wooster | OH: Cleveland - CV Wooster | OH | AF | PowerTrack | SOL-10763
Aguadilla | PR: Aguadilla - Coca Cola | PR |  | PowerTrack | SOL-10072
Bayamon | PR: Bayamon - Coca Cola | PR |  | PowerTrack | SOL-10073
St Francis | PR: Carolina - St. Francis | PR |  | PowerTrack | SOL-10034
Temple Sinai | DC: Chevy Chase -Sinai | DC |  | PowerTrack | SOL-10028
Weinberg 1 | DC: Washington - Weinberg 1 | DC | AEF | PowerTrack | SOL-10039
Weinberg 2 | DC: Washington - Weinberg 2 | DC | AEF | PowerTrack | SOL-10045
Weinberg 3 | DC: Washington - Weinberg 3 | DC | AEF | PowerTrack | SOL-10042