## Year to Date
HAJJAR SOLAR LLC |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 856813.067 | 85710.863 | 771102.204 | 899.7% | 1163555.432 | -306742.365 | -26.36%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
South Easton - Hajjar Solar LLC | MA | 267868.937 | 0 | 267868.937 |  | 376359.082 | -108490.145 | -28.83%
Hanover - Hajjar Solar LLC | MA | 499453.605 | 0 | 499453.605 |  | 578290.044 | -9164.83 | -1.585%
MA: Pembroke - 28 Riverside Dr. | MA | 38327.525 | 85710.863 | -47383.338 | -55.28% | 208906.306 | -170578.781 | -81.65%
MA: Hyannis - 67 Sea St. | MA | 51163 | 0 | 51163 |  | 0 | 0

## 1st Qtr
HAJJAR SOLAR LLC |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 138923.53 | 0 | 138923.53 | 0% | 167101.31 | -28177.78 | -16.86%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
South Easton - Hajjar Solar LLC | MA | 47225.25 | 0 | 47225.25 |  | 66238.2 | -19012.95 | -28.7%
Hanover - Hajjar Solar LLC | MA | 91698.28 | 0 | 91698.28 |  | 100863.11 | -9164.83 | -9.086%
MA: Pembroke - 28 Riverside Dr. | MA | 0 | 0 | 0 |  | 0 | 0
MA: Hyannis - 67 Sea St. | MA | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
HAJJAR SOLAR LLC |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 252982.335 | 35221.049 | 217761.286 | 618.3% | 382494.263 | -129511.928 | -33.86%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
South Easton - Hajjar Solar LLC | MA | 80271.125 | 0 | 80271.125 |  | 131589.847 | -51318.722 | -39%
Hanover - Hajjar Solar LLC | MA | 160572.21 | 0 | 160572.21 |  | 210710.416 | -50138.206 | -23.79%
MA: Pembroke - 28 Riverside Dr. | MA | 0 | 35221.049 | -35221.049 | -100% | 40194 | -40194 | -100%
MA: Hyannis - 67 Sea St. | MA | 12139 | 0 | 12139 |  | 0 | 0

## 3rd Qtr
HAJJAR SOLAR LLC |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 316231.103 | 0 | 316231.103 | 0% | 413184.531 | -96953.428 | -23.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
South Easton - Hajjar Solar LLC | MA | 100417.812 | 0 | 100417.812 |  | 117684.494 | -17266.682 | -14.67%
Hanover - Hajjar Solar LLC | MA | 173292.855 | 0 | 173292.855 |  | 181753.037 | -8460.182 | -4.655%
MA: Pembroke - 28 Riverside Dr. | MA | 6591.436 | 0 | 6591.436 |  | 113747 | -107155.564 | -94.21%
MA: Hyannis - 67 Sea St. | MA | 35929 | 0 | 35929 |  | 0 | 35929

## 4th Qtr
HAJJAR SOLAR LLC |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 148676.099 | 50489.814 | 98186.285 | 194.5% | 200775.328 | -52099.229 | -25.95%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
South Easton - Hajjar Solar LLC | MA | 39954.75 | 0 | 39954.75 |  | 60846.541 | -20891.791 | -34.34%
Hanover - Hajjar Solar LLC | MA | 73890.26 | 0 | 73890.26 |  | 84963.481 | -11073.221 | -13.03%
MA: Pembroke - 28 Riverside Dr. | MA | 31736.089 | 50489.814 | -18753.725 | -37.14% | 54965.306 | -23229.217 | -42.26%
MA: Hyannis - 67 Sea St. | MA | 3095 | 0 | 3095 |  | 0 | 0

## Jan
HAJJAR SOLAR LLC |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 28219.31 | 0 | 28219.31 | 0% | 28052.3 | 167.01 | 0.5954% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 9957.75 | N/A |  |  | 11033 | -1075.25 | -9.746% | 1.Inverter 1 left unit has tripped offline at 11AM on 12/31 and back online on 01/02, it has been RMA'd since 11/18/24. Inverter 1 primary unit has been RMA'D since 01/15. 2.Inverter 2 left unit was offline from 12/30/24 and back online on 01/04/25. | 1.SR090032, SR095614. 2.SR095301 & SR095351 | SR095614 | SR095301 | SR095351
Hanover - Hajjar Solar LLC | MA | 18261.56 | N/A |  |  | 17019.3 | 1242.26 | 7.299%
MA: Pembroke - 28 Riverside Dr. | MA
MA: Hyannis - 67 Sea St. | MA

## Feb
HAJJAR SOLAR LLC |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 37139.0254 | 0 | 37139.0254 | 0% | 50160.96 | -13021.9346 | -25.96% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 12463.6254 | N/A |  |  | 18443.24 | -5979.6146 | -32.42% | 1.Inverter 1 left unit tripped offline at 14:00 on 02/23 and remained offline through-out the month. Inverter 1 primary unit has been RMA'D since 01/15 back online on 02/16. 2.Inverter 2 left unit was offline from 02/25 and right unit was offline from 02/28. 3. Low generation due to snow/rain. | 1.SR090032, SR095614 & SR097696 2.SR097934 | SR095614 | SR097696 | SR097934
Hanover - Hajjar Solar LLC | MA | 24675.4 | N/A |  |  | 31717.72 | -7042.32 | -22.2% | 1.Low generation due to rain/snow.
MA: Pembroke - 28 Riverside Dr. | MA
MA: Hyannis - 67 Sea St. | MA

## Mar
HAJJAR SOLAR LLC |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 73565.1946 | 0 | 73565.1946 | 0% | 88888.05 | -15322.8554 | -17.24% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 24803.8746 | N/A |  |  | 36761.96 | -11958.0854 | -32.53% | 1.Inverter 1 left unit tripped offline from 14:00 on 02/23 and remained offline through out the month. 2.Inverter 2 left unit was offline from 02/25 and back online on 03/02. On 03/03 technician RMA'd left unit. Inverter 2 right unit was offline on 02/28 and back online on 03/01. Agian offline on 03/06, 03/07, 03/17 and 03/18. Inverter 2 central unit was tripped offline from 15:00 on 03/24. On 03/26, technician RMA'D center relay board. 3.Inverters 2&3 were offline on 03/17 and back online on 03/18. Inverter 2 was offline from 03/30. | 1.SR095614 & SR097696 2. SR097934 &SR099467 3. SR098663 | SR097696 | SR097934 | SR099467 | SR098663
Hanover - Hajjar Solar LLC | MA | 48761.32 | N/A |  |  | 52126.09 | -3364.77 | -6.455% | 1. Inverter 2 middle unit began derating by 15 kW on 03/03. A technician was dispatched and performed an optimizer repair and firmware update. However, the issue reoccurred on 03/04 and has persisted throughout the month. The issue is suspected to be related to a failing optimizer or moisture affecting MC4 connectors under certain conditions. Further investigation is needed with LV technicians. | 1.SR097974
MA: Pembroke - 28 Riverside Dr. | MA
MA: Hyannis - 67 Sea St. | MA

## Apr
HAJJAR SOLAR LLC |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 78491.33 | 0 | 78491.33 | 0% | 101923.152 | -23431.822 | -22.99% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 23748.75 | 0 | 23748.75 |  | 39407.049 | -15658.299 | -39.73% | 1.Inverter 1 left unit tripped offline from 14:00 on 02/23 and back online on 04/04. 2.Inverter 2 left unit was offline from 03/26 and back online on 04/04. Inverter 2 right unit was offline on 03/30 and back online on 04/04. Inverter 2 central unit was tripped offline at 15:00 on 03/24. On 03/26, technician RMA'D center relay board and remained offline through out the month. 3. Inverter 3 tripped offline at 07:00 on 04/07 and back online at 10:30 on 04/10.and again tripped offline at 16:30 on 04/24 and back online at 13:30 on 04/25. and once again tripped offline at 07:00 on 04/26 and back online at 10:00 on 04/28. 4. Inverter 1 center unit was underproducing approximately 14.6 kW since 08/27/24. | 1.SR095614 & SR097696 2. SR097934 &SR099467 3. SR099482, SR100360, SR100526 4. SR097696 | SR097696 | SR097934 | SR099467 | SR099482 | SR100360 | SR100526 | SR097696
Hanover - Hajjar Solar LLC | MA | 54742.58 | 0 | 54742.58 |  | 62516.103 | -7773.523 | -12.43% | 1. Inverter 2 middle unit began derating by 15 kW since 03/03 by compared to its peers and reporting "Internal fan fault".. additionally Inverter 2 right unit tripped offline at 16:00 on 04/15 and primary unit was offline from 07:00 AM and both units are reporting "3 Phase Arc" detection fault and back online at 06:00 04/17. 2. Inverter 2 right unit tripped offline on 04/19 at 11:00 am and middle unit is derating by 7kW compared to its peers and both units are reporting a "3 Phase Possible Arc Detection' fault." and back online at 12:00 on 04/21. 3. Inverter 2 right unit again tripped offline on 04/21 at 16:00 and middle unit tripped offline at 18:00 on 04/22 and is reporting "3 Phase Possible Arc Detection".and back online at 12:00 on 04/23. 4. Inverter 2 center unit is offline at 18:00 on 04/30 and reporting "3 phase possible arc detection". 5. Inverter 1 was offline at 10:15 on 04/28 to end of the month. | 1.SR097974, SR099877 2. SR100046 3. SR100188 4. SR100813 5. SR100539 | SR099877 | SR100046 | SR100188 | SR100813 | SR100539
MA: Pembroke - 28 Riverside Dr. | MA
MA: Hyannis - 67 Sea St. | MA

## May
HAJJAR SOLAR LLC |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 75979.355 | 0 | 75979.355 | 0% | 122094.365 | -46115.01 | -37.77% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 25258.875 | 0 | 25258.875 |  | 46426.23 | -21167.355 | -45.59% | 1. Inverter 2 right unit was offline at 07:00 on 05/30 and back online at 14:00 on 04/04. and again offline at 07:00 on 05/31. Inverter 2 central unit was tripped offline at 15:00 on 03/24. On 03/26, technician RMA'D center relay board and remained offline through out the month. 2. Inverter 1 center unit is and producing approximately 14.6 kW since 08/27/24. | 1. SR097934 &SR099467 2. SR097696 | SR099467 | SR097696
Hanover - Hajjar Solar LLC | MA | 50720.48 | 0 | 50720.48 |  | 75668.135 | -24947.655 | -32.97% | 1. Inverter 2 center unit is offline at 18:00 on 04/30 and reporting "3 phase possible arc detection" and back online at 14:00 on 05/01.It's under Fan RMA replacement. 2. Inverter 1 was offline at 10:15 on 04/28. and back online at 14:30 on 05/01. Additionally inverter 1 right unit is offline since 05/01 and is being RMA'd. 3. Inverter 2 middle unit began derating by 15 kW since 03/03 by compared to its peers and reporting "Internal fan fault". | 1. SR100813 2. SR100539 3. SR097974 | SR100539 | SR097974
MA: Pembroke - 28 Riverside Dr. | MA
MA: Hyannis - 67 Sea St. | MA

## Jun
HAJJAR SOLAR LLC |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 98511.65 | 35221.049 | 63290.601 | 179.7% | 158476.746 | -59965.096 | -37.84%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 31263.5 | 0 | 31263.5 |  | 45756.568 | -14493.068 | -31.67% | 1. Inverter 2 right unit was offline at 07:00 on 05/31 and back online at 07:00 on 06/02. and again tripped offline at 07:00 on 06/30 and back online at 09:00 on 06/30. Inverter 2 central unit was tripped offline at 15:00 on 03/24 and back online at 11:00 on 06/16. 2. Inverter 1 center unit is and producing approximately 14.6 kW since 08/27/24. | 1. SR097934 &SR099467 2. SR097696 | SR099467 | SR097696
Hanover - Hajjar Solar LLC | MA | 55109.15 | 0 | 55109.15 |  | 72526.178 | -17417.028 | -24.01% | 1. Inverter 2 center unit is offline at 10:00 on 05/04 and reporting "3 phase possible arc detection" and offline throurghout the month.It's under Fan RMA replacement. 2. Inverter 2 middle unit began derating by 15 kW since 03/03 by compared to its peers and reporting "Internal fan fault". 3. Inverter 1 right unit is offline since 05/01 and is being RMA'd. | 1. SR100813 2. SR097974 3. SR100539 | SR097974 | SR100539
MA: Pembroke - 28 Riverside Dr. | MA | 0 | 35221.049 | -35221.049 | -100% | 40194 | -40194 | -100% | 1. Inverters 1 and 2 have been offline since 5/27 and are currently under RMA. | 1. SR103208
MA: Hyannis - 67 Sea St. | MA | 12139 | N/A |  |  | N/A |  |  | 1. Inverter 1 is offline & inverter 2 has a history of intermittent communication issue possibly offline(The site donot have meter). | 1. SR104427

## Jul
HAJJAR SOLAR LLC |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 11949 | 0 | 11949 | 0% | 157756 | -145807 | -92.43%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 36391.687 | N/A |  |  | 45207 | -8815.313 | -19.5% | 1. Inverter 3 was offline at 07:00 on 07/11 and back online at 13:00 on 07/13. And again offline at 07:00 on 07/14 and later back online at 15:00 on 07/15. 2. Inverter 1 center unit is and producing approximately 14.6 kW since 08/27/24. | 1. SR099873 2. SR097696 | SR097696
Hanover - Hajjar Solar LLC | MA | 58423.765 | N/A |  |  | 70549 | -12125.235 | -17.19% | 1. Inverter 2 center unit is offline at 10:00 on 05/04 and reporting "3 phase possible arc detection" and offline throurghout the month.It's under Fan RMA replacement. 2. Inverter 2 middle unit began derating by 15 kW since 03/03 by compared to its peers and reporting "Internal fan fault". 3. Inverter 1 right unit is offline since 05/01 and is being RMA'd. | 1. SR100813 2. SR097974 3. SR100539 | SR097974 | SR100539
MA: Pembroke - 28 Riverside Dr. | MA | 0 | N/A |  |  | 42000 | -42000 | -100% | 1. Inverters 1 and 2 have been offline since 5/27 and are currently under RMA. | 1. SR103208
MA: Hyannis - 67 Sea St. | MA | 11949 | N/A |  |  | N/A |  |  | 1. Inverter 1 is offline & inverter 2 has a history of intermittent communication issue possibly offline(The site donot have meter). | 1. SR104427

## Aug
HAJJAR SOLAR LLC |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 123581.391 | 0 | 123581.391 | 0% | 142089 | -18507.609 | -13.03%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 37471 | N/A |  |  | 39930 | -2459 | -6.158% | 1. Inverter 3 was offline at 07:00 on 08/09 and back online at 16:30 on 08/09 and Reporting "DC Isolation. and again offline at 07:00 on 08/31 and Reporting "DC Isolation" in SE portal. 2. Inverter 1 center unit is and producing approximately 14.6 kW since 08/27/24. | 1. SR099873 2. SR097696 | SR097696
Hanover - Hajjar Solar LLC | MA | 65530.35 | N/A |  |  | 63159 | 2371.35 | 3.755% | 1. Inverter 2 center unit is offline at 10:00 on 05/04 and reporting "3 phase possible arc detection" on 08/07, technician replaced Inverter 2 center unit and is back online at 11:00 on 08/07. and again Inverter 2 middle unit tripped offline at 16:30 on 08/11 and reporting "3 Phase Possible Arc Detection and back online at 07:00 on 08/12. Once again Inverter 2 middle unit tripped offline at 15:15 on 08/15 and remained offline throuhg out the month. 2. Inverter 2 middle unit began derating by 15 kW since 03/03 by compared to its peers and reporting "Internal fan fault". 3. Inverter 1 right unit is offline since 05/01 and is being RMA'd, on 08/07, technician replaced Inverter 1 right unit and is back online at 11:00 on 08/07. 4. Inverter 1 right unit was offline at 07:00 on 08/18 and reporting "3 Phase Possible Arc Detection" and back online at 07:00 on 08/19. | 1. SR100813, SR106367, SR106570 2. SR097974 3. SR100539 4. SR106473 | SR106367 | SR106570 | SR097974 | SR100539 | SR106473
MA: Pembroke - 28 Riverside Dr. | MA | 6490.041 | N/A |  |  | 39000 | -32509.959 | -83.36% | 1. Inverters 1 and 2 have been offline since 5/27 and are currently under RMA. | 1. SR103208
MA: Hyannis - 67 Sea St. | MA | 14090 | N/A |  |  | N/A |  |  | 1. Inverter 1 is offline & inverter 2 has a history of intermittent communication issue possibly offline(The site donot have meter). | 1. SR104427

## Sep
HAJJAR SOLAR LLC |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 85885.26 | 0 | 85885.26 | 0% | 113339.531 | -27454.271 | -24.22%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
South Easton - Hajjar Solar LLC | MA | 26555.125 | N/A |  |  | 32547.494 | -5992.369 | -18.41% | 1. Inverter 4 tripped offline at 13:15 on 09/15 and remained offline for the rest of the month. 2. Inverter 1 center unit is and producing approximately 14.6 kW since 08/27/24. | 1. SR107997 2. SR097696 | SR097696
Hanover - Hajjar Solar LLC | MA | 49338.74 | N/A |  |  | 48045.037 | 1293.703 | 2.693% | 1. Inverter 2, unit 2.3 tripped offline at 15:15 on 08/15 and has remained offline since then. 2. Inverter 2 middle unit began derating by 15 kW since 03/03 by compared to its peers and reporting "Internal fan fault". | 1. SR106367, SR106570 2. SR097974 | SR106570 | SR097974
MA: Pembroke - 28 Riverside Dr. | MA | 101.395 | N/A |  |  | 32747 | -32645.605 | -99.69% | 1. Inverters 1 and 2 have been offline since 05/27. Inverter 1 came back online at 15:00 on 09/19; since then, the meter has not been reporting accurate data as the polarities have been changed. | 1. SR103208
MA: Hyannis - 67 Sea St. | MA | 9890 | N/A |  |  | N/A |  |  | 1. Inverter 1 is offline & inverter 2 has a history of intermittent communication issue possibly offline(The site donot have meter). | 1. SR104427

## Oct
HAJJAR SOLAR LLC |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 71560.04 | 21948.553 | 49611.487 | 226% | 90305.097 | -18745.057 | -20.76%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
South Easton - Hajjar Solar LLC | MA | 19587.25 | N/A |  |  | 28104.583 | -8517.333 | -30.31% | 1. Inverter 4 tripped offline at 13:15 on 09/15 and remained offline for the rest of the month. 2. Inverter 1 center unit is and producing approximately 14.6 kW since 08/27/24. 3. Inverter 1 left unit tripped offline at 10:15 reporting ‘AC High Voltage’ and remained offline throughout the month. | 1. SR107997, SR111317 2. SR097696 3. SR111318 | 1. Closed 2. Closed 3. Closed | SR111317 | SR097696 | SR111318
Hanover - Hajjar Solar LLC | MA | 34812.86 | N/A |  |  | 38337.208 | -3524.348 | -9.193% | 1. Inverter 2, unit 2.3 tripped offline at 15:15 on 08/15 and has remained offline since then. | 1. SR106367, SR106570 | 1. Pending | SR106570
MA: Pembroke - 28 Riverside Dr. | MA | 15004.93 | 21948.553 | -6943.623 | -31.64% | 23863.306 | -8858.376 | -37.12% | 1. Inverter 2 is underperforming by 30 kW since 10/24. | 1. SR112823 | 1. New
MA: Hyannis - 67 Sea St. | MA | 2155 | N/A | [5 empty] | 1. All inverters were not communicating due to some network issue.(The site donot have meter). | 1. SR104427, SR107294 | 1. Pending | SR107294

## Nov
HAJJAR SOLAR LLC |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 44601.109 | 14931.361 | 29669.748 | 198.7% | 64854.631 | -20253.522 | -31.23%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
South Easton - Hajjar Solar LLC | MA | 12049.5 | N/A |  |  | 20165.958 | -8116.458 | -40.25% | 1. Inverter 4 tripped offline at 13:15 on 09/15 and remained offline for the rest of the month. 2. Inverter 1 center unit is and producing approximately 14.6 kW since 08/27/24. 3. Inverter 1 (left unit) tripped offline at 10:15 reporting ‘AC High Voltage’ and came back online at 13:15 on 11/20. It tripped offline again at 12:45 on 11/24 due to an isolation fault and came back online at 08:45 on 11/26. 4. Inverter 1 (left unit) tripped offline at 12:30 on 11/28, reporting ‘AC fault and remained offline for the rest of the month. | 1. SR107997,SR111317 2. SR097696 3. SR111318, SR111702 4. SR111883 | 1. Closed 2. Closed 3. Closed 4. Pending | SR111317 | SR097696 | SR111318 | SR111702 | SR111883
Hanover - Hajjar Solar LLC | MA | 22034 | N/A |  |  | 27884.673 | -5850.673 | -20.98% | 1. The site tripped offline at 07:45 on 11/30 with all inverters reporting ‘Grid Voltage,’ and came back online at 13:45 on 11/30. 2. Inverter 2, unit 2.3 middle unit tripped offline at 15:15 on 08/15 and has remained offline since then. | 1. SR111838 2. SR106367, SR106570 | 1. Closed 2. Pending | SR106367 | SR106570
MA: Pembroke - 28 Riverside Dr. | MA | 9947.609 | 14931.361 | -4983.752 | -33.38% | 16804 | -6856.391 | -40.8% | 1. Inverter 2 is underperforming by 30 kW since 10/24. | 1. SR112823 | 1. New
MA: Hyannis - 67 Sea St. | MA | 570 | N/A |  |  | N/A |  |  | 1. All inverters were not communicating due to some network issue.(The site donot have meter). | 1. SR104427, SR107294 | 1. Pending | SR107294

## Dec
HAJJAR SOLAR LLC |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 32514.95 | 13609.9 | 18905.05 | 138.9% | 45615.6 | -13100.65 | -28.72%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
South Easton - Hajjar Solar LLC | MA | 8318 | N/A |  |  | 12576 | -4258 | -33.86% | 1. Inverter 1 left unit was back online on 12/03 but 3 strings were offline for whole month. 2. Site has low production on 12/02, 12/07, 12/14 to 12/16, 12/27 to 12/29 due to snow. | 1. SR111883 | 1. Pending
Hanover - Hajjar Solar LLC | MA | 17043.4 | N/A |  |  | 18741.6 | -1698.2 | -9.061% | 1.Inverter 2, unit 2.3 middle unit tripped offline at 15:15 on 08/15 and has remained offline since then. | 1.SR106367, SR106570 | 1.Pending | SR106570
MA: Pembroke - 28 Riverside Dr. | MA | 6783.55 | 13609.9 | -6826.35 | -50.16% | 14298 | -7514.45 | -52.56% | 1. Inverter 2 is underperforming by 30 kW since 10/24. | 1. SR112823 | 1.New
MA: Hyannis - 67 Sea St. | MA | 370 | N/A |  |  | N/A |  |  | 1. All inverters were not communicating due to some network issue.(The site donot have meter). | 1. SR104427, SR107294 | 1. Pending | SR107294

## Sites
Portfolio: | HAJJAR SOLAR LLC
Site DAS Name | Site | State | Update | DAS
24 Norfolk Ave | South Easton - Hajjar Solar LLC | MA |  | PowerTrack
389 Columbia Road | Hanover - Hajjar Solar LLC | MA | AF | PowerTrack
28 Riverside Drive | MA: Pembroke - 28 Riverside Dr. | MA |  | PowerTrack
CP 460 - 67 Sea St | MA: Hyannis - 67 Sea St. | MA |  | PowerTrack