## Year to Date
KPCA Investment, LLC |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 4141321.7187 | 4311771.638 | -170449.9193 | -3.953% | 4805107.139 | -663785.4203 | -13.81%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 222941.4266 | 225103.617 | -2162.1904 | -0.9605% | 339656 | -116714.5734 | -34.36%
Murrieta - 28150 Keller Rd | CA | 766325 | 772468.768 | -6143.768 | -0.7953% | 880788.963 | 0 | 0%
La Habra - 601 E Imperial Way | CA | 157484.05 | 124305.041 | 33179.009 | 26.69% | 179763.967 | -22279.917 | -12.39%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 820121.1296 | 855583.205 | -35462.0754 | -4.145% | 902065.673 | 0 | 0%
Irwindale - 12761 Schabarum Ave | CA | 201792.49 | 166532.843 | 35259.647 | 21.17% | 250619.15 | -48826.66 | -19.48%
Santa Rosa - 2240 Mercury Way | CA | 652829.6225 | 726888.952 | -74059.3295 | -10.19% | 780709 | 0 | 0%
Dublin - 3100 Dublin Blvd | CA | 1319828 | 1440889.212 | -121061.212 | -8.402% | 1471504.386 | -151676.386 | -10.31%

## 1st Qtr
KPCA Investment, LLC |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 0 | 0 | 0 |  | 0 | 0
Murrieta - 28150 Keller Rd | CA | 0 | 0 | 0 |  | 0 | 0
La Habra - 601 E Imperial Way | CA | 0 | 0 | 0 |  | 0 | 0
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 0 | 0 | 0 |  | 0 | 0
Irwindale - 12761 Schabarum Ave | CA | 0 | 0 | 0 |  | 0 | 0
Santa Rosa - 2240 Mercury Way | CA | 0 | 0 | 0 |  | 0 | 0
Dublin - 3100 Dublin Blvd | CA | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
KPCA Investment, LLC |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 1771758.0585 | 1834976.275 | -63218.2165 | -3.445% | 1939577.029 | -167818.9705 | -8.652%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 105148.9374 | 88704.65 | 16444.2874 | 18.54% | 132650 | -27501.0626 | -20.73%
Murrieta - 28150 Keller Rd | CA | 301660 | 301975.25 | -315.25 | -0.1044% | 338989.4 | -37329.4 | -11.01%
La Habra - 601 E Imperial Way | CA | 60220.63 | 48057.75 | 12162.88 | 25.31% | 67344.57 | -7123.94 | -10.58%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 357011.5841 | 364194.09 | -7182.5059 | -1.972% | 372880.589 | -15869.0049 | -4.256%
Irwindale - 12761 Schabarum Ave | CA | 84093.87 | 65700.18 | 18393.69 | 28% | 95470.97 | -11377.1 | -11.92%
Santa Rosa - 2240 Mercury Way | CA | 294721.0371 | 315356.7 | -20635.6629 | -6.544% | 324424 | -29702.9629 | -9.156%
Dublin - 3100 Dublin Blvd | CA | 568902 | 650987.655 | -82085.655 | -12.61% | 607817.5 | -38915.5 | -6.402%

## 3rd Qtr
KPCA Investment, LLC |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 1583161.5404 | 1688703.693 | -105542.1526 | -6.25% | 1914876.354 | -331714.8136 | -17.32%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 90434.2525 | 87474.947 | 2959.3055 | 3.383% | 129673 | -39238.7475 | -30.26%
Murrieta - 28150 Keller Rd | CA | 289564.5 | 296131.788 | -6567.288 | -2.218% | 349616.033 | -60051.533 | -17.18%
La Habra - 601 E Imperial Way | CA | 61294.87 | 48470.57 | 12824.3 | 26.46% | 72455.727 | -11160.857 | -15.4%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 312541.0868 | 330562.619 | -18021.5322 | -5.452% | 363579.234 | -51038.1472 | -14.04%
Irwindale - 12761 Schabarum Ave | CA | 75985.3 | 65616.524 | 10368.776 | 15.8% | 98977.86 | -22992.56 | -23.23%
Santa Rosa - 2240 Mercury Way | CA | 253233.5312 | 293509.225 | -40275.6938 | -13.72% | 311213 | -57979.4688 | -18.63%
Dublin - 3100 Dublin Blvd | CA | 500108 | 566938.02 | -66830.02 | -11.79% | 589361.5 | -89253.5 | -15.14%

## 4th Qtr
KPCA Investment, LLC |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 786402.1198 | 788091.67 | -1689.5502 | -0.2144% | 950653.756 | -164251.6362 | -17.28%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Chino - 3750-3770 Grand Ave | CA | 27358.2368 | 48924.02 | -21565.7832 | -44.08% | 77333 | -49974.7632 | -64.62%
Murrieta - 28150 Keller Rd | CA | 175100.5 | 174361.73 | 738.77 | 0.4237% | 192183.53 | -17083.03 | -8.889%
La Habra - 601 E Imperial Way | CA | 35968.55 | 27776.721 | 8191.829 | 29.49% | 39963.67 | -3995.12 | -9.997%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 150568.4588 | 160826.496 | -10258.0372 | -6.378% | 165605.85 | -15037.3912 | -9.08%
Irwindale - 12761 Schabarum Ave | CA | 41713.32 | 35216.139 | 6497.181 | 18.45% | 56170.32 | -14457 | -25.74%
Santa Rosa - 2240 Mercury Way | CA | 104875.0542 | 118023.027 | -13147.9728 | -11.14% | 145072 | -40196.9458 | -27.71%
Dublin - 3100 Dublin Blvd | CA | 250818 | 222963.537 | 27854.463 | 12.49% | 274325.386 | -23507.386 | -8.569%

## Jan
KPCA Investment, LLC |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Feb
KPCA Investment, LLC |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Mar
KPCA Investment, LLC |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA
Murrieta - 28150 Keller Rd | CA
La Habra - 601 E Imperial Way | CA
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA
Irwindale - 12761 Schabarum Ave | CA
Santa Rosa - 2240 Mercury Way | CA
Dublin - 3100 Dublin Blvd | CA

## Apr
KPCA Investment, LLC |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 498732.2597 | 522792 | -24059.7403 | -4.602% | 576056.18 | -77323.9203 | -13.42%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 31190.7633 | 26716.3 | 4474.4633 | 16.75% | 40273 | -9082.2367 | -22.55% | 1. Meter A phase CT dropped 20 amps on 9/26/24. There is a 5 % variance between the meter and total inverter power. Will be addressed in next PM. | 1.SR098881
Murrieta - 28150 Keller Rd | CA | 87140 | 90233.95 | -3093.95 | -3.429% | 100122.5 | -12982.5 | -12.97% | 1.The site is producing as expected. The higher delta value indicates that the forecasted values are on the higher side.
La Habra - 601 E Imperial Way | CA | 17571.88 | 14932.1 | 2639.78 | 17.68% | 20943.08 | -3371.2 | -16.1% | 1.The site is producing as expected. The higher delta value indicates that the forecasted values are on the higher side.
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 97799.4949 | 102139.7 | -4340.2051 | -4.249% | 110380.3 | -12580.8051 | -11.4% | 1.Inverter 22 has been down a string (5 kW) since it was re-energized on 05/22/2024. The Operations Team is currently reviewing the issue. 2.Inverter 10 was offline from 04/01 and came back online at 10:30 on 04/04. It went offline again at 17:00 on 04/25 and remained offline for the rest of the month. A dispatch has been scheduled for next month. | 1.SR098879 2.SR099137,SR100773 | SR099137 | SR100773
Irwindale - 12761 Schabarum Ave | CA | 25974.62 | 20129.85 | 5844.77 | 29.04% | 29983.3 | -4008.68 | -13.37% | 1.The site is producing as expected. The higher delta value indicates that the forecasted values are on the higher side.
Santa Rosa - 2240 Mercury Way | CA | 78610.0015 | 86048.7 | -7438.6985 | -8.645% | 98920 | -20309.9985 | -20.53% | 1.Inverter 16 is having an history of multiple trip events. On 04/02, a technician addressed that faults occured due to PV imbalance issues and adjusted settings of comibner boxes. However, the inverter tripped again on 04/03 at 13:45, came online at 11:30 on 04/04,even after technician troubleshooted again inverter tripped at 12:45on 04/04. Issue got resolved after technician ensured all strands were compressed and torqued to 50 in-lbs. Inverter is back online at 14:00 on 04/22 | 1.SR099120,SR099410,SR099504 | SR099410 | SR099504
Dublin - 3100 Dublin Blvd | CA | 160445.5 | 182591.4 | -22145.9 | -12.13% | 175434 | -14988.5 | -8.544% | 1. Inverters 3, 5, and 7 may be swapped with 4, 6, and 8 in PowerTrack, as their performance suggests mismatched string counts—3, 5, and 7 (7-string) are performing like 8-string units, and vice versa. | 1.SR100567

## May
KPCA Investment, LLC |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 624624.6719 | 660255.13 | -35630.4581 | -5.396% | 673935.73 | -49311.0581 | -7.317%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 34717.2294 | 30123.32 | 4593.9094 | 15.25% | 45926 | -11208.7706 | -24.41% | 1.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exwasts between the meter readings and the total inverter power. Thwas wassue was scheduled to be investigated during the upcoming preventive maintenance (PM) event. 2.Inverter 5 started late for production at 07:45 on 05/19.wassue got self resoled. | 1.SR098881 2.SR101671 | SR101671
Murrieta - 28150 Keller Rd | CA | 100090 | 104378.3 | -4288.3 | -4.108% | 118934.8 | -18844.8 | -15.84% | 1. Multiple inverters experiencied tripping events from 10:30AM to 15:30 due technician was onsite for preventive maintenance. 2. Inverter 5 was offline from 15:30 to 16:30 due technician was onsite for preventive maintenance. 3. The site was producing as expected. The higher delta value indicates that the forecasted values are on the higher side. | 1. PM13593 2. PM13593
La Habra - 601 E Imperial Way | CA | 19128.62 | 16120.48 | 3008.14 | 18.66% | 23850.17 | -4721.55 | -19.8% | 1.Inverter 3 down a string from 5/06. issue did not resolve. 2. Inverter 4 was offline from 10:55 to 11:20 on 05/06 due to technician was onsite for preventive maintenance. | 1.SR101329 2. PM13591.
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 128682.0512 | 133149.1 | -4467.0488 | -3.355% | 129050.2 | -368.1488 | -0.2853%
Irwindale - 12761 Schabarum Ave | CA | 27504.75 | 21662.73 | 5842.02 | 26.97% | 32927.56 | -5422.81 | -16.47% | 1. Multiple inverters experiencied tripping events from 11:30AM to 15:30 due technician was onsite for preventive maintenance. 2. The site was producing as expected. The higher delta value indicates that the forecasted values are on the higher side. | 1. PM13589
Santa Rosa - 2240 Mercury Way | CA | 110658.0214 | 118241.5 | -7583.4786 | -6.414% | 110018 | 640.0214 | 0.5817%
Dublin - 3100 Dublin Blvd | CA | 203844 | 236579.7 | -32735.7 | -13.84% | 213229 | -9385 | -4.401% | 1.Inverter 14 tripped offline at 11:15 and self resolved at 11:25 on 05/03. 2. Inverters 3, 5, and 7 may be swapped with inverters 4, 6, and 8 in PowerTrack. Invs 3, 5, and 7 are seven string inverters that are performing like eight string inverters, while 4, 6, and 8 are eight string inverters that are performing like seven strings. Will investigate during PM event. | 1.SR100962 2. SR100567 | SR100567

## Jun
KPCA Investment, LLC |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 648401.1269 | 651929.145 | -3528.0181 | -0.5412% | 689585.119 | -41183.9921 | -5.972%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 39240.9447 | 31865.03 | 7375.9147 | 23.15% | 46451 | -7210.0553 | -15.52% | 1.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exwasts between the meter readings and the total inverter power. This issue was scheduled to be investigated during the upcoming preventive maintenance (PM) event. 2.Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. | 1. SR098881 2. SR103049 | SR103049
Murrieta - 28150 Keller Rd | CA | 114430 | 107363 | 7067 | 6.582% | 119932.1 | -5502.1 | -4.588%
La Habra - 601 E Imperial Way | CA | 23520.13 | 17005.17 | 6514.96 | 38.31% | 22551.32 | 968.81 | 4.296% | 1.Inverter 3 down a string from 5/06. Issue was haven't resolved. | 1. SR101329
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 130530.038 | 128905.29 | 1624.748 | 1.26% | 133450.089 | -2920.051 | -2.188%
Irwindale - 12761 Schabarum Ave | CA | 30614.5 | 23907.6 | 6706.9 | 28.05% | 32560.11 | -1945.61 | -5.975% | 1.Inverter 2 tripped offline at 06:15 on 06/23, reporting a 'Steady State GFCI Fault – Fault0090.' The inverter came back online on 06/24. | 1. SR103317
Santa Rosa - 2240 Mercury Way | CA | 105453.0142 | 111066.5 | -5613.4858 | -5.054% | 115486 | -10032.9858 | -8.688%
Dublin - 3100 Dublin Blvd | CA | 204612.5 | 231816.555 | -27204.055 | -11.74% | 219154.5 | -14542 | -6.636% | 1.Inverters 3, 5, and 7 may be swapped with inverters 4, 6, and 8 in PowerTrack. Invs 3, 5, and 7 are seven string inverters that are performing like eight string inverters, while 4, 6, and 8 are eight string inverters that are performing like seven strings. Will investigate during PM event. | 1. SR100567

## Jul
KPCA Investment, LLC |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 623987.737 | 663153.109 | -39165.372 | -5.906% | 718627 | -94639.263 | -13.17%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 38033.494 | 34071.27 | 3962.224 | 11.63% | 48864 | -10830.506 | -22.16% | 1. Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. 2.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exist between the meter readings and the total inverter power. | 1. SR103049 2. SR104160 | SR104160
Murrieta - 28150 Keller Rd | CA | 115259 | 114481.1 | 777.9 | 0.6795% | 126237 | -10978 | -8.696%
La Habra - 601 E Imperial Way | CA | 24207.37 | 18656.803 | 5550.567 | 29.75% | 25624 | -1416.63 | -5.529%
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 123422.003 | 129061.81 | -5639.807 | -4.37% | 141665 | -18242.997 | -12.88% | 1. Inverter 16 is having reoccurring late starts from 6/12. 2. Inverter 20 is down a string since 7/7. | 1. SR103140 2. SR104320 | SR104320
Irwindale - 12761 Schabarum Ave | CA | 31536.37 | 25932.523 | 5603.847 | 21.61% | 37219 | -5682.63 | -15.27% | 1.Inverter 5 String 4 has low performance. | 1.SR102034
Santa Rosa - 2240 Mercury Way | CA | 97975.5 | 110139.48 | -12163.98 | -11.04% | 117314 | -19338.5 | -16.48%
Dublin - 3100 Dublin Blvd | CA | 193554 | 230810.123 | -37256.123 | -16.14% | 221704 | -28150 | -12.7% | 1.Inverters 3, 5, and 7 may be swapped with inverters 4, 6, and 8 in PowerTrack. Invs 3, 5, and 7 are seven string inverters that are performing like eight string inverters, while 4, 6, and 8 are eight string inverters that are performing like seven strings. | 1. SR100567

## Aug
KPCA Investment, LLC |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 548563.9734 | 603181.84 | -54617.8666 | -9.055% | 654651.87 | -106087.8966 | -16.21%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 31906.6545 | 30044.7 | 1861.9545 | 6.197% | 45234 | -13327.3455 | -29.46% | 1.Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. 2.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exist between the meter readings and the total inverter power. | 1.SR103049 2.SR104160 | SR104160
Murrieta - 28150 Keller Rd | CA | 95153 | 99725.96 | -4572.96 | -4.586% | 114410.4 | -19257.4 | -16.83% | 1.Site is producing as expected, may be issue with forecasted value
La Habra - 601 E Imperial Way | CA | 21199.63 | 16694.73 | 4504.9 | 26.98% | 26525.81 | -5326.18 | -20.08% | 1.Site is producing as expected, may be issue with forecasted value
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 106893.0438 | 114393.8 | -7500.7562 | -6.557% | 123121.9 | -16228.8562 | -13.18% | 1. Inverter 16 is having reoccurring late starts from 6/12. 2. Inverter 20 is down a string since 7/7. | 1.SR103140 2.SR104320 | SR104320
Irwindale - 12761 Schabarum Ave | CA | 25933.63 | 22533.55 | 3400.08 | 15.09% | 33846.76 | -7913.13 | -23.38% | 1.Inverter 5 String 4 has low performance. 2. Inverters 1 and 2 tripped offline at 7:00 on 08/27 and later back online on 08/28 at 07:00 | 1.SR102034 2.SR107041 | SR107041
Santa Rosa - 2240 Mercury Way | CA | 92708.0152 | 107429.3 | -14721.2848 | -13.7% | 107538 | -14829.9848 | -13.79%
Dublin - 3100 Dublin Blvd | CA | 174770 | 212359.8 | -37589.8 | -17.7% | 203975 | -29205 | -14.32% | 1.Low production due to weather on 08/16

## Sep
KPCA Investment, LLC |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 410609.83 | 422368.744 | -11758.914 | -2.784% | 541597.484 | -130987.654 | -24.19%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Chino - 3750-3770 Grand Ave | CA | 20494.104 | 23358.977 | -2864.873 | -12.26% | 35575 | -15080.896 | -42.39% | 1.Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. 2.The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exist between the meter readings and the total inverter power. On 09/16 technician confirmed Replacement CT being quoted. 3.Inverter 5 tripped offline multiple days through out the month. 4.Inverters 1, 2, 3, and 4, along with AC Box 3 will remain offline on 09/25 for safety reasons, as the electrical box that is connected to these inverters is damaged, and it needs to be ensured that the electrical box is back in good condition before turning back on these inverters. These inverters will remain offline until the issue is resolved | 1.SR103049 2.SR104160 , SR104160 3.SR107548 4.SR108510 | SR104160 | SR104160 | SR107548 | SR108510
Murrieta - 28150 Keller Rd | CA | 79152.5 | 81924.728 | -2772.228 | -3.384% | 108968.633 | -29816.133 | -27.36% | 1.Site is producing as expected, may be issue with forecasted value
La Habra - 601 E Imperial Way | CA | 15887.87 | 13119.037 | 2768.833 | 21.11% | 20305.917 | -4418.047 | -21.76% | 1.Site is producing as expected, may be issue with forecasted value
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 82226.04 | 87107.009 | -4880.969 | -5.603% | 98792.334 | -16566.294 | -16.77% | 1. Inverter 16 is having reoccurring late starts from 6/12. 2. Inverter 20 is down a string since 7/7. | 1.SR103140 2.SR104320 | SR104320
Irwindale - 12761 Schabarum Ave | CA | 18515.3 | 17150.451 | 1364.849 | 7.958% | 27912.1 | -9396.8 | -33.67% | 1.Inverter 5 String 4 has low performance. 2.Inverter 2 tripped offline at 6:15 on 09/02 reporting "Steady State GFCI fault - Fault0090". Self resolve on 09/03 3.Inverter 2 dropped a string on 09/18 | 1.SR102034 2. SR107305 3. SR108644 | SR107305 | SR108644
Santa Rosa - 2240 Mercury Way | CA | 62550.016 | 75940.445 | -13390.429 | -17.63% | 86361 | -23810.984 | -27.57%
Dublin - 3100 Dublin Blvd | CA | 131784 | 123768.097 | 8015.903 | 6.477% | 163682.5 | -31898.5 | -19.49% | 1.Site is producing as expected, may be issue with forecasted value

## Oct
KPCA Investment, LLC |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 352157.7018 | 354315.303 | -2157.6012 | -0.6089% | 412083.446 | -59925.7442 | -14.54%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Chino - 3750-3770 Grand Ave | CA | 11963.0368 | 21453.31 | -9490.2732 | -44.24% | 30206 | -18242.9632 | -60.4% | 1. Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. 2. The A-phase CT on the meter recorded a drop of 20 amps on 09/26/2024. In May, the drop was reduced to 10 amps on the same phase. A 5% variance currently exist between the meter readings and the total inverter power. On 09/16 technician confirmed Replacement CT being quoted. 3. Inverter 5 started late multiple days through out the month. 4. Inverters 1, 2, 3, and 4, along with AC Box 3 will remain offline on 09/25 for safety reasons, as the electrical box that is connected to these inverters is damaged, and it needs to be ensured that the electrical box is back in good condition before turning back on these inverters. These inverters will remain offline until the issue is resolved | 1.SR103049 2. SR108381 3.SR107548 4.SR108510 | 1.Pending 2.Pending 3.Pending 4.Pending | SR108381 | SR107548 | SR108510
Murrieta - 28150 Keller Rd | CA | 74713 | 74409.23 | 303.77 | 0.4082% | 79915.35 | -5202.35 | -6.51% | 1. Inverter 2 tripped offline at 10:45 reporting steady state GFCI fault - Fault0090 Static GFCI high on 10/14. It came back online on 10/15 | 1.SR109470 | 1.Closed
La Habra - 601 E Imperial Way | CA | 15416.5 | 12287.47 | 3129.03 | 25.47% | 17169.92 | -1753.42 | -10.21% | 1. Site was producing as expected.
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 69605.51 | 73078.226 | -3472.716 | -4.752% | 76785.43 | -7179.92 | -9.351% | 1. Inverter 16 is having reoccurring late starts from 6/12. 2. Inverter 20 is down a string since 7/7. | 1.SR103140 2. SR104320 | 1.Pending 2.Pending | SR104320
Irwindale - 12761 Schabarum Ave | CA | 17638.62 | 15926.16 | 1712.46 | 10.75% | 22524.36 | -4885.74 | -21.69% | 1.Inverter 5 String 4 has low performance. 2.Inverter 2 dropped a string on 09/18. On 10/27 no string issues found on inverter 2 | 1. SR102034 2. SR108644 | 1.Pending 2.Workin progress | SR108644
Santa Rosa - 2240 Mercury Way | CA | 48677.0351 | 56672.54 | -7995.5049 | -14.11% | 66427 | -17749.9649 | -26.72% | 1. Inverter 3 has evening shading. 2 Inverter 16 has evening and morning shading.
Dublin - 3100 Dublin Blvd | CA | 114144 | 100488.367 | 13655.633 | 13.59% | 119055.386 | -4911.386 | -4.125% | 1. Site is producing as expected.

## Nov
KPCA Investment, LLC |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 236059.107 | 237205.094 | -1145.987 | -0.4831% | 300318 | -64258.893 | -21.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Chino - 3750-3770 Grand Ave | CA | 7236.2 | 14992.3 | -7756.1 | -51.73% | 23963 | -16726.8 | -69.8% | 1. The meter was not reporting the full production of the inverters for the entire month due to a bad CT. 2. Inverters 1 to 4 was offline for whole month. 3. Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. | 1. SR108381 2. SR108510 3. SR103049 | 1. Pending 2.Pending 3.Pending | SR108510 | SR103049
Murrieta - 28150 Keller Rd | CA | 52767 | 52438.15 | 328.85 | 0.6271% | 66549 | -13782 | -20.71% | 1. Site is producing as expected.
La Habra - 601 E Imperial Way | CA | 10738.8 | 8152.342 | 2586.458 | 31.73% | 13897 | -3158.2 | -22.73% | 1. Site is producing as expected.
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 44913.9 | 48522.8 | -3608.9 | -7.438% | 50533 | -5619.1 | -11.12% | 1. Inverter 16 was offline from 06:00 to 11:00 on 11/19. 2. Inverter 20 started late at 11:00 on 11/14, 10:00 on 11/15, and 09:00 on 11/16 and it has had a down string since 07/07. | 1. SR111709, SR103140 2. SR104320, SR111097 | 1.Pending 2. Pending, Closed 3. Closed, Closed | SR103140 | SR104320 | SR111097
Irwindale - 12761 Schabarum Ave | CA | 12685.7 | 10226.925 | 2458.775 | 24.04% | 18320 | -5634.3 | -30.75% | 1. Inverter 5 String 4 has low performance. | 1. SR102034 | 1. Pending
Santa Rosa - 2240 Mercury Way | CA | 32062.507 | 35264.647 | -3202.14 | -9.08% | 43187 | -11124.493 | -25.76% | 1. Site is producing as expected.
Dublin - 3100 Dublin Blvd | CA | 75655 | 67607.93 | 8047.07 | 11.9% | 83869 | -8214 | -9.794% | 1. Site is producing as expected.

## Dec
KPCA Investment, LLC |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 198185.3109 | 196571.273 | 1614.0379 | 0.8211% | 238252.31 | -40066.9991 | -16.82%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Chino - 3750-3770 Grand Ave | CA | 8159 | 12478.41 | -4319.41 | -34.62% | 23164 | -15005 | -64.78% | 1. The meter was not reporting the full production of the inverters for the entire month due to a bad CT. 2. Inverters 1 to 4 was offline for whole month. 3. Inverter 1 is underperforming by 5 kW down compared to its peer inverters since 06/16 at 14:00. | 1. SR108381 2. SR108510 3. SR103049 | 1. Pending 2.Closed 3.Pending | SR103049
Murrieta - 28150 Keller Rd | CA | 47620.5 | 47514.35 | 106.15 | 0.2234% | 45719.18 | 1901.32 | 4.159%
La Habra - 601 E Imperial Way | CA | 9813.25 | 7336.909 | 2476.341 | 33.75% | 8896.75 | 916.5 | 10.3% | 1. Site is producing as expected.
Kaiser - KP3 - SCA Skyport - CN7901 Site | CA | 36049.0488 | 39225.47 | -3176.4212 | -8.098% | 38287.42 | -2238.3712 | -5.846%
Irwindale - 12761 Schabarum Ave | CA | 11389 | 9063.054 | 2325.946 | 25.66% | 15325.96 | -3936.96 | -25.69% | 1. Inverter 5 String 4 has low performance. | 1. SR102034 | 1. Pending
Santa Rosa - 2240 Mercury Way | CA | 24135.5121 | 26085.84 | -1950.3279 | -7.477% | 35458 | -11322.4879 | -31.93% | 1.Site production was low on 12/20 to 12/22 , 12/26, 12/30 , 12/31 due to snow
Dublin - 3100 Dublin Blvd | CA | 61019 | 54867.24 | 6151.76 | 11.21% | 71401 | -10382 | -14.54% | 1.Site production was low on 12/20, 12/21 , 12/31 due to snow
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As meter is not reporting full production due to bad CT actual energy was taken from total inverter energy

## Sites
Portfolio: | KPCA Investment, LLC
Site DAS Name | Site | State | Update | DAS
Kaiser - KP3 - Chino Grand CA6581 | Chino - 3750-3770 Grand Ave | CA | AEF | PowerTrack
Murrietta MOB - CA5341 | Murrieta - 28150 Keller Rd | CA | AEF | PowerTrack
Kaiser - KP3 - La Habra - CA3841 Site | La Habra - 601 E Imperial Way | CA | AEF | PowerTrack
San Jose - Skyport | Kaiser - KP3 - SCA Skyport - CN7901 Site | CA |  | PowerTrack
Kaiser - KP3 - Irwindale MOB & Garage - CA5681 Site | Irwindale - 12761 Schabarum Ave | CA | AEF | PowerTrack
Santa Rosa 6 - CN7001 | Santa Rosa - 2240 Mercury Way | CA | AEF | PowerTrack
Kaiser - KP3 - Dublin - CN2A99 Site | Dublin - 3100 Dublin Blvd | CA |  | PowerTrack