## Year to Date
Luminace |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 32727484.2607 | 35098725.4132 | -2371241.1525 | -6.756% | 47172517.194 | -14445032.9333 | -30.62%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 527721.1504 | 473685.93 | 54035.2204 | 11.41% | 458206.66 | -46377.76 | -10.12%
Berkeley - NJ-22-C893 Berkeley I | NJ | 3220890 | 2614645.9792 | 606244.0208 | 23.19% | 7014619.13 | -3793729.13 | -54.08%
Berkeley - NJ-22-C894 Berkeley II | NJ | 4365321.3791 | 4275984.3 | 89337.0791 | 2.089% | 7055253 | -2689931.6209 | -38.13%
BEMS Landfill East | NJ | 2133737.16 | 4692792.901 | -2559055.741 | -54.53% | 6401119.99 | -4267382.83 | -66.67%
Southampton - BEMS West NJ-22-C898 | NJ | 6018437 | 6734664.2 | -716227.2 | -10.63% | 6748949 | -730512 | -10.82%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 84161.9129 | 32338.865 | 51823.0479 | 160.3% | 31068 | -811.3398 | -2.611%
Lakewood Township - Public Works | NJ | 1430908.1 | 837809.312 | 593098.788 | 70.79% | 1288116.051 | 142792.049 | 11.09%
Canby - Dover - OR-23-C003 | OR | 2988122.918 | 2950277.11 | 37845.808 | 1.283% | 3139998 | -151875.082 | -4.837%
Estacada - Clayfield - OR-23-C001 | OR | 2118413.0294 | 2225583.01 | -107169.9806 | -4.815% | 3497736 | -1379322.9706 | -39.43%
Willamina - Waterford - OR-23-C006 | OR | 2058744.9667 | 2469919.001 | -411174.0343 | -16.65% | 3018213.72 | -959468.7533 | -31.79%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 3929391.49 | 3832361.55 | 97029.94 | 2.532% | 4075837 | -146445.51 | -3.593%
OR-23-C002 SPI - Cork Solar | OR | 1794235.415 | 1713322.435 | 80912.98 | 4.723% | 1754657.043 | 39578.372 | 2.256%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 624212.5853 | 758237.72 | -134025.1347 | -17.68% | 922006 | -297793.4147 | -32.3%
OR: Dundee - Gun Club - OR-23-C009 | OR | 985293.47 | 1026799.3 | -41505.83 | -4.042% | 1133548.6 | -148255.13 | -13.08%
OR: Molalla - Marquam - OR-23-C010 | OR | 447893.684 | 460303.8 | -12410.116 | -2.696% | 633189 | -185295.316 | -29.26%

## 1st Qtr
Luminace |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1526713.3764 | 1623475.4862 | -96762.1098 | -5.96% | 5982362.51 | -4455649.1336 | -74.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 115892.2504 | 0 | 115892.2504 |  | 0 | 0
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 32042.4562 | -32042.4562 | -100% | 1495580.21 | -1495580.21 | -100%
Berkeley - NJ-22-C894 Berkeley II | NJ | 109808.1055 | 271422.9 | -161614.7945 | -59.54% | 1480295 | -1370486.8945 | -92.58%
BEMS Landfill East | NJ | 0 | 13254.93 | -13254.93 | -100% | 1554068.3 | -1554068.3 | -100%
Southampton - BEMS West NJ-22-C898 | NJ | 1043156 | 1306755.2 | -263599.2 | -20.17% | 1352961 | -309805 | -22.9%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 13246.3581 | 0 | 13246.3581 |  | 0 | 0
Lakewood Township - Public Works | NJ | 244610.6624 | 0 | 244610.6624 |  | 99458 | 145152.6624 | 145.9%
Canby - Dover - OR-23-C003 | OR | 0 | 0 | 0 |  | 0 | 0
Estacada - Clayfield - OR-23-C001 | OR | 0 | 0 | 0 |  | 0 | 0
Willamina - Waterford - OR-23-C006 | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C005 Solops SPI - Belvedere Solar | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C002 SPI - Cork Solar | OR | 0 | 0 | 0 |  | 0 | 0
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 0 | 0 | 0 |  | 0 | 0
OR: Dundee - Gun Club - OR-23-C009 | OR | 0 | 0 | 0 |  | 0 | 0
OR: Molalla - Marquam - OR-23-C010 | OR | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Luminace |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 8503548.1283 | 9039653.033 | -536104.9047 | -5.931% | 13787020.76 | -5283472.6317 | -38.32%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 168345.6 | 181763.78 | -13418.18 | -7.382% | 187096.3 | -18750.7 | -10.02%
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 2101906.67 | -2101906.67 | -100%
Berkeley - NJ-22-C894 Berkeley II | NJ | 1267343.2736 | 788162.7 | 479180.5736 | 60.8% | 2118046 | -850702.7264 | -40.16%
BEMS Landfill East | NJ | 2909 | 1275699.521 | -1272790.521 | -99.77% | 2062841.79 | -2059932.79 | -99.86%
Southampton - BEMS West NJ-22-C898 | NJ | 1803228 | 1916638.5 | -113410.5 | -5.917% | 2092575 | -289347 | -13.83%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 29075.4536 | 0 | 29075.4536 |  | 0 | 0
Lakewood Township - Public Works | NJ | 484004.4261 | 0 | 484004.4261 |  | 266490 | 217514.4261 | 81.62%
Canby - Dover - OR-23-C003 | OR | 1059524.378 | 1010842.3 | 48682.078 | 4.816% | 1019387 | 40137.378 | 3.937%
Estacada - Clayfield - OR-23-C001 | OR | 1217604.408 | 1107693.5 | 109910.908 | 9.923% | 1101450 | 116154.408 | 10.55%
Willamina - Waterford - OR-23-C006 | OR | 449018.424 | 862021.177 | -413002.753 | -47.91% | 938139 | -489120.576 | -52.14%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 1425196.633 | 1339749.9 | 85446.733 | 6.378% | 1362976 | 62220.633 | 4.565%
OR-23-C002 SPI - Cork Solar | OR | 597298.532 | 557081.655 | 40216.877 | 7.219% | 536113 | 61185.532 | 11.41%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 0 | 0 | 0 |  | 0 | 0
OR: Dundee - Gun Club - OR-23-C009 | OR | 0 | 0 | 0 |  | 0 | 0
OR: Molalla - Marquam - OR-23-C010 | OR | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
Luminace |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 15118792.0511 | 16119406.912 | -1000614.8609 | -6.208% | 17611337.014 | -2492544.9629 | -14.15%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 157804.4 | 175968.83 | -18164.43 | -10.32% | 177861.65 | -20057.25 | -11.28%
Berkeley - NJ-22-C893 Berkeley I | NJ | 1905939 | 1536702.823 | 369236.177 | 24.03% | 2074278.25 | -168339.25 | -8.116%
Berkeley - NJ-22-C894 Berkeley II | NJ | 1826861 | 1967232.2 | -140371.2 | -7.135% | 2097528 | -270667 | -12.9%
BEMS Landfill East | NJ | 1442937.16 | 2149210.75 | -706273.59 | -32.86% | 1563365.2 | -120428.04 | -7.703%
Southampton - BEMS West NJ-22-C898 | NJ | 1983670.9942 | 2190394 | -206723.0058 | -9.438% | 2061812 | -78141.0058 | -3.79%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 30721.4527 | 20037.303 | 10684.1497 | 53.32% | 19448 | -309.9883 | -1.594%
Lakewood Township - Public Works | NJ | 467497.8865 | 547225.362 | -79727.4755 | -14.57% | 337587.051 | 129910.8355 | 38.48%
Canby - Dover - OR-23-C003 | OR | 1495774.471 | 1493860.3 | 1914.171 | 0.1281% | 1630843 | -135068.529 | -8.282%
Estacada - Clayfield - OR-23-C001 | OR | 726268.494 | 932320.1 | -206051.606 | -22.1% | 1836618 | -1110349.506 | -60.46%
Willamina - Waterford - OR-23-C006 | OR | 1249139.9827 | 1170906.724 | 78233.2587 | 6.681% | 1490721.72 | -241581.7373 | -16.21%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 1966371.993 | 1957366.4 | 9005.593 | 0.4601% | 2094153 | -127781.007 | -6.102%
OR-23-C002 SPI - Cork Solar | OR | 878665.22 | 821887.42 | 56777.8 | 6.908% | 869553.043 | 9112.177 | 1.048%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 237462.39 | 357689.4 | -120227.01 | -33.61% | 424314 | -186851.61 | -44.04%
OR: Dundee - Gun Club - OR-23-C009 | OR | 483722.546 | 514135 | -30412.454 | -5.915% | 538888.1 | -55165.554 | -10.24%
OR: Molalla - Marquam - OR-23-C010 | OR | 265955.061 | 284470.3 | -18515.239 | -6.509% | 394366 | -128410.939 | -32.56%

## 4th Qtr
Luminace |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 7578430.7049 | 8316189.982 | -737759.2771 | -8.871% | 9791796.91 | -2213366.2051 | -22.6%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 85678.9 | 115953.32 | -30274.42 | -26.11% | 93248.71 | -7569.81 | -8.118%
Berkeley - NJ-22-C893 Berkeley I | NJ | 1314951 | 1045900.7 | 269050.3 | 25.72% | 1342854 | -27903 | -2.078%
Berkeley - NJ-22-C894 Berkeley II | NJ | 1161309 | 1249166.5 | -87857.5 | -7.033% | 1359384 | -198075 | -14.57%
BEMS Landfill East | NJ | 687891 | 1254627.7 | -566736.7 | -45.17% | 1220844.7 | -532953.7 | -43.65%
Southampton - BEMS West NJ-22-C898 | NJ | 1188382.0058 | 1320876.5 | -132494.4942 | -10.03% | 1241601 | -53218.9942 | -4.286%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 11118.6484 | 12301.562 | -1182.9136 | -9.616% | 11620 | -501.3516 | -4.315%
Lakewood Township - Public Works | NJ | 234795.125 | 290583.95 | -55788.825 | -19.2% | 584581 | -349785.875 | -59.84%
Canby - Dover - OR-23-C003 | OR | 432824.069 | 445574.51 | -12750.441 | -2.862% | 489768 | -56943.931 | -11.63%
Estacada - Clayfield - OR-23-C001 | OR | 174540.1274 | 185569.41 | -11029.2826 | -5.943% | 559668 | -385127.8726 | -68.81%
Willamina - Waterford - OR-23-C006 | OR | 360586.56 | 436991.1 | -76404.54 | -17.48% | 589353 | -228766.44 | -38.82%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 537822.864 | 535245.25 | 2577.614 | 0.4816% | 618708 | -80885.136 | -13.07%
OR-23-C002 SPI - Cork Solar | OR | 318271.663 | 334353.36 | -16081.697 | -4.81% | 348991 | -30719.337 | -8.802%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 386750.1953 | 400548.32 | -13798.1247 | -3.445% | 497692 | -110941.8047 | -22.29%
OR: Dundee - Gun Club - OR-23-C009 | OR | 501570.924 | 512664.3 | -11093.376 | -2.164% | 594660.5 | -93089.576 | -15.65%
OR: Molalla - Marquam - OR-23-C010 | OR | 181938.623 | 175833.5 | 6105.123 | 3.472% | 238823 | -56884.377 | -23.82%

## Jan
Luminace |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 391768.8975 | 660242.88 | -268473.9825 | -40.66% | 1616542 | -1224773.1025 | -75.77% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 14808.792 | N/A |  |  | N/A |  |  | 1. CSS resolved the DAS issues on 01/03, and M0 started reporting the production on 01/03. However, M1 is reporting negative values. As per the drawings, the site capacity is 365 kW, but meter M0 is reporting 295 kW, and M1 is reporting -295 kW. We have consider M0 production as total site production. Reached out to AE #557940 | 1.SR094989, SR096863 | SR096863
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 31205.78 | -31205.78 | -100% | 412354 | -412354 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1. SR093414
Berkeley - NJ-22-C894 Berkeley II | NJ | 109808.1055 | 271422.9 | -161614.7945 | -59.54% | 406892 | -297083.8945 | -73.01% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1. SR093414
BEMS Landfill East | NJ | 0 | 0 | 0 |  | 435058 | -435058 | -100% | 1.Utility company has shut down site since 06/11/24. | 1.SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 267152 | 357614.2 | -90462.2 | -25.3% | 362238 | -95086 | -26.25% | 1.Site tripped offline at 2:30AM on 01/21 due to Phase A voltage missing Fault and back online at 10AM on 01/30. | 1.SR095756
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter M1 is reporting negative values from 01/03 we have consider M0 production as total site production.

## Feb
Luminace |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 431689.124 | 397154.4762 | 34534.6478 | 8.696% | 1851765.4 | -1420076.276 | -76.69% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 27512.157 | N/A |  |  | N/A |  |  | 1.M1 meter is reporting negative values from 01/03 and through out the Month. AE says likely an onsite issue and to swap CT lead polarity. 2.Site stopped communicating from 02/26 due to some DAS equipment was RMA'd. CSS is about to do capacity test at site after DAS issues resolved. 3. Expected and forecasted data are unavailable. | 1.SR096863 2.SR094989, SR097768 | SR094989 | SR097768
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 836.6762 | -836.6762 | -100% | 461858.4 | -461858.4 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1.SR093413
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | N/A |  |  | 456469 | -456469 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1.SR093414
BEMS Landfill East | NJ | 0 | N/A |  |  | 498875 | -498875 | -100% | 1.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 306069 | 396317.8 | -90248.8 | -22.77% | 403220 | -97151 | -24.09% | 1. Site was tripped offline at 12:15AM on 02/22 due to Phase A voltage missing fault and back online at 11:45AM on 02/28. | 1.SR097638
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 4807.5 | N/A |  |  | N/A |  |  | 1. Expected and forecasted data are unavailable.
Lakewood Township - Public Works | NJ | 93300.467 | N/A |  |  | 31343 | 61957.467 | 197.7% | 1. Forecasted data was very low and expected data are unavailable.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter M1 is reporting negative values from 01/03 we have consider M0 production as total site production.

## Mar
Luminace |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 703255.355 | 566078.13 | 137177.225 | 24.23% | 2514055.11 | -1810799.755 | -72.03% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 73571.3014 | N/A |  |  | N/A |  |  | 1.Site communications are back at 11:45AM on 03/25 after RMA installation. 2. We don't have expected and forecasted energy values for this site. | 1.SR094989,SR097768 | SR097768
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | N/A |  |  | 621367.81 | -621367.81 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098409,SR093413 | SR093413
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | N/A |  |  | 616934 | -616934 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098411,SR093414 | SR093414
BEMS Landfill East | NJ | 0 | 13254.93 | -13254.93 | -100% | 620135.3 | -620135.3 | -100% | 1.The site communication was back at 10:15AM and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 469935 | 552823.2 | -82888.2 | -14.99% | 587503 | -117568 | -20.01% | 1.Site tripped offline 18:15 on 03/05 and back online at 12:45 on 03/14. | 1.SR097638
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 8438.8581 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 151310.1954 | N/A |  |  | 68115 | 83195.1954 | 122.1% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Apr
Luminace |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 854032.0153 | 717297.95 | 136734.0653 | 19.06% | 2800077.99 | -1946045.9747 | -69.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 54203.1 | 57596.35 | -3393.25 | -5.891% | 56794.59 | -2591.49 | -4.563%
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 676075 | -676075 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1. SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | 0 | 0 |  | 676850 | -676850 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1. SR098411
BEMS Landfill East | NJ | 0 | 12059.7 | -12059.7 | -100% | 651557.4 | -651557.4 | -100% | 1.The site communication was back at 10:15AM and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 635861 | 647641.9 | -11780.9 | -1.819% | 658293 | -22432 | -3.408%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 9269.4465 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 154698.4688 | N/A |  |  | 80508 | 74190.4688 | 92.15% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## May
Luminace |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 3877714.643 | 3723083.84 | 154630.803 | 4.153% | 5379743.8 | -1502029.157 | -27.92% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 54648.5 | 59815.54 | -5167.04 | -8.638% | 63486.3 | -8837.8 | -13.92% | 1. Low production due to rain
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 710210 | -710210 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 701245.2736 | 191085.9 | 510159.3736 | 267% | 710606 | -9360.7264 | -1.317% | 1.The site was dealing with utility-related issues due to damaged CTs and PTs in their metering bank.Site was back online at 16:00EDT on 05/20. | 1.SR098411
BEMS Landfill East | NJ | 0 | 586005 | -586005 | -100% | 695675.5 | -695675.5 | -100% | 1.The site communication was back at 10:15 and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 628239 | 645088.6 | -16849.6 | -2.612% | 704768 | -76529 | -10.86% | 1. Low production due to rain
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 9749.9441 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 157465.6563 | N/A |  |  | 92403 | 65062.6563 | 70.41% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR | 499021.269 | 471441.3 | 27579.969 | 5.85% | 494897 | 4124.269 | 0.8334% | 1. Multiple trackers had been stuck since 04/03 and started tracking again on 05/22. 2. Inverters 7, 8, and 16 are experiencing morning shading, with inverter 8 in particular not reaching its full production until 09:45. | 1. SR101115 2. SR101155 | SR101155
Estacada - Clayfield - OR-23-C001 | OR | 554193.004 | 515253.5 | 38939.504 | 7.557% | 532245 | 21948.004 | 4.124% | 1. Multiple trackers had been stuck since 05/07 and started tracking again on 05/22. 2. The site tripped offline at 14:00 on 05/12 and came back online at 09:00 on 05/13. | 1. SR101126 2. SR101287 | SR101287
Willamina - Waterford - OR-23-C006 | OR | 345311.5 | 387541.9 | -42230.4 | -10.9% | 464151 | -118839.5 | -25.6% | 1. All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. 2. The site tripped offline at 10:00 on 05/23 and came back online at 11:15 on 05/29. | 1. SR101124 2. SR101894 | SR101894
OR-23-C005 Solops SPI - Belvedere Solar | OR | 641330.014 | 599695.6 | 41634.414 | 6.943% | 653170 | -11839.986 | -1.813% | 1. Site tripped offline at 16:07 on 05/15 and came back online at 08:30 on 05/20. | 1. SR101566
OR-23-C002 SPI - Cork Solar | OR | 286510.482 | 267156.5 | 19353.982 | 7.244% | 258132 | 28378.482 | 10.99%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Jun
Luminace |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 3771801.47 | 4599271.243 | -827469.773 | -17.99% | 5607198.97 | -1835397.5 | -32.73% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 59494 | 64351.89 | -4857.89 | -7.549% | 66815.41 | -7321.41 | -10.96% | 1. Site has low production on 06/08, 06/26, 06/15, 06/16, 06/17, 06/27 due to low irradiance.
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 715621.67 | -715621.67 | -100% | 1.Site was offline for whole month. | 1.SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 566098 | 597076.8 | -30978.8 | -5.188% | 730590 | -164492 | -22.51% | 1.Site tripped offline since 13:00 on 06/27. | 1.SR103839
BEMS Landfill East | NJ | 2909 | 677634.821 | -674725.821 | -99.57% | 715608.89 | -712699.89 | -99.59% | 1.Site was offline for whole month. | 1.SR098408, SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 539128 | 623908 | -84780 | -13.59% | 729514 | -190386 | -26.1% | 1.Site tripped offline at 14:45 on 06/05 and was back online at 16:15 on 06/05,again tripped offline at 07:45 on 06/08 reporting reporting "Missing Phase A Voltage" and was back online at 10:00 on 06/09,again tripped offline at 23:45 on 06/10 and was back online at 08:15 on 06/12,again tripped offline at 20:00 on 06/14 and remained offline throughout the month. | 1.SR102671
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 10056.063 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 171840.301 | N/A |  |  | 93579 | 78261.301 | 83.63% | 1.Inverter 2.3 was underperforming by 6KW since 06/01 during peak hours and remained the same throughout the month | 1.SR103097
Canby - Dover - OR-23-C003 | OR | 560503.109 | 539401 | 21102.109 | 3.912% | 524490 | 36013.109 | 6.866%
Estacada - Clayfield - OR-23-C001 | OR | 663411.404 | 592440 | 70971.404 | 11.98% | 569205 | 94206.404 | 16.55% | 1.Tracker motor 68 was struck at -58 degrees at 08:30 pdt on 06/10 and was back at 13:45 pdt on 06/24 | 1.SR103219
Willamina - Waterford - OR-23-C006 | OR | 103706.924 | 474479.277 | -370772.353 | -78.14% | 473988 | -370281.076 | -78.12% | 1.All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. | 1.SR101124
OR-23-C005 Solops SPI - Belvedere Solar | OR | 783866.619 | 740054.3 | 43812.319 | 5.92% | 709806 | 74060.619 | 10.43%
OR-23-C002 SPI - Cork Solar | OR | 310788.05 | 289925.155 | 20862.895 | 7.196% | 277981 | 32807.05 | 11.8%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Jul
Luminace |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 5167208.148 | 5683836.835 | -516628.687 | -9.089% | 5773431.353 | -606223.205 | -10.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 57705 | 63485.59 | -5780.59 | -9.105% | 67817.09 | -10112.09 | -14.91% | 1. Inverter 8 tripped offline at 17:00 on 07/06 and back online on 07/07. Inverter again went offline at 9:15 on 07/07 and back online at 12:40 on the same day. and inverter 8 started late on 07/21 at 10:45. | 1. SR104065
Berkeley - NJ-22-C893 Berkeley I | NJ | 586285 | 562423.289 | 23861.711 | 4.243% | 753344.5 | -167059.5 | -22.18% | 1. The site had been offline for several months and came back online at 15:30 on 07/02. 2. Site was offline from 12:00 to 14:00 on 07/29 due to PM Event | 1. SR098409 2. PM11764
Berkeley - NJ-22-C894 Berkeley II | NJ | 697981 | 698857.1 | -876.1 | -0.1254% | 760155 | -62174 | -8.179% | 1. SIte was offline since 06/27 and back online at 13:00 on 07/03. 2. Inverter tripped offline 16:45 on 07/31 due to"Error Error" and remaied offline. | 1. SR103839 2. SR105463 | SR105463
BEMS Landfill East | NJ | 328242.16 | 743855.75 | -415613.59 | -55.87% | 283735 | 44507.16 | 15.69% | 1. The site had been offline for several months and came back online at 15:00 on 07/21. | 1.SR098408, SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 771229 | 807871.5 | -36642.5 | -4.536% | 764197 | 7032 | 0.9202% | 1. Site started late on 07/17 at 08:30. | 1. SR102671
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 11583.441 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 139268.824 | 195547.462 | -56278.638 | -28.78% | 94258 | 45010.824 | 47.75% | 1. Site tripped offline at 16:15 on 07/01 and back online at 8:00 on 07/09. | 1. SR103899
Canby - Dover - OR-23-C003 | OR | 606657.224 | 607264 | -606.776 | -0.09992% | 628020 | -21362.776 | -3.402%
Estacada - Clayfield - OR-23-C001 | OR | 345245.485 | 407692.8 | -62447.315 | -15.32% | 731514 | -386268.515 | -52.8% | 1. Tracker motor 26.5 was strucked since 07/07. Tracker has not returned to service and will remain open for client visibility during ongoing EPC punch lists 2. Site tripped offline at 8:30 on 07/15. This site has not returned to service and will remain open for client visibility during ongoing EPC punch lists | 1. SR104276 2. SR104461 | SR104461
Willamina - Waterford - OR-23-C006 | OR | 446366.5 | 465402.724 | -19036.224 | -4.09% | 547504.72 | -101138.22 | -18.47% | 1. Site was offline from 08:15 on 07/26 to 09:15 on 07/28 and again site was offline from 20:30 o 07/28 to end of month. 2. Since the meter did not communicate from 06/06 to 07/10, the total meter energy was backfilled on 07/10. Therefore, we used the inverter energy from 07/01 to 07/10 and added it with the production meter energy from 07/11 to 07/31. | 1. SR105123
OR-23-C005 Solops SPI - Belvedere Solar | OR | 828134.537 | 805271.2 | 22863.337 | 2.839% | 823154 | 4980.537 | 0.6051%
OR-23-C002 SPI - Cork Solar | OR | 348509.977 | 326165.42 | 22344.557 | 6.851% | 319732.043 | 28777.934 | 9.001%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Aug
Luminace |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 4965475.9051 | 4988205.532 | -22729.6269 | -0.4557% | 5787157.721 | -821681.8159 | -14.2% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 55645.4 | 61869.44 | -6224.04 | -10.06% | 60498.02 | -4852.62 | -8.021% | 1. Inverter 4 was underproduced for whole month. | 1. SR107731
Berkeley - NJ-22-C893 Berkeley I | NJ | 693283 | 539725.412 | 153557.588 | 28.45% | 701899.15 | -8616.15 | -1.228% | 1.Site was offline at 20:15 on 08/20 and came back at 12:00 on 08/21 | 1.SR106617
Berkeley - NJ-22-C894 Berkeley II | NJ | 626497 | 679139.4 | -52642.4 | -7.751% | 712241 | -85744 | -12.04% | 1.Inverter 1 offline 16:45 on 07/31 and it came back online at 10:15 on 08/04 2.Site was offline on 08/14 and came back online at 13:15 on 08/15 3.Site was offline at 20:25 to 10:15 on 08/21 | 1.SR105463 2.SR106265 3.SR106618 | SR106265 | SR106618
BEMS Landfill East | NJ | 663197 | 776737.4 | -113540.4 | -14.62% | 687675.5 | -24478.5 | -3.56% | 1. Inverter 1 combiner 13, 14, 15 and 16 are offline since site regained its communications on 07/21. | 1.SR106977
Southampton - BEMS West NJ-22-C898 | NJ | 695453 | 774345.9 | -78892.9 | -10.19% | 697041 | -1588 | -0.2278% | 1. Site was producing as expected.
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 10886.3789 | 11437.18 | -550.8011 | -4.816% | 10813 | 73.3789 | 0.6786%
Lakewood Township - Public Works | NJ | 184757.1875 | 194634.4 | -9877.2125 | -5.075% | 174400.051 | 10357.1365 | 5.939%
Canby - Dover - OR-23-C003 | OR | 503949.346 | 491321.7 | 12627.646 | 2.57% | 580932 | -76982.654 | -13.25% | 1. Inverter 8 and 6 have heavy morning shading
Estacada - Clayfield - OR-23-C001 | OR | 141023.273 | 201984.4 | -60961.127 | -30.18% | 624249 | -483225.727 | -77.41% | 1.Tracker motor 26.5 was strucked since 07/07. Back online 10:00 on 08/22 2The site tripped offline at 08:30 on 07/15. The inverters came back online at 16:45 on 08/20, but the meter was not communicating as of 17:25. Meter communications were restored at 10:45 on 08/22. 3.All trackers are stowed from 8/23/25 reporting "Manual_Mode_2: Manual Mode ON Manual_Mode_3: Manual Mode ON". on 08/29 all trackers are tracking except row 18 (18.1 through 18.10) 4.Site tripped offline at 07:45 to 16:30 on 08/27 | 1.SR104276 2. SR104461 3. SR106841 4. SR107017 | SR104461 | SR106841 | SR107017
Willamina - Waterford - OR-23-C006 | OR | 419845.1437 | 325034.6 | 94810.5437 | 29.17% | 510859 | -91013.8563 | -17.82% | 1. All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. 2.Site was back online at 12:15 on 08/05 and again site tripped offline at 08:00 on 08/08 and came back online at 16:15 on 08/11 | 1.SR101124 2. SR105123 | SR105123
OR-23-C005 Solops SPI - Belvedere Solar | OR | 678379.971 | 666487.9 | 11892.071 | 1.784% | 724856 | -46476.029 | -6.412%
OR-23-C002 SPI - Cork Solar | OR | 292559.205 | 265487.8 | 27071.405 | 10.2% | 301694 | -9134.795 | -3.028%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR
OR: Dundee - Gun Club - OR-23-C009 | OR
OR: Molalla - Marquam - OR-23-C010 | OR

## Sep
Luminace |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 4986107.998 | 5447364.545 | -461256.547 | -8.468% | 6050747.94 | -1064639.942 | -17.6%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 44454 | 50613.8 | -6159.8 | -12.17% | 49546.54 | -5092.54 | -10.28% | 1. Inverter 4 was underperforming by 6kW for whole month. 2. Inverter 8 was offline fom 07:00 to 11:15 on 09/10. | 1. SR107731 2. SR107760 | SR107760
Berkeley - NJ-22-C893 Berkeley I | NJ | 626371 | 434554.122 | 191816.878 | 44.14% | 619034.6 | 7336.4 | 1.185% | 1. Combiner 1-5 was isolated for whole month. | 1. SR106974
Berkeley - NJ-22-C894 Berkeley II | NJ | 502383 | 589235.7 | -86852.7 | -14.74% | 625132 | -122749 | -19.64% | 1. Site was offline from 16:00 on 09/04 to 12:00 on 09/08. 2. Inverter was derated to 2800kW for whole month due to bad fan. | 1. SR107483 2. SR107895 | SR107895
BEMS Landfill East | NJ | 451498 | 628617.6 | -177119.6 | -28.18% | 591954.7 | -140456.7 | -23.73% | 1. Site was offline from 12:00 on 09/01 to 10:45 on 09/02 and again the site was offline from 11:00 on 09/03 to 10:30 on 09/04 and again the site was offline from 13:00 on 09/14 to 09:00 on 09/19 and again the inverter was offline from 08:30 to 11:15 on 09/23 and from 09:00 to 10:45 on 09/24. | 1. SR107944, SR107388, SR107269 | SR107388 | SR107269
Southampton - BEMS West NJ-22-C898 | NJ | 516988.9942 | 608176.6 | -91187.6058 | -14.99% | 600574 | -83585.0058 | -13.92% | 1. Site was offline from 11:30 to 14:00 on 09/23 and again site was offline from 19:00 on 09/23 to 07:00 on 09/26 and again the site was offline from 16:30 on 09/27 to end of the month. | 1. SR108453, SR108684 | SR108684
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 8251.6328 | 8600.123 | -348.4902 | -4.052% | 8635 | -383.3672 | -4.44%
Lakewood Township - Public Works | NJ | 143471.875 | 157043.5 | -13571.625 | -8.642% | 68929 | 74542.875 | 108.1% | 1. As per weather station the plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.
Canby - Dover - OR-23-C003 | OR | 385167.901 | 395274.6 | -10106.699 | -2.557% | 421891 | -36723.099 | -8.704%
Estacada - Clayfield - OR-23-C001 | OR | 239999.736 | 322642.9 | -82643.164 | -25.61% | 480855 | -240855.264 | -50.09% | 1. The site was offline from 08:45 on 09/01 to 13:00 on 09/02, from 07:30 to 17:45 on 09/03, and from 07:30 to 16:00 on 09/08. It was also offline from 15:00 on 09/12 to 08:30 on 09/17. Additionally, the site was offline from 09:00 on 09/25 through the end of the month. 2. All trackers were not communicated from 09/10 to end of the month. | 1. SR107017 2. SR106841 | SR106841
Willamina - Waterford - OR-23-C006 | OR | 382928.339 | 380469.4 | 2458.939 | 0.6463% | 432358 | -49429.661 | -11.43% | 1. The rating of all inverters are 122.14kW but they are limited to 85kW. | 1. SR101124
OR-23-C005 Solops SPI - Belvedere Solar | OR | 459857.485 | 485607.3 | -25749.815 | -5.303% | 546143 | -86285.515 | -15.8% | 1. All trackers were not communicating from 09/05 to end of the month. 2. Site was offline from 07:45 to 15:15 on 09/02. | 1. SR107723 2. SR107292 | SR107292
OR-23-C002 SPI - Cork Solar | OR | 237596.038 | 230234.2 | 7361.838 | 3.198% | 248127 | -10530.962 | -4.244%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 237462.39 | 357689.4 | -120227.01 | -33.61% | 424314 | -186851.61 | -44.04% | 1. Inverter 16 was offline from 09:30 on 09/28 to 02:30 on 09/29. 2. Inverter 3 being offline for most of the days in month. 3. Inverter 11 started late on 09/06 at 10:00. 4. Meter was not capturing total inverter production for whole month. 5. Motor 28 through 40 was stuck. | 1. SR108693 2. SR108253 3. SR107549 4. SR107187 5. SR107186 | SR108253 | SR107549 | SR107187 | SR107186
OR: Dundee - Gun Club - OR-23-C009 | OR | 483722.546 | 514135 | -30412.454 | -5.915% | 538888.1 | -55165.554 | -10.24% | 1. Inverter 8 and 2 had heavy morning shading.
OR: Molalla - Marquam - OR-23-C010 | OR | 265955.061 | 284470.3 | -18515.239 | -6.509% | 394366 | -128410.939 | -32.56% | 1. Inverters was 10,14,15 are underperforming by 7kW, and inverters 1,3,8,12,13 are underperforming by 5kW for whole month. 2. All trackers were stuck for whole month. | 1. SR108553 2. SR108552 | SR108552

## Oct
Luminace |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 3746334.5699 | 3815106.086 | -68771.5161 | -1.803% | 4778606.42 | -1032271.8501 | -21.6%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Raymond Ed Re-Development - DC-23-0001 | DC | 41881.7 | 51253.6 | -9371.9 | -18.29% | 40799.02 | 1082.68 | 2.654% | 1. Inverter 8 was offline fom 07:00 to 12:30 on 10/30 due to insulation resistance low. 2. Inverter 4 underperforming by 6kW since 09/10. | 1. SR110376 2. SR107731 | 1. pending 2. Closed | SR107731
Berkeley - NJ-22-C893 Berkeley I | NJ | 569330 | 362283.8 | 207046.2 | 57.15% | 538602.5 | 30727.5 | 5.705% | 1. Combiner 1-5 was isolated for whole month. 2. The site went offline at 04:45 on 10/30 due to the SEL relay being open. Later, a technician reset the relay, and the site was back online at 11:15 on 10/31. | 1. SR106974 2. SR110353 | 1. Closed 2. Closed | SR110353
Berkeley - NJ-22-C894 Berkeley II | NJ | 515913 | 562736.9 | -46823.9 | -8.321% | 544464 | -28551 | -5.244% | 1. The site went offline at 04:45 on 10/30 due to the SEL relay being open. Later, a technician reset the relay, and the site was back online at 11:15 on 10/31. 2. The inverter was derated to 2800 kW since 09/12 due to a faulty fan. After the fan was replaced on 10/14, the inverter has been producing as expected. | 1. SR107483 2. SR107895 | 1. Closed 2. Closed | SR107895
BEMS Landfill East | NJ | 388069 | 518793.3 | -130724.3 | -25.2% | 507032.4 | -118963.4 | -23.46% | 1. Inverter is derating at 120kW since 10/17 and reporting "FRT". 2. Site tripped offline at 17:30 on 10/17 and back online at 10:15 on 10/24. | 1. SR107944 2.SR109662 | 1. pendin 2. Closed | SR109662
Southampton - BEMS West NJ-22-C898 | NJ | 553958.0058 | 565464.6 | -11506.5942 | -2.035% | 514787 | 39171.0058 | 7.609% | 1. The site tripped offline at 16:30 on 09/27. After the technician closed the recloser, the site was back online at 09:30 on 10/01. 2. The site tripped offline at 12:30 on 10/30 due to SEL relay open after remotely closed in the relay site is back online at 08:15 on 10/30. | 1. SR108453, SR108684 2. SR110363 | 1. Closed 2. Closed | SR108684 | SR110363
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 5682.1406 | 6072.086 | -389.9454 | -6.422% | 5947 | -264.8594 | -4.454%
Lakewood Township - Public Works | NJ | 111622.375 | 128188.3 | -16565.925 | -12.92% | 524200 | -412577.625 | -78.71% | 1. Inverter 2-3 is underperforming approximately 6kW compared to its peers since 06/18. Quote expired | 1. SR103097 | 1. closed
Canby - Dover - OR-23-C003 | OR | 242980.461 | 253658.8 | -10678.339 | -4.21% | 253269 | -10288.539 | -4.062% | 1.Inverter 8 tripped offline at 14:30 on 10/05, reporting a "Fault: Loss of Main." It was back online at 07:00 on 10/08. | 1. SR109068 | 1. Closed
Estacada - Clayfield - OR-23-C001 | OR | 8898.2392 | 13578.6 | -4680.3608 | -34.47% | 290850 | -281951.7608 | -96.94% | 1. The site went offline at 09:00 on 09/25 due to the SEL relay being in an open state. After the EPC was onsite and closed the relay, the site was back online at 11:00 on 10/29. However, it tripped offline again at 08:45 on 10/30 due to the recloser being in an open state and remained offline through the end of the month. 2. All trackers were not communicated from 09/10 to end of the month. | 1. SR107017 2. SR106841 | 1. Pending 2. pending | SR106841
Willamina - Waterford - OR-23-C006 | OR | 148020.301 | 183078.2 | -35057.899 | -19.15% | 278687 | -130666.699 | -46.89% | 1. The rating of all inverters are 122.14kW but they are limited to 85kW. 2. Site tripped offline at 08:35 on 10/16 and back online at 17:15 on 10/29. | 1. SR101124 2. SR109596 | 1. Pending 2. pending | SR109596
OR-23-C005 Solops SPI - Belvedere Solar | OR | 303876.678 | 309990 | -6113.322 | -1.972% | 317302 | -13425.322 | -4.231% | 1. All trackers were not communicating starting from 09/05, and all trackers resumed normal tracking on 10/14. | 1. SR107723 | 1. Closed
OR-23-C002 SPI - Cork Solar | OR | 166530.081 | 166178.5 | 351.581 | 0.2116% | 160287 | 6243.081 | 3.895%
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 224317.4943 | 226176.3 | -1858.8057 | -0.8218% | 257061 | -32743.5057 | -12.74% | 1. Inverter 3 being offline for most of the days in month. 3. Motors 28 through 40 were stuck, and all tracker motors have been operating normally since 10/16. | 1. SR108253 2. SR107186 | 1. Pending 2. Closed | SR107186
OR: Dundee - Gun Club - OR-23-C009 | OR | 283316.471 | 291819.6 | -8503.129 | -2.914% | 306495.5 | -23179.029 | -7.563% | 1. Inverter 8 and 2 had heavy morning shading.
OR: Molalla - Marquam - OR-23-C010 | OR | 181938.623 | 175833.5 | 6105.123 | 3.472% | 238823 | -56884.377 | -23.82% | 1. Inverters 10, 14, and 15 were underperforming by 7 kW, while inverters 1, 3, 8, 12, and 13 were underperforming by 5 kW. All inverters have been producing as expected since 10/07. 2. All trackers were stuck since 09/25 and all trackers resumed normal tracking from 10/07. 3. Site was offline at 13:30 on 10/25 and offline through the end of the month. | 1. SR108553 2. SR108552 3. SR110001 | 1. Closed 2. Closed 3. pending | SR108552 | SR110001

## Nov
Luminace |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 2298179.1048 | 2491008.389 | -192829.2842 | -7.741% | 2797317.62 | -499138.5152 | -17.84%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Raymond Ed Re-Development - DC-23-0001 | DC | 27129.7 | 37157.19 | -10027.49 | -26.99% | 29884.82 | -2755.12 | -9.219% | 1. Inverter 8 started late for the production at 11:45 on 11/03 2. Inverter 4 underperforming by 6kW since 09/10. | 1. SR110376 2. SR107731 | 1.Closed 2.Closed | SR107731
Berkeley - NJ-22-C893 Berkeley I | NJ | 434359 | 431931.7 | 2427.3 | 0.562% | 441944.3 | -7585.3 | -1.716%
Berkeley - NJ-22-C894 Berkeley II | NJ | 350590 | 350589.9 | 0.1 | 2.852e-05% | 447273 | -96683 | -21.62% | 1. The inverter was derated to 2800 kW since 09/12 due to a faulty fan. After the fan was replaced on 10/14, the inverter has been producing as expected. 2.Inverter came back online at 13:15 on 11/04 | 1. SR107895 2. SR107483 | 1.Closed 2.closed | SR107483
BEMS Landfill East | NJ | 273275 | 381659.8 | -108384.8 | -28.4% | 398647.2 | -125372.2 | -31.45% | 1.Site tripped offline at 01:00 on 11/06 and it came back online at 10:30 on 11/07 2.Site offline from 16:30 to 17:30 on 11/14 and again offline on 11/15 came back online at 08:45 on11/18 3.Site was offline on 11/24 and came back online at 09:15 on 11/25 4.Inverter is offline at 19:30 on 11/29 and remained offline throughout the month. | 1.SR110708 2.SR111113 3.SR111513 4.SR111844 | 1.Closed 2.Closed 3.Pending 4.Closed | SR111113 | SR111513 | SR111844
Southampton - BEMS West NJ-22-C898 | NJ | 372982 | 400391.1 | -27409.1 | -6.846% | 405788 | -32806 | -8.085%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 3288.9766 | 3454.859 | -165.8824 | -4.801% | 3503 | -214.0234 | -6.11%
Lakewood Township - Public Works | NJ | 71255.625 | 86632.63 | -15377.005 | -17.75% | 34329 | 36926.625 | 107.6% | 1. Inverter 2-3 is underperforming approximately 6kW compared to its peers since 06/18. Quote expired 2. Inverter 2.2 and 2.3 should each have 10 strings connected per drawing. Based on production anomalies the PM photos were checked and inverter 2.2, derated to 55kW, has 11 strings connected while inverter 2.3, 60kW, only has 9. The extra string on the derated inverter results in production losses during high-irradiance months. | 1.SR103097 2.SR110653 | 1.Closed 2.Pending | SR110653
Canby - Dover - OR-23-C003 | OR | 108098.691 | 109293 | -1194.309 | -1.093% | 134473 | -26374.309 | -19.61% | 1.Tracker Motor 16.1 through 16.10 are stuck. Tracker motor 5.1 is also stuck from 11/02 | 1. SR110673 | 1.Pending
Estacada - Clayfield - OR-23-C001 | OR | 93110.9822 | 99761.35 | -6650.3678 | -6.666% | 153570 | -60459.0178 | -39.37% | 1.Site was offline at 08:45 on 10/30 and it came back online at 16:00 on 11/05 and again tripped offline at 08:00 on 11/09 and it came back online at 16:00 11/11 2. All trackers were not communicated from 09/10 to end of the month. | 1.SR107017 2.SR106841 | 1.Closed 2.Pending | SR106841
Willamina - Waterford - OR-23-C006 | OR | 126474.851 | 139589.9 | -13115.049 | -9.395% | 179467 | -52992.149 | -29.53% | 1.Site tripped offline from 10:45 to 12:00 on 11/20 and again offline from 11:00 to 13:15 on 11/21 due trchnician was on site to perform PM 2.The rating of all inverters are 122.14kW but they are limited to 85kW. Keeping track of this SR as work will not be completed by EPC until Q2 2026 | 1.SR111401 2.SR101124 | 1.Closed 2.Closed | SR101124
OR-23-C005 Solops SPI - Belvedere Solar | OR | 131827.561 | 128834.6 | 2992.961 | 2.323% | 167910 | -36082.439 | -21.49% | 1.Site was offline from 10:15 to 11:15 on 11/03 due technician was on site to perform PM | 1.PM17639 | 1.Completed
OR-23-C002 SPI - Cork Solar | OR | 84931.57 | 91220.83 | -6289.26 | -6.895% | 104075 | -19143.43 | -18.39% | 1.Site tripped offline from 09:15 to 10:00 on 11/14 | 1.PM 17633 | 1.Completed
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 92790.394 | 99303.63 | -6513.236 | -6.559% | 136515 | -43724.606 | -32.03% | 1.All inverters tripped offline at 10:15 on11/11 and came back online at 10:15 on 11/14 2.Inverter 11 starting late for the production most of the days throughout the month 3.Inverter 3 tripped offline at 10:15 on 11/11 and later back online at 10:15 on 10/14 | 1. SR110907 2.SR112336 3.SR108253 | 1.Denied 2.Pending 3.Pending | SR112336 | SR108253
OR: Dundee - Gun Club - OR-23-C009 | OR | 128064.754 | 131187.9 | -3123.146 | -2.381% | 159938.3 | -31873.546 | -19.93% | 1. Inverter 8 and 2 had heavy morning shading. 2.Inverter 14 tripped offline at 09:00 on 11/24 to end of the month | 2. SR111730 | 2.Denied
OR: Molalla - Marquam - OR-23-C010 | OR | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was offline at 13:30 on 10/25 and offline through the end of the month. | 1.SR110001 | 1.Denied

## Dec
Luminace |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 1533917.0303 | 2010075.507 | -476158.4767 | -23.69% | 2215872.87 | -681955.8397 | -30.78%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Raymond Ed Re-Development - DC-23-0001 | DC | 16667.5 | 27542.53 | -10875.03 | -39.48% | 22564.87 | -5897.37 | -26.14% | 1.Inverter 4 underperforming by 6kW since 09/10. 2.Site was offline from 10:45 to 11:15 on 12/30 while technician was on site. 3. Inverters have morning and evening shading | 1.SR107731 2.PM13109 | 1.Closed 2.Completed
Berkeley - NJ-22-C893 Berkeley I | NJ | 311262 | 251685.2 | 59576.8 | 23.67% | 362307.2 | -51045.2 | -14.09% | 1.Site tripped offline at 10:45 on 12/24 and it came back online at 08:45 on 12/31 2.Site tripped offline at 10:15 on 12/14 and it came back online on 12/15and again Site offline from 07:00 to 10:45 on 12/19 | 1. SR113590 2.SR112704 | 1.Closed 2.Closed | SR112704
Berkeley - NJ-22-C894 Berkeley II | NJ | 294806 | 335839.7 | -41033.7 | -12.22% | 367647 | -72841 | -19.81% | 1.Site tripped offline at 10:15 on 12/14 and it came back online on 12/16 2.Site tripped offline at 10:45 on 12/24 and it came back online at 10:00 on 12/31 3.Site tripped offline at 22:15 on 12/18 and it came back online at 10:15 on 12/19 | 1. SR112705 2.SR113587 3. SR113159 | 1.Closed 2.Closed 3.Closed | SR113587 | SR113159
BEMS Landfill East | NJ | 26547 | 354174.6 | -327627.6 | -92.5% | 315165.1 | -288618.1 | -91.58% | 1.Site back online at 15:15 12/01 2.Site was offline from 04:00 to 11:00 on 12/04 and again site was offline from 12/05 through the end of the month. | 1. SR111844 2. SR112315 | 1.closed | SR112315
Southampton - BEMS West NJ-22-C898 | NJ | 261442 | 355020.8 | -93578.8 | -26.36% | 321026 | -59584 | -18.56% | 1.Site was offline at 08:15 on 12/14 and it came back online at 09:30 on 12/17 2.Site tripped offline at 16:00 on 12/19 and back online at 13:45 on 12/22 | 1.SR112703 2.SR113259 | 1.closed 2.closed | SR113259
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 2147.5312 | 2774.617 | -627.0858 | -22.6% | 2170 | -22.4688 | -1.035% | 1. Site was offline from 12/14 to 12/16.
Lakewood Township - Public Works | NJ | 51917.125 | 75763.02 | -23845.895 | -31.47% | 26052 | 25865.125 | 99.28% | 1. Inverter 2-3 is underperforming approximately 6kW compared to its peers since 06/18. Quote expired 2. Inverter 2.2 and 2.3 should each have 10 strings connected per drawing. Based on production anomalies the PM photos were checked and inverter 2.2, derated to 55kW, has 11 strings connected while inverter 2.3, 60kW, only has 9. The extra string on the derated inverter results in production losses during high-irradiance months. On 12/10 technician relocated string to inverter, inverter producing as expected. 3.Site production was low on 12/02, 12/14,12/23 due to snow | 1. SR103097 2. SR110653 | 1.Closed 2.Closed | SR110653
Canby - Dover - OR-23-C003 | OR | 81744.917 | 82622.71 | -877.793 | -1.062% | 102026 | -20281.083 | -19.88% | 1.Tracker Motor 16.1 through 16.10 are stuck. Tracker motor 5.1 tracking normally from 12/17 | 1.SR110673 | 1.closed
Estacada - Clayfield - OR-23-C001 | OR | 72530.906 | 72229.46 | 301.446 | 0.4173% | 115248 | -42717.094 | -37.07% | 1.Site tripped offline at 09:30 on 12/14 and came back online at 09:00 on 12/15 2.Site tripped offline at 01:00 on 12/17 and it came back online at 10:00 on 12/24 | 1. SR112706 2. SR112951 | 1.Closed 2.Closed | SR112951
Willamina - Waterford - OR-23-C006 | OR | 86091.408 | 114323 | -28231.592 | -24.69% | 131199 | -45107.592 | -34.38% | 1.Site tripped offline from 12:45 to 15:30 on 12/17 and again site tripped offline at 14:15 on 12/18 it came back online at 15:45 on 12/22 | 1.SR112949 | 1.closed
OR-23-C005 Solops SPI - Belvedere Solar | OR | 102118.625 | 96420.65 | 5697.975 | 5.909% | 133496 | -31377.375 | -23.5% | 1. Tracker 25 stuck at -50 DEG for whole month | 1. SR110829 | 1. closed
OR-23-C002 SPI - Cork Solar | OR | 66810.012 | 76954.03 | -10144.018 | -13.18% | 84629 | -17818.988 | -21.06% | 1. Site has low production on 12/08, 12/09, 12/18.
OR: Oregon City - Buckner Creek - OR-23-C008 | OR | 69642.307 | 75068.39 | -5426.083 | -7.228% | 104116 | -34473.693 | -33.11% | 1.Inverter 11 starting late for the production most of the days throughout the month 2. Inverter 2 has been underperforming starting 12/10 with max production between 10-15kW and also tripped offline at 13:15 on 12/12 untill end of the month. 3.Site was offline at 01:30 on 12/17 and it came back online on 12/18 | 1.SR112336 2. SR112696 | 1.Denied 2.Denied | SR112696
OR: Dundee - Gun Club - OR-23-C009 | OR | 90189.699 | 89656.8 | 532.899 | 0.5944% | 128226.7 | -38037.001 | -29.66% | 1. Soiling station lost comms on 11/7; weather station lost comms on 12/12. 2.Inverter 14 tripped offline at 09:00 on 11/24 to end of the month | 1. SR113154 2. SR111730 | 1.Pending 2.Denied | SR111730
OR: Molalla - Marquam - OR-23-C010 | OR | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was offline at 13:30 on 10/25 and offline through the end of the month.

## Sites
Portfolio: | Luminace
Site DAS Name | Site | State | Update | DAS
DC-23-0001 - Raymond Elementary Redev | Raymond Ed Re-Development - DC-23-0001 | DC | AEF | PowerTrack
NJ-22-C893 - CS Energy - Berkeley I | Berkeley - NJ-22-C893 Berkeley I | NJ | AEF | PowerTrack
NJ-22-C894 - CS Energy - Berkeley II | Berkeley - NJ-22-C894 Berkeley II | NJ | AEF | PowerTrack
Southampton - BEMS East NJ-22-C897 | BEMS Landfill East | NJ |  | PowerTrack
NJ-22-C898 - BEMS Landfill West | Southampton - BEMS West NJ-22-C898 | NJ | AEF | PowerTrack
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ |  | PowerTrack
Lakewood Township - Public Works | Lakewood Township - Public Works | NJ |  | PowerTrack
OR-23-C003 Dover - SPI | Canby - Dover - OR-23-C003 | OR | AEF | PowerTrack
OR-23-C001 SPI - Clayfield Solar | Estacada - Clayfield - OR-23-C001 | OR | AEF | PowerTrack
SPI - Waterford Solar | Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR-23-C005 Solops SPI - Belvedere Solar | OR | AEF
Molalla - Cork - OR-23-C002 | OR-23-C002 SPI - Cork Solar | OR
OR-23-C008 Buckner Solar | OR: Oregon City - Buckner Creek - OR-23-C008 | OR |  | PowerTrack
OR-23-C009 Green Key Gun Club Solar | OR: Dundee - Gun Club - OR-23-C009 | OR |  | PowerTrack
OR-23-C010 Marquam Creek Solar | OR: Molalla - Marquam - OR-23-C010 | OR |  | PowerTrack