## Year to Date
Mira corp |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1391672.916 | 1467461.731 | -75788.815 | -5.165% | 1136350.589 | 255322.327 | 22.47%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Hartford Landfill - MIRA | CT | 1391672.916 | 1467461.731 | -75788.815 | -5.165% | 1136350.589 | 255322.327 | 22.47%

## 1st Qtr
Mira corp |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 292897 | 354994.716 | -62097.716 | -17.49% | 213718.908 | 79178.092 | 37.05%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Hartford Landfill - MIRA | CT | 292897 | 354994.716 | -62097.716 | -17.49% | 213718.908 | 79178.092 | 37.05%

## 2nd Qtr
Mira corp |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 403947 | 384553.216 | 19393.784 | 5.043% | 386340.141 | 17606.859 | 4.557%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Hartford Landfill - MIRA | CT | 403947 | 384553.216 | 19393.784 | 5.043% | 386340.141 | 17606.859 | 4.557%

## 3rd Qtr
Mira corp |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 449397 | 440115.299 | 9281.701 | 2.109% | 379346 | 70051 | 18.47%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Hartford Landfill - MIRA | CT | 449397 | 440115.299 | 9281.701 | 2.109% | 379346 | 70051 | 18.47%

## 4th Qtr
Mira corp |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 245431.916 | 287798.5 | -42366.584 | -14.72% | 156945.54 | 88486.376 | 56.38%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
CT: Hartford Landfill - MIRA | CT | 245431.916 | 287798.5 | -42366.584 | -14.72% | 156945.54 | 88486.376 | 56.38%

## Jan
Mira corp |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 90505 | 117865.95 | -27360.95 | -23.21% | 52040.246 | 38464.754 | 73.91%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 90505 | 117865.95 | -27360.95 | -23.21% | 52040.246 | 38464.754 | 73.91% | 1.The site went offline at 14:30 on 01/18 due to a utility outage and was restored at 09:15 on 01/19 after utility power was restored. 2.Site production low due to snow /weather | 1.SR095700

## Feb
Mira corp |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 62302 | 98706.619 | -36404.619 | -36.88% | 65916 | -3614 | -5.483%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 62302 | 98706.619 | -36404.619 | -36.88% | 65916 | -3614 | -5.483% | 1.The site went offline at 01:15 on 02/24 due to a utility outage and was restored at 12:30 on 02/26; it went offline again at 11:15 on 02/27 as Eversource took the solar offline due to a distribution line issue and was brought back online at 12:15 on 02/28 after the technician closed all three medium voltage line cutouts. | 1.SR097691, SR097895 | SR097895

## Mar
Mira corp |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 140090 | 138422.147 | 1667.853 | 1.205% | 95762.662 | 44327.338 | 46.29%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 140090 | 138422.147 | 1667.853 | 1.205% | 95762.662 | 44327.338 | 46.29%

## Apr
Mira corp |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 143095 | 136602.3 | 6492.7 | 4.753% | 115609.215 | 27485.785 | 23.77%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 143095 | 136602.3 | 6492.7 | 4.753% | 115609.215 | 27485.785 | 23.77%

## May
Mira corp |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 127566 | 118575.491 | 8990.509 | 7.582% | 132385.797 | -4819.797 | -3.641%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 127566 | 118575.491 | 8990.509 | 7.582% | 132385.797 | -4819.797 | -3.641%

## Jun
Mira corp |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 133286 | 129375.425 | 3910.575 | 3.023% | 138345.129 | -5059.129 | -3.657%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 133286 | 129375.425 | 3910.575 | 3.023% | 138345.129 | -5059.129 | -3.657% | 1.Site tripped offline and meter voltages dropped to 0 at 18:45 on 06/30 | 1.SR103801

## Jul
Mira corp |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 147281 | 144422.812 | 2858.188 | 1.979% | 146052 | 1229 | 0.8415%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 147281 | 144422.812 | 2858.188 | 1.979% | 146052 | 1229 | 0.8415% | 1.Site tripped offline and meter voltages dropped to 0 at 18:45 on 06/30 and was back online at 08:45 on 07/01. | 1.SR107183

## Aug
Mira corp |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 161031 | 157240.812 | 3790.188 | 2.41% | 131022 | 30009 | 22.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 161031 | 157240.812 | 3790.188 | 2.41% | 131022 | 30009 | 22.9% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.

## Sep
Mira corp |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 141085 | 138451.675 | 2633.325 | 1.902% | 102272 | 38813 | 37.95%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 141085 | 138451.675 | 2633.325 | 1.902% | 102272 | 38813 | 37.95% | 1. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance.

## Oct
Mira corp |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 119871 | 18652.7 | 101218.3 | 542.6% | 71927.7 | 47943.3 | 66.65%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
CT: Hartford Landfill - MIRA | CT | 119871 | 18652.7 | 101218.3 | 542.6% | 71927.7 | 47943.3 | 66.65% | 1. The weather station and all inverters stopped communicating with the DAS after the technician replaced the DAS equipment. The system was back online at 16:15 on 10/28. 2. Site was offline from 08:30 to 15:00 on 10/15/25 3. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance. 4. String Combiner boxes are reporting zero value in AlsoEnergy from 09/01/2024 | 1. SR107543 2. SR109532 | 1. Closed 2. Closed | SR109532

## Nov
Mira corp |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 61214 | 134396.5 | -73182.5 | -54.45% | 45014.61 | 16199.39 | 35.99%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
CT: Hartford Landfill - MIRA | CT | 61214 | 134396.5 | -73182.5 | -54.45% | 45014.61 | 16199.39 | 35.99% | 1. Inverter 1 having no communication, production can be confirmed at meter. 2. Meter is experiencing intermittent communication in the site but the energy is always backfilled 3. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance. Additionally compared to previous year the deviation has increased to 54% for the november month due to heavy snowfall this year or any combiner boxes might be offline resulting in lower production 4. String Combiner boxes are reporting zero value in AlsoEnergy from 09/01/2024 | 1. SR114168, SR112026, SR107543 2. SR110858 | 1. Open 2. Open | SR112026 | SR107543 | SR110858

## Dec
Mira corp |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 64346.916 | 134749.3 | -70402.384 | -52.25% | 40003.23 | 24343.686 | 60.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
CT: Hartford Landfill - MIRA | CT | 64346.916 | 134749.3 | -70402.384 | -52.25% | 40003.23 | 24343.686 | 60.85% | 1. Inverter 1 having no communication, production can be confirmed at meter. 2. Meter is experiencing intermittent communication in the site but the energy is always backfilled 3. The plant is performing as expected. The forecasted (theoretical) values may appear lower and they are based on long-term average weather data (typically over 10–15 years). In contrast, the actual vs. expected generation reflects real-time weather conditions during the period, offering a more accurate representation of current performance. Additionally compared to previous year the deviation has increased to 64 % for december month due to heavy snowfall this year or any combiner boxes might be offline resulting in lower production 4. String Combiner boxes are reporting zero value in AlsoEnergy from 09/01/2024 | 1. SR114168, SR112026, SR107543 2. SR110858 | 1. Open 2. Open | SR112026 | SR107543 | SR110858

## Sites
Portfolio: | Mira corp
Site DAS Name | Site | State | Update | DAS
Hartford Landfill | CT: Hartford Landfill - MIRA | CT | AEF | PowerTrack