## Year to Date
Troy School District |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 2376982.69 | 2839809.96 | -462827.27 | -16.3% | 0 | 2376982.69 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Joliet - Craughwell | IL | 397638.75 | 451767 | -54128.25 | -11.98% | 0 | 0
Joliet - Heritage Trail | IL | 258433.75 | 469982 | -211548.25 | -45.01% | 0 | 0
Plainfield - Troy | IL | 466391.19 | 501416 | -35024.81 | -6.985% | 0 | 0
Plainfield - William B Orenic | IL | 422243.75 | 464484 | -42240.25 | -9.094% | 0 | 0
Shorewood - Cronin | IL | 468311 | 509531.96 | -41220.96 | -8.09% | 0 | 0
Shorewood - Hofer | IL | 363964.25 | 442629 | -78664.75 | -17.77% | 0 | 0

## 1st Qtr
Troy School District |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 461942.57 | 577975.17 | -116032.6 | -20.08% | 0 | 461942.57 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Joliet - Craughwell | IL | 68519.5 | 88972 | -20452.5 | -22.99% | 0 | 0
Joliet - Heritage Trail | IL | 71279.5 | 94634 | -23354.5 | -24.68% | 0 | 0
Plainfield - Troy | IL | 84493.07 | 98759 | -14265.93 | -14.45% | 0 | 0
Plainfield - William B Orenic | IL | 76819 | 92662 | -15843 | -17.1% | 0 | 0
Shorewood - Cronin | IL | 84906.5 | 103007.17 | -18100.67 | -17.57% | 0 | 0
Shorewood - Hofer | IL | 75925 | 99941 | -24016 | -24.03% | 0 | 0

## 2nd Qtr
Troy School District |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 855465.43 | 932664.97 | -77199.54 | -8.277% | 0 | 855465.43 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Joliet - Craughwell | IL | 141319 | 147283 | -5964 | -4.049% | 0 | 0
Joliet - Heritage Trail | IL | 97156.25 | 150583 | -53426.75 | -35.48% | 0 | 0
Plainfield - Troy | IL | 160620.93 | 160175 | 445.93 | 0.2784% | 0 | 0
Plainfield - William B Orenic | IL | 144388.25 | 146249 | -1860.75 | -1.272% | 0 | 0
Shorewood - Cronin | IL | 163515.25 | 168960.97 | -5445.72 | -3.223% | 0 | 0
Shorewood - Hofer | IL | 148465.75 | 159414 | -10948.25 | -6.868% | 0 | 0

## 3rd Qtr
Troy School District |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 760331 | 883541 | -123210 | -13.95% | 0 | 760331 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Joliet - Craughwell | IL | 138137 | 147853 | -9716 | -6.571% | 0 | 0
Joliet - Heritage Trail | IL | 62628 | 152149 | -89521 | -58.84% | 0 | 0
Plainfield - Troy | IL | 157857 | 165667 | -7810 | -4.714% | 0 | 0
Plainfield - William B Orenic | IL | 147349 | 152800 | -5451 | -3.567% | 0 | 0
Shorewood - Cronin | IL | 161107 | 158787 | 2320 | 1.461% | 0 | 0
Shorewood - Hofer | IL | 93253 | 106285 | -13032 | -12.26% | 0 | 0

## 4th Qtr
Troy School District |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 299243.69 | 445628.82 | -146385.13 | -32.85% | 0 | 299243.69 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Joliet - Craughwell | IL | 49663.25 | 67659 | -17995.75 | -26.6% |  | 0
Joliet - Heritage Trail | IL | 27370 | 72616 | -45246 | -62.31% |  | 0
Plainfield - Troy | IL | 63420.19 | 76815 | -13394.81 | -17.44% |  | 0
Plainfield - William B Orenic | IL | 53687.5 | 72773 | -19085.5 | -26.23% |  | 0
Shorewood - Cronin | IL | 58782.25 | 78776.82 | -19994.57 | -25.38% |  | 0
Shorewood - Hofer | IL | 46320.5 | 76989 | -30668.5 | -39.83% |  | 0

## Jan
Troy School District |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 89649 | 160957 | -71308 | -44.3% | 0 | 89649 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 12686 | 24570 | -11884 | -48.37% | N/A |  |  | 1. Low generation due to snow/rain
Joliet - Heritage Trail | IL | 13469 | 26110 | -12641 | -48.41% | N/A |  |  | 1. Low generation due to snow/rain
Plainfield - Troy | IL | 16785 | 27888 | -11103 | -39.81% | N/A |  |  | 1. Low generation due to snow/rain
Plainfield - William B Orenic | IL | 15189 | 26078 | -10889 | -41.76% | N/A |  |  | 1. Inverters 2, 3, 4, and 5 were tripped offline at 8:30 AM on 01/30/25 due to a permanent static GFCI fault (16) and issue self-resolved on 01/31/25. | 1. SR096152
Shorewood - Cronin | IL | 16823 | 28100 | -11277 | -40.13% | N/A |  |  | 1. Low generation due to snow/rain
Shorewood - Hofer | IL | 14697 | 28211 | -13514 | -47.9% | N/A |  |  | 1. Low generation due to snow/rain

## Feb
Troy School District |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 146034.66 | 176372 | -30337.34 | -17.2% | 0 | 146034.66 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 21859 | 27097 | -5238 | -19.33% | N/A |  |  | 1. Low generation due to snow/rain
Joliet - Heritage Trail | IL | 22097 | 28467 | -6370 | -22.38% | N/A |  |  | 1. Low generation due to snow/rain
Plainfield - Troy | IL | 27054.16 | 30214 | -3159.84 | -10.46% | N/A |  |  | 1. Low generation due to snow/rain
Plainfield - William B Orenic | IL | 24770.5 | 28297 | -3526.5 | -12.46% | N/A |  |  | 1.Inverters 2, 3, 4, and 5 were tripped offline at 9:30 AM on 02/06 due to a permanent static GFCI fault (16) and self-resolved on 02/07. Inverters 3, 4, and 5 tripped offline again at 1:15 PM on 02/08 and were later resolved on 02/09. Upon the technician's arrival on 02/11, the parameters were adjusted, and the inverters were brought back online. | 1. SR096152
Shorewood - Cronin | IL | 26290 | 31465 | -5175 | -16.45% | N/A |  |  | 1. Low generation due to snow/rain
Shorewood - Hofer | IL | 23964 | 30832 | -6868 | -22.28% | N/A |  |  | 1. Low generation due to snow/rain

## Mar
Troy School District |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 226258.91 | 240646.17 | -14387.26 | -5.979% | 0 | 226258.91 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 33974.5 | 37305 | -3330.5 | -8.928% | N/A
Joliet - Heritage Trail | IL | 35713.5 | 40057 | -4343.5 | -10.84% | N/A
Plainfield - Troy | IL | 40653.91 | 40657 | -3.09 | -0.0076% | N/A
Plainfield - William B Orenic | IL | 36859.5 | 38287 | -1427.5 | -3.728% | N/A
Shorewood - Cronin | IL | 41793.5 | 43442.17 | -1648.67 | -3.795% | N/A
Shorewood - Hofer | IL | 37264 | 40898 | -3634 | -8.886% | N/A

## Apr
Troy School District |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 247995.25 | 256315.15 | -8319.9 | -3.246% | 0 | 247995.25 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 38951.5 | 40309 | -1357.5 | -3.368% | N/A
Joliet - Heritage Trail | IL | 37505.5 | 41708 | -4202.5 | -10.08% | N/A |  |  | 1. Inverter 1 is offline and reporting permanent fault bus high failure and bus voltage difference is high on 04/23 and later it is back online at 9:30 on 04/24. Again inverter 1 is offline on 04/25 and reporting permanent fault bus high failure and bus voltage difference is high and it is being RMA'd 2. Inverter 2.1 was offline on 04/09 and back online on 04/10. | 1. SR100203, SR100411 2. SR099608 | SR100411 | SR099608
Plainfield - Troy | IL | 44348.5 | 43667 | 681.5 | 1.561% | N/A |  |  | 1. Technician has confirmed that the pyranometer is experiencing the shading in the afternoon | 1.SR099771
Plainfield - William B Orenic | IL | 40008.5 | 40237 | -228.5 | -0.5679% | N/A
Shorewood - Cronin | IL | 45821.5 | 46545.15 | -723.65 | -1.555% | N/A
Shorewood - Hofer | IL | 41359.75 | 43849 | -2489.25 | -5.677% | N/A |  |  | 1. Inverter 7 didn't started for production on 04/05 and back online on 04/07 and again offline on 04/08 and back online at 11:15 on 04/08. | 1.SR099449

## May
Troy School District |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 304617.31 | 326914.39 | -22297.08 | -6.82% | 0 | 304617.31 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 49559 | 51606 | -2047 | -3.967% | N/A
Joliet - Heritage Trail | IL | 39379.75 | 53287 | -13907.25 | -26.1% | N/A |  |  | 1. Inverter 1 was offline for whole month and being RMA | 1. SR100411
Plainfield - Troy | IL | 56123.56 | 56003 | 120.56 | 0.2153% | N/A |  |  | 1. Technician has confirmed that the pyranometer is experiencing the shading in the afternoon | 1.SR099771
Plainfield - William B Orenic | IL | 50439.75 | 51104 | -664.25 | -1.3% | N/A
Shorewood - Cronin | IL | 56877.5 | 58996.39 | -2118.89 | -3.592% | N/A |  |  | 1. Meter is not capturing all inverter's total power. Reached out to the DAS provider and waiting for the response from the ASG team | 1. SR101081
Shorewood - Hofer | IL | 52237.75 | 55918 | -3680.25 | -6.582% | N/A |  |  | 1. Inverter 7 did not start for production on 05/04 and reporting Bus high failure fault and back online on 05/05. Again inverter 7 didn't started for production on 05/28 and back online on 05/30. | 1. SR100984

## Jun
Troy School District |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 302852.87 | 349435.43 | -46582.56 | -13.33% | 0 | 302852.87 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 52808.5 | 55368 | -2559.5 | -4.623% | N/A
Joliet - Heritage Trail | IL | 20271 | 55588 | -35317 | -63.53% | N/A |  |  | 1. Inverters 2.1, and 2.2 are offline at 13:00 on 06/05 and continued through out the month. Inverter 3.1 is also offline at 8:15 on 06/06 and continued through out the month. Client holded for dispatch due to ongoing maintenance by school. | 1. SR102543
Plainfield - Troy | IL | 60148.87 | 60505 | -356.13 | -0.5886% | N/A |  |  | 1. Technician has confirmed that the pyranometer is experiencing the shading in the afternoon | 1.SR099771
Plainfield - William B Orenic | IL | 53940 | 54908 | -968 | -1.763% | N/A
Shorewood - Cronin | IL | 60816.25 | 63419.43 | -2603.18 | -4.105% | N/A |  |  | 1. Meter is not capturing all inverter's total power. Reached out to the DAS provider and waiting for the response from the ASG team | 1. SR101081
Shorewood - Hofer | IL | 54868.25 | 59647 | -4778.75 | -8.012% | N/A |  |  | 1. Inverter 7 offline on 06/06 and back online on 06/07 and again offline on 06/13 and back online on 06/15 and inverter is being RMA'd | 1. SR100984

## Jul
Troy School District |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 278081 | 315516 | -37435 | -11.86% | 0 | 278081 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 47348 | 49498 | -2150 | -4.344% | N/A |  |  | 1. Inverter 2.1 is derated to 20kW on 07/05 and reporting "Fan fault" and occured multiple day in a month. | 1. SR104047
Joliet - Heritage Trail | IL | 15120 | 51975 | -36855 | -70.91% | N/A |  |  | 1. Inverter 1 is offline since 04/25/25 and reporting "permanent fault bus high failure and bus voltage difference is high" and inverter is under RMA'd. 2. Inverters 2.1, and 2.2 are offline at 13:00 on 06/05 and continued through out the month. Inverter 3.1 is also offline at 8:15 on 06/06 and continued through out the month. Client holded for dispatch due to ongoing maintenance by school. | 1. SR100203, SR100411 2. SR102543 | SR100411 | SR102543
Plainfield - Troy | IL | 56226 | 56615 | -389 | -0.6871% | N/A |  |  | 1. Technician has confirmed that the pyranometer is experiencing the shading in the afternoon | 1.SR099771
Plainfield - William B Orenic | IL | 50455 | 51963 | -1508 | -2.902% | N/A
Shorewood - Cronin | IL | 56116 | 49498 | 6618 | 13.37% | N/A |  |  | 1. Meter is not capturing all inverter's total power. Reached out to the DAS provider and waiting for the response from the AASG team. | 1. SR101081, SR106362 | SR106362
Shorewood - Hofer | IL | 52816 | 55967 | -3151 | -5.63% | N/A |  |  | 1. Inverter 7 is being RMA'd. on 08/01 technician replaced powerhead for the inverter and inverter is back online and producing as expected. | 1. SR100984

## Aug
Troy School District |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 291459 | 327713 | -36254 | -11.06% | 0 | 291459 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 48543 | 52664 | -4121 | -7.825% | N/A |  |  | 1.1. Inverter 2.1 was underperforming since 07/05 and issue was resolved on 08/16. | 1.SR104047
Joliet - Heritage Trail | IL | 25108 | 53344 | -28236 | -52.93% | N/A |  |  | 1.Inverter 1 derating at 42KW since 12:15 on 08/02 reporting " external fan alarm" and inverter was RMA'd on 08/13. Inverters 2.1, and 2.2 are offline at 13:00 on 06/05 and continued through out the month. Inverter 3.1 is also offline at 8:15 on 06/06 and continued through out the month. | 1.SR105562 2.SR102543 | SR102543
Plainfield - Troy | IL | 56070 | 58872 | -2802 | -4.759% | N/A
Plainfield - William B Orenic | IL | 51725 | 54019 | -2294 | -4.247% | N/A |  |  | 1.Inverter 3 was offline on 08/12 reporting "permanent fault bus high failure" and was back online on 08/13 and was gain offline on 08/19 reporting "permanent fault bus high failure" and was back online on 08/20 .Self resolved. | 1.SR106075
Shorewood - Cronin | IL | 55200 | 52664 | 2536 | 4.815% | N/A |  |  | 1. Meter is not capturing all inverter's total power. Reached out to the DAS provider and waiting for the response from the AASG team. | 1.SR106362 2.SR108081 | SR108081
Shorewood - Hofer | IL | 54813 | 56150 | -1337 | -2.381% | N/A

## Sep
Troy School District |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 245991 | 292976 | -46985 | -16.04% | 0 | 245991 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Joliet - Craughwell | IL | 42246 | 45691 | -3445 | -7.54% | N/A
Joliet - Heritage Trail | IL | 22400 | 46830 | -24430 | -52.17% | N/A |  |  | 1. Inverters 2.1, and 2.2 are offline at 13:00 on 06/05 and continued through out the month. Inverter 3.1 is also offline at 8:15 on 06/06 and continued through out the month. | 1. SR102543
Plainfield - Troy | IL | 45561 | 50180 | -4619 | -9.205% | N/A |  |  | 1. Few modules were offline for whole month. | 1. SR106730
Plainfield - William B Orenic | IL | 45169 | 46818 | -1649 | -3.522% | N/A
Shorewood - Cronin | IL | 50178 | 53139 | -2961 | -5.572% | N/A |  |  | 1. Meter is not capturing all inverter's total power. Reached out to the DAS provider and waiting for the response from the AASG team. | 1.SR106362 2.SR108081 | SR108081
Shorewood - Hofer | IL | 40437 | 50318 | -9881 | -19.64% | N/A |  |  | 1. Inverter 2 was offline from 07:45 on 09/10 to end of the month. | 1. SR107779

## Oct
Troy School District |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 166251.69 | 209501.82 | -43250.13 | -20.64% | 0 | 166251.69 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Joliet - Craughwell | IL | 28268.25 | 32291 | -4022.75 | -12.46% | N/A |  |  | 1. Inverter 2.1 was derated 20kW for whole month. | 1. SR104047 | 1. Pending
Joliet - Heritage Trail | IL | 15130 | 33764 | -18634 | -55.19% | N/A |  |  | 1. Inverters 1, 2.1, 2.2, 3.1 were offline for whole month | 1. SR102543 | 1. Pending
Plainfield - Troy | IL | 35035.19 | 36017 | -981.81 | -2.726% | N/A
Plainfield - William B Orenic | IL | 31647.5 | 33883 | -2235.5 | -6.598% | N/A
Shorewood - Cronin | IL | 31167.25 | 37559.82 | -6392.57 | -17.02% | N/A |  |  | 1. Meter is not capturing all inverter's total power. Reached out to the DAS provider and waiting for the response from the AASG team. | 1.SR106362 | 1. closed
Shorewood - Hofer | IL | 25003.5 | 35987 | -10983.5 | -30.52% | N/A |  |  | 1. Inverter 2 was offline from 07:45 on 09/10 to end of the month. | 1. SR107779 | 1. closed

## Nov
Troy School District |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 100585 | 136286 | -35701 | -26.2% | 0 | 100585 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Joliet - Craughwell | IL | 16378 | 20618 | -4240 | -20.56% | N/A |  |  | 1. Inverter 2.1 was derated 20kW for whole month. | 1. SR104047 | 1. Pending
Joliet - Heritage Trail | IL | 9253 | 22221 | -12968 | -58.36% | N/A |  |  | 1. Inverters 1, 2.1, 2.2, 3.1 were offline for whole month | 1. SR102543 | 1. Pending
Plainfield - Troy | IL | 20962 | 23457 | -2495 | -10.64% | N/A |  |  | 1.Site produtcion was low on 11/18, 11/19,11/20 due to snow
Plainfield - William B Orenic | IL | 17821 | 22274 | -4453 | -19.99% | N/A |  |  | 1. inverter 3 was offline on 11/12, 11/15, 11/25 11/26. 11/30. 2. Inverter 2 was offline from 11/26 to end of the month. | 1. SR111704 2. SR111704, SR111347 | 1. Pending 2. Pending | SR111347
Shorewood - Cronin | IL | 21129 | 24079 | -2950 | -12.25% | N/A |  |  | 1. Meter is not capturing all inverter's total power. Reached out to the DAS provider and waiting for the response from the AASG team. | 1.SR106362 | 1. closed
Shorewood - Hofer | IL | 15042 | 23637 | -8595 | -36.36% | N/A |  |  | 1. Inverter 2 was offline from 07:45 on 09/10 to 11/24 at 11:30 | 1. SR107779 | 1. closed

## Dec
Troy School District |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 32407 | 99841 | -67434 | -67.54% | 0 | 32407 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Joliet - Craughwell | IL | 5017 | 14750 | -9733 | -65.99% | N/A |  |  | 1. Inverter 2.1 was derated 20kW for whole month. 2. Site was barely producing from 12/01 to 12/10, 12/18, 12/25 to 12/27, 12/30 due to snow. | 1. SR104047 | 1. Pending
Joliet - Heritage Trail | IL | 2987 | 16631 | -13644 | -82.04% | N/A |  |  | 1. Inverters 1, 2.1, 2.2, 3.1 were offline for whole month and on 12/09 tech replaced the fan on inverter 1 ad the inverter 1 was back online. 2. Site was barely producing from 12/01 to 12/10, 12/18, 12/25 to 12/27, 12/30 due to snow. | 1. SR102543, SR105562 | 1. Pending
Plainfield - Troy | IL | 7423 | 17341 | -9918 | -57.19% | N/A |  |  | 1. Site was barely producing from 12/01 to 12/10, 12/18, 12/25 to 12/27, 12/30 due to snow.
Plainfield - William B Orenic | IL | 4219 | 16616 | -12397 | -74.61% | N/A |  |  | 1. Inverters 2 and 3 were being RMA'd. | 1. SR111780 | 1. Pending
Shorewood - Cronin | IL | 6486 | 17138 | -10652 | -62.15% | N/A |  |  | 1. Site was offlie from 10:45 on 12/17 to 07:00 on 12/18. 2. Meter didn't captured the full inverter production from 12/01 to 07:00 on 12/18 | 1. SR113053 2. SR106362 | 1. closed 2. Closed
Shorewood - Hofer | IL | 6275 | 17365 | -11090 | -63.86% | N/A |  |  | 1. Site was barely producing from 12/01 to 12/10, 12/18, 12/25 to 12/27, 12/30 due to snow.

## Sites
Portfolio: | Troy School District
Site DAS Name | Site | State | Update | DAS
IL: Joliet - Craughwell ES | Joliet - Craughwell | IL |  | AssetPlanner
IL: Joliet - Heritage Trail | Joliet - Heritage Trail | IL |  | AssetPlanner
IL: Plainfield - Troy MS | Plainfield - Troy | IL |  | AssetPlanner
IL: Plainfield - William B Orenic IS | Plainfield - William B Orenic | IL |  | AssetPlanner
IL: Shorewood - Cronin ES | Shorewood - Cronin | IL |  | AssetPlanner
IL: Shorewood - Hofer ES | Shorewood - Hofer | IL |  | AssetPlanner