## Year to Date
True Green Capital Management LLC |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 41717311.2182 | 35727215.1441 | 5990096.0741 | 16.77% | 46589857.27 | -4872546.0518 | -10.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 18432546.015 | 19121165.87 | -688619.855 | -3.601% | 20728442.47 | 1045142.545 | 5.042%
Warsaw - Hemings | VA | 9889152.6 | 7009194.43 | 2879958.17 | 41.09% | 10404623.64 | 765879.96 | 7.361%
Mount Jackson - Randolf | VA | 6031534.5032 | 6126107.936 | -94573.4328 | -1.544% | 7163543.86 | -2343.1568 | -0.03271%
Callands Gretna - Monroe | VA | 4661035 | 3319758.406 | 1341276.594 | 40.4% | 4782321.7 | 402502.9 | 8.416%
Rockbridge Baths - Small Mouth Bass | VA | 2703043.1 | 150988.5021 | 2552054.5979 | 1690% | 3510925.6 | -199341 | -5.678%

## 1st Qtr
True Green Capital Management LLC |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 7849609.1976 | 7880724.59 | -31115.3924 | -0.3948% | 8287872.8 | -438263.6024 | -5.288%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 3600100 | 3879318.6 | -279218.6 | -7.198% | 3751976.6 | -151876.6 | -4.048%
Warsaw - Hemings | VA | 2066881.6 | 2273767 | -206885.4 | -9.099% | 2102775 | -35893.4 | -1.707%
Mount Jackson - Randolf | VA | 1190682.5976 | 1219182.5 | -28499.9024 | -2.338% | 1427826.5 | -237143.9024 | -16.61%
Callands Gretna - Monroe | VA | 991945 | 508456.49 | 483488.51 | 95.09% | 1005294.7 | -13349.7 | -1.328%
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
True Green Capital Management LLC |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 12798493.3056 | 10929618.5 | 1868874.8056 | 17.1% | 15450717.3 | -2652223.9944 | -17.17%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 5967940 | 6302907 | -334967 | -5.314% | 7143808 | 2165171 | 30.31%
Warsaw - Hemings | VA | 3089302.7 | 2273458.8 | 815843.9 | 35.89% | 3418110 | 952543.7 | 27.87%
Mount Jackson - Randolf | VA | 1591041.6056 | 1704180.4 | -113138.7944 | -6.639% | 2280381.1 | 440326.7056 | 19.31%
Callands Gretna - Monroe | VA | 1442040 | 649072.3 | 792967.7 | 122.2% | 1515983.2 | 449846.4 | 29.67%
Rockbridge Baths - Small Mouth Bass | VA | 708169 | 0 | 708169 |  | 1092435 | 224275.5 | 20.53%

## 3rd Qtr
True Green Capital Management LLC |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 13413442.6 | 10001469.952 | 3411972.648 | 34.11% | 15281198.97 | -1867756.37 | -12.22%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 6128755 | 6210126.77 | -81371.77 | -1.31% | 7003669.07 | -874914.07 | -12.49%
Warsaw - Hemings | VA | 2771456.2 | 502250.43 | 2269205.77 | 451.8% | 3132778.64 | -361322.44 | -11.53%
Mount Jackson - Randolf | VA | 1949285.5 | 1956086.336 | -6800.836 | -0.3477% | 2220095.26 | -270809.76 | -12.2%
Callands Gretna - Monroe | VA | 1389163 | 1333006.416 | 56156.584 | 4.213% | 1394645.4 | -5482.4 | -0.3931%
Rockbridge Baths - Small Mouth Bass | VA | 1174782.9 | 0 | 1174782.9 |  | 1530010.6 | -355227.7 | -23.22%

## 4th Qtr
True Green Capital Management LLC |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 7655766.115 | 6915402.1021 | 740364.0129 | 10.71% | 7570068.2 | 85697.915 | 1.132%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 2735751.015 | 2728813.5 | 6937.515 | 0.2542% | 2828988.8 | -93237.785 | -3.296%
Warsaw - Hemings | VA | 1961512.1 | 1959718.2 | 1793.9 | 0.09154% | 1750960 | 210552.1 | 12.02%
Mount Jackson - Randolf | VA | 1300524.8 | 1246658.7 | 53866.1 | 4.321% | 1235241 | 65283.8 | 5.285%
Callands Gretna - Monroe | VA | 837887 | 829223.2 | 8663.8 | 1.045% | 866398.4 | -28511.4 | -3.291%
Rockbridge Baths - Small Mouth Bass | VA | 820091.2 | 150988.5021 | 669102.6979 | 443.1% | 888480 | -68388.8 | -7.697%

## Jan
True Green Capital Management LLC |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1608150.4032 | 1762398 | -154247.5968 | -8.752% | 2081938.1 | -473787.6968 | -22.76%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 748299 | 805370.6 | -57071.6 | -7.086% | 885341.6 | -137042.6 | -15.48% | 1. Inverter 57 was offline throughout the month due to fault permanent power module failure. 2. Inverters 29, 30, 32, 64, 68, 69, 78, and 80 are offline due to a hunt. The LOTO has been applied to the inverters, and all trackers are stuck. | 1. SR094033 2. SR095849
Warsaw - Hemings | VA | 479142.2 | 554593.9 | -75451.7 | -13.6% | 548915 | -69772.8 | -12.71% | 1. Trackers group A to J are currently in wind stow status for whole month. | 1. SR096181
Mount Jackson - Randolf | VA | 127473.2032 | 147694.2 | -20220.9968 | -13.69% | 364481.5 | -237008.2968 | -65.03% | 1. Site tripped offline on 12/30 due to a squirrel climbing the utility pole and shorting the phase B fuse after installing cut out fuse on 01/21 the site was back online at 11:00am on 01/21. 2. Site was tripped offline at 14:15 on 01/29 due to inverter voltages was dropped & reported "Grid Phase Voltage Out of Range" and site was back online at 16:20 on 01/21. 3. Inverter 23 is underproducing due to FTC tracker - network control unit 2: tracker motor 7 is not tracking. | 1. SR095130 2. SR096122 3. SR096074
Callands Gretna - Monroe | VA | 253236 | 254739.3 | -1503.3 | -0.5901% | 283200 | -29964 | -10.58% | 1.Trackers D28, A27, and C26 are stuck for whole month due to defective batteries. | 1. SR091277
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month due to bad modem. | 1. SR094062

## Feb
True Green Capital Management LLC |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2408512.6 | 2367744.39 | 40768.21 | 1.722% | 2545793.2 | -137280.6 | -5.392%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 1053549 | 1144122 | -90573 | -7.916% | 1113658 | -60109 | -5.397% | 1. Inverter 2 tripped offline at 09:04 AM on 02/06/25, reporting a Permanent fault of power module. On 02/07/25, the technician reset the inverter, but the same fault occurred. Chint confirmed a power head failure, and a ticket was issued for replacement. On 02/27/25, the technician replaced the malfunctioning inverter with a new one brought back online at 10:15AM the same day. 2. Inverter 57 back online at 11:45AM on 02/07/25 after technician replaced old powerhead with new. 3.Inverter 9 tripped offline at 09:30 AM on 02/18/25 due to a permanent power module failure. Parts are required to bring it back online, and it remained offline throughout the month 4. Inverter 65 is derated by 50 kW due to an external fan error on 02/21, 02/22. On 02/24/25, a technician found no faults, compared output with nearby inverters (which were similar), and confirmed with Chint that no issues were detected. 5. Inverter 42 was derated by approximately 54 kW compared to its peers due to an external fan error on 02/21 to 02/23. On 02/24/25, a technician discovered a string wrapped around the fans, removed the old pull from the unit, and brought it to the expected production level the same day. 6. Inverter 60 was derating by approximately 50 kW due to an external fan fault issue from 02/27/25. 7. Inverters 29, 30, 64, 68, 69, 78,79 and 80 are offline and confirmed with Hunt these inverters are LOTOd. Additionally all trackers were struck. | 1.SR096391 2. SR094033 3. SR097304 4. SR097622 5. SR097663 6. SR097884 7. SR095849, SR083529, SR085269
Warsaw - Hemings | VA | 638142.1 | 701308.1 | -63166 | -9.007% | 663175 | -25032.9 | -3.775% | 1. Inverter 21 was derating by 50kW from 02/24 due to External Fan fault. 2. Trackers A to J have been stuck since 01/31/25. On 02/04/25, a technician found 56 stuck trackers across the site. On 02/13/25, the technician removed the fuse and power-cycled each tracker, restoring tracking on most of the site. However, 22 trackers remained stuck, and a ticket was submitted to meet with Soltec technicians to diagnose the recurring communication issue. On 02/18/25, the technician found some trackers were not communicating with RSUs. After installing a new tracker, 12 trackers still required additional troubleshooting. | 1. SR097728 2. SR096181
Mount Jackson - Randolf | VA | 437522.5 | 422842.5 | 14680 | 3.472% | 449760.2 | -12237.7 | -2.721% | 1. Inverter 23 is underproducing due to FTC tracker - network control unit 2 and tracker motor 7 are not tracking. On 02/03/25, the technician found 3 trackers stuck and power-cycled them. After 30 minutes, they resumed tracking, but tracker motor 7 requires additional troubleshooting. On 02/19/25, the technician confirmed with steven and RMA'd the motor. 2. Trackers 8, 10, 45, and 46 have been stuck since 02/16/25. On 02/19/25, the technician found them in the stow position due to defective batteries, requiring additional troubleshooting. By 02/27/25, motors 8 and 45 self-resolved, while 10 and 46 remain stuck. | 1. SR096074, SR096778 2. SR097433, SR097757
Callands Gretna - Monroe | VA | 279299 | 99471.79 | 179827.21 | 180.8% | 319200 | -39901 | -12.5% | 1.The Hukseflux SR15-D1 - POA is missing communication since 02/14/25. GHI, double mod, and BPOA are currently communicating. 2. Trackers D28, A27, and C26 are stuck for whole month due to defective batteries. 3. Multiple tracker motors have been stuck since 02/11/25 due to snow | 1. SR097908 2. SR091277 3. SR096700
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month due to bad modem. | 1. SR094062

## Mar
True Green Capital Management LLC |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3832946.1944 | 3750582.2 | 82363.9944 | 2.196% | 3660141.5 | 172804.6944 | 4.721%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 1798252 | 1929826 | -131574 | -6.818% | 1752977 | 45275 | 2.583% | 1.Inverter 13 has been underproducing by approximately 30 kW compared to its peers since the MC4 connectors were replaced in early December 2024 to resolve ongoing tripping issues. On 03/11, technician replaced 3 fuses with no continuity and inverter started producing inline with peers. 2.Inverter 28 tripped offline at 12:15PM on 03/31 due to permanent fault of power module - Fault0010 and Power Module Protection - Protect0120. 3.Strings down on inverters 29 and 30 from 03/17. 4.Inverter 66 tripped offline at 16:15 on 03/31 due to AC SPD Fault. 5.Inverter 64 was offline from 12/18/24 which was LOTO'd. 6.Inverters 29, 30, 64, 68, 69, 78,79 and 80 are offline from 12/26/24 and confirmed with Hunt these inverters are LOTOd and back online at 12:15PM on 03/17. 7.Soltec Tracker Full T01: Motors 22, 77, 138 were stuck. Soltec Tracker Full T02: Motors 4, 21, 23, 32, 37, 58, 61, 83 were stuck. Soltec Tracker Full T03: Motors 13, 52 were stuck. Soltec Tracker Full T04: Motors 1, 11, 27, 28, 29, 32, 39, 51, 57, 65, 75, 88, 94, 112, 113 were stuck. 8.Inverter 9 was offline from 02/18 due to Bus (sum) Over Voltage fault and inverter power head was being RMA'D from 02/24. On 03/07, the technician replaced the RMA'd inverter power head with a new unit, and the inverter is now operating in line with peer inverters. 9.Inverter 60 was derating by approximately 50 kW due to an external fan fault issue from 02/27/25 and producing normal after technician replaced RMA'D fan with new fan on 03/10. | 1.SR098364 2.SR099220 3.SR099222 4.SR099295 5.SR099221 6.SR095849 7.SR099224 8.SR097304 9.SR097884 | SR099220 | SR099222 | SR099295 | SR099221 | SR095849 | SR099224
Warsaw - Hemings | VA | 949597.3 | 1017865 | -68267.7 | -6.707% | 890685 | 58912.3 | 6.614% | 1.Inverter 21 was derating approximately by 50KW due to external fan fault on high irradiance days. Additionally 5 trackers were stuck. 2.12 trackers were stuck from 02/18. On 03/10 technician checked in and worked with erika and brought back 5 trackers back online and 4 trackers were still truck. One new tracker has no lights good fuse and module is only putting out 30 V. Will need a new module. | 1.SR097728,SR098569, SR096181 & SR098568. | SR098569 | SR096181 | SR098568
Mount Jackson - Randolf | VA | 625686.8944 | 648645.8 | -22958.9056 | -3.54% | 613584.8 | 12102.0944 | 1.972% | 1. Inverter 15 tripped offline at 13:30 on 03/08 due to Inverter Over Current and self resolved and back online on 03/09. Inverter 15 tripped offline at 14:30 on 03/11 due to Inverter Over Current and self-resolved and back online on 03/12. 2.Inverter 18 tripped offline at 12:15PM on 03/22 due to Inverter Over Current - ProtectOO30 and self resolved and back online on 03/23. On 03/26, technician performed firmware upgrade for inverter. Inverter 18 tripped offline at 11:45AM on 03/01 due to Inverter Over Current and self resolved and back online on 03/02 3.All inverters tripped offline from 13:15 on 03/29 due to Grid Phase Voltage Out of Range - GridV.OutLim fault additionally meter stopped communicating. 4.NCU 1 motors 10 and 46 were stuck. On 03/17, the technician ran several reset commands via the Mission Control dashboard—motor 10 resumed tracking, while motor 46 remained stuck and requires motor replacement. 5.NCU 2 motor 7 was stuck and motor was being RMA'd 6.Site tripped tripped offline on 03/16 at 14:15, and later back online on 03/17 (We started monitoring these sites again from 03/21 as per the information provided. Due to this we dont have any SR's for this issue.). 7.Inverter 7 tripped offline at 15:15 on 03/17 and back online on 03/18. (We started monitoring these sites again from 03/21 as per the information provided.Due to this we dont have any SR's for this issue.). | 1.SR098302 2.SR098925, SR097945 3.SR099141 4.SR097757 5.SR098566 | SR098925 | SR099141 | SR097757 | SR098566
Callands Gretna - Monroe | VA | 459410 | 154245.4 | 305164.6 | 197.8% | 402894.7 | 56515.3 | 14.03% | 1.Hukseflux SR15-D1-POA & Huskseflux SR15-D1-BPOA stopped communicating from 03/16/25. Huskseflux SR15-D1-BPOA has resumed communication on 03/29. The Hukseflux SR15-D1 - POA is missing communication since 02/14/25 and resumed communication at 16:00 on 03/03 2.Trackers D28, A27, and C26 have been stuck all month due to bad batteries. On March 3, tech installed 2 new batteries, but 5 trackers remain stuck—3 not yet added, 2 showing low voltage. HMI login failed due to system error. 3.Multiple tracker motors have been stuck since 02/11/25. Shared SPS info with Soltec; awaiting response. Unable to access Soltec internal HMI onsite due to server connection issue. | 1.SR099420, SR097908 2.SR091277 3.SR096700
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month due to bad modem. | 1.SR097305 & SR098700 | SR098700

## Apr
True Green Capital Management LLC |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 3804632.0056 | 3568997.8 | 235634.2056 | 6.602% | 4304859.3 | -500227.2944 | -11.62%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 1778353 | 1925780 | -147427 | -7.655% | 2098765 | -320412 | -15.27% | 1.Inverter 28 tripped offline at 12:15 on 03/31 due to a permanent power module fault (Fault0010) and Power Module Protection error (Protect0120). The technician initiated an RMA for the powerhead on 04/07 and replaced it with a new unit on 04/24. The inverter is back online and producing in line with its peers. 2.Inverter 64 was offline from 12/18/24 which was LOTO'd. 3.Inverters 29 and 30 have strings down due to missing panels caused by storm damage. 4.Inverter 66 tripped offline at 16:15 on 03/31 due to an AC SPD fault. The technician RMA’d the powerhead on 04/07 and replaced it with a new one on 04/11. The inverter is now back online and producing normally. 5.Inverter 50 tripped offline at 09:45 on 04/12 due to Permanent fault of power module - Fault0010 Power Module Protection - Protect0120 fault. On 04/14 technician RMA'D powerhead of the inverter and on 04/24 technician replaced with new powerhead and inverter started for production according to peers. 6.Inverter 36 tripped offline at 14:15 on 04/15 due to Bus (sum) Over Voltage (firmware) - Protect0090. On 04/24, Technicians responded to a permanent power failure. Chint was contacted for an RMA, and the inverter was replaced using a spare from inventory. The unit has been commissioned and is now producing power. 7.Inverter 42 was tripped offline at 16:30 on 04/16 due to Bus Imbalance - Protect0070 fault. On 04/24, Technicians responded to a permanent power failure. Chint was contacted for an RMA, and the inverter was replaced using a spare from inventory. The unit has been commissioned and is now producing power. 8.Soltec Tracker Full T01: Motors 22, 77, 138 were stuck. Soltec Tracker Full T02: Motors 4, 21, 23, 32, 37, 58, 61, 83 were stuck. Soltec Tracker Full T03: Motors 13, 52 were stuck. Soltec Tracker Full T04: Motors 1, 11, 27, 28, 29, 32, 39, 51, 57, 65, 75, 88, 94, 112, 113 were stuck. | 1.SR099220 2.SR099221 3.SR099222 4.SR099295 5.SR099759 6.SR099835 7.SR099913 8.SR099224 | SR099221 | SR099222 | SR099295 | SR099759 | SR099835 | SR099913 | SR099224
Warsaw - Hemings | VA | 997106.8 | 1042780 | -45673.2 | -4.38% | 1046855 | -49748.2 | -4.752% | 1.Inverter 21 was derating by 50 kW from 02/24 due to an "External Fan Error" fault. This issue occurred on days with high irradiance and was resolved on 04/22 after the technician replaced the faulted fan. 2.Mutiple trackers are stuck, and Solectria is actively working on troubleshooting the issue. | 1.SR098569,SR099625 2.SR098568,SR098376, | SR099625 | SR098568 | SR098376
Mount Jackson - Randolf | VA | 563764.2056 | 600437.8 | -36673.5944 | -6.108% | 698984.1 | -135219.8944 | -19.35% | 1. Site tripped offline at 11:45 on 03/31 due to blown MV fuse and back online at 12:15 on 04/03 after technician along with MV crew replaced MV fuse and utility re-energized the site. 2.Inverter 18 was tripped offline at 11:30 on 04/16 due to Inverter Over Current fault and back online on 04/17. 3.Inverter 15 tripped offline at 13:00 on 04/21 due to an Inverter Over Current fault and was back online on 04/22. It tripped again at 15:00 on 04/28 with the same fault and was restored on 04/29. 4.Site tripped offline at 15:56 on 04/27 due to Grid Phase Voltage Out of Range - GridV.OutLim fault and back online at 13:30 on 04/28. 5.Inverter 7 tripped offline at 18:00 on 04/29 due to Inverter Over Current fault and back online on 04/30. 6.NCU 2 motor 7 was stuck and motor was being RMA'd and on 04/17/25, the technician confirmed a defective tracker motor, replaced it, power cycled the controller, cleared the fault in Mission Control, and verified the tracker is now operating correctly with its peers. | 1.SR099141 2.SR099914 3.SR100087 & SR100473 4.SR100473 5.SR100673 6.SR098566 | SR099914 | SR100087 | SR100473 | SR100473 | SR100673 | SR098566
Callands Gretna - Monroe | VA | 465408 | 0 | 465408 |  | 460255.2 | 5152.8 | 1.12% | 1.On 04/18 the technician attempted to add a new tracker using the Soltec computer onsite, but the system showed it wasn't connected to the server. The previously installed tracker (C30) remains in stow and Soltec has not responded. 2.The POA sensor (Hukseflux SR15-D1-POA) stopped communicating on 03/16/25 due to a fault and is currently being RMA'd. Additionally, the wire for the BPOA was found to be damaged. | 1.SR098567 2.SR099419 & SR099420 | SR099419 | SR099420
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 |  |  | 0 |  |  | 1. Site was not communicated for whole month due to bad modem. 2. Inverter 19 all 3 external fans were RMA'D due to external fan fault. 3. The client reported that the site tripped offline between 10:30 AM and 11:30 AM on 04/23 and was producing at a steady but low output of 23.824 kW. Normal production resumed on 04/24, but data backfilling is progressing slowly with 4,962,922 files in the queue. Confirmation is needed to proceed with the internet provider switch. 4.Stuck tracker reported by Nick Lindsholm. Troubleshooting will proceed once communication is restored. A Soltec ticket cannot be created until the serial number of the affected unit is identified. | 1.SR097305 & SR098700 2.SR099878 3.SR100221 4.SR100415 | SR098700 | SR099878 | SR100221 | SR100415

## Jun
True Green Capital Management LLC |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 4506188.5 | 3776961.9 | 729226.6 | 19.31% | 5695287.9 | -1189099.4 | -20.88%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 1849625 | 1871565 | -21940 | -1.172% | 2595332 | -745707 | -28.73% | 1. Inverter 73 tripped offline at 12:00 CDT on 06/04 and reporting "Bus Imbalance - Protect0070". Technician discovered permanent power head failure fault later he replaced the powerhead on site and inverter back online at 13:00 CDT on 06/05 and also technician replaced the powerhead for inverter 55. 2.Inverter 78 tripped offline on 6/8/25 at 13:25 CDT and reporting permanent fault of power module - Fault0010 later the technician has replaced the inverter on site and it is back online at 14:15 on 06/13. 3. While performing PM on 06/18 btween 10:45 to 13:30, technician found inverter 30 power grid relay fault was detected. Technician was unable to power cycle reset and later he replaced new powerhead. 4. Inverters 54 & 55 have tripped offline at 17:45 CDT on 06/22 and due to Fault0010 Power Module Protection - Protect0120 and back online at 12:30 CDT on 06/24 5. Inverter 64 was LOTO'd and was offline for whole month. | 1.SR102470 2.SR102702 3. SR103139 4. SR103277 5. | SR102702 | SR103139 | SR103277
Warsaw - Hemings | VA | 1104759 | 836321.2 | 268437.8 | 32.1% | 1193055 | -88296 | -7.401% | 1. The weather station Hukseflux SR15 – POA has been communicating properly from 06/06 at 09:00am 2.11 trackers currently struck from 06/17 | 1.SR102509 2.SR101583 | SR101583
Mount Jackson - Randolf | VA | 518678 | 540127.4 | -21449.4 | -3.971% | 824172.1 | -305494.1 | -37.07% | 1. All inverters are offline on 06/02 at 01:00am due to "Loss of Main - GridV.OutLim " and later back online at 12:00 on 06/06. Again all inverters tripped offline at 11:00 AM on 06/07 due to "Grid Phase Voltage Out of Range - GridV.OutLim", later the site back online at 13:45 on 06/07. 2. Inverter 15 tripped at 12:45pm on 06/08 and back online at 06/09 | 1. SR102342 2.SR100087 | SR100087
Callands Gretna - Monroe | VA | 532168 | 528948.3 | 3219.7 | 0.6087% | 527978.8 | 4189.2 | 0.7934% |  | 1.SR102470 2.SR102702 3. SR103139 4. SR103277 5.
Rockbridge Baths - Small Mouth Bass | VA | 500958.5 | 0 | 500958.5 |  | 554750 | -53791.5 | -9.697% | 1. The site has been experiencing a power quality issue affecting generation since 05/10. 2. 4 trackers have struck from 05/19 | 1.SR101462 2.SR101580 | SR101580

## May
True Green Capital Management LLC |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 4487672.8 | 3583658.8 | 904014 | 25.23% | 5450570.1 | -962897.3 | -17.67%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 2339962 | 2505562 | -165600 | -6.609% | 2449711 | -109749 | -4.48% | 1. Site production was low on 05/25, 05/26, 05/27, 05/28 due to technician was on site for preventive maintenance work. 2. Inverter 58 tripped offline at 11:30 on 05/03 due to a "Permanent Fault of Power Module". A technician later replaced the power head on site, and the inverter came back online at 08:45 on 05/05. 3. Inverter 14 tripped offline at 10:15 on 05/06 due to "Permanent fault of power module - Fault0010". Later, a technician on site replaced the power head, and the inverter came back online at 09:30 on 05/08. 4. Inverter 21 tripped offline at 10:12 on 05/13 due to "Grid Line Voltage Out of Range - GridV.OutLim". Later, a technician on site power-cycled the inverter, and it came back online at 17:04 on 05/13. 5. Inverter 72 tripped offline at 17:30 on 05/23 due to "Permanent fault of power module - Fault0010, Power Module Protection - Protect0120". Later, with support from Chint, the technician was able to remotely reset the inverter, and it came back online at 13:30 on 05/27. 6. Inverter 72 tripped offline at 11:06 on 05/29 due to "Permanent fault of power module - Fault0010, Power Module Protection - Protect0120". Inverter RMA dispatch has been scheduled for the month of June | 1. PM9696 2. SR100960 3. SR101064 4. SR101885 5. SR101923 6. SR102146
Warsaw - Hemings | VA | 987436.9 | 394357.6 | 593079.3 | 150.4% | 1178200 | -190763.1 | -16.19% | 1. The weather station Hukseflux SR15 – POA has been communicating intermittently since 05/14. | 1. SR102509
Mount Jackson - Randolf | VA | 508599.4 | 563615.2 | -55015.8 | -9.761% | 757224.9 | -248625.5 | -32.83% | 1. Inverter 15 tripped offline at 14:40 on 05/07 due to 'Inverter Over Current - Protect0030' and came back online at 06:00 on 05/08. 2. The site tripped offline due to "Grid Phase Voltage Out of Range - GridV.OutLim" at 10:45 on 05/10 and came back online at 07:15 on 05/12. 3. The site tripped offline due to "Grid Phase Voltage Out of Range - GridV.OutLim" at 11:15 on 05/24 and came back online at 11:03 on 05/27. | 1. SR100087 2. SR100473 3. SR101911
Callands Gretna - Monroe | VA | 444464 | 120124 | 324340 | 270% | 527749.2 | -83285.2 | -15.78% | 1. The Hukseflux SR15-D1-BPOA had intermittent communication since 03/16. During a site visit on 05/22, the technician found the SCADA was defective, installed a new one, and stated that the BPOA will remain offline until the correct cable is installed. Additional troubleshooting was also recommended. | 1. SR099420
Rockbridge Baths - Small Mouth Bass | VA | 207210.5 | 0 | 207210.5 |  | 537685 | -330474.5 | -61.46% | 1. The site has been experiencing a power quality issue affecting generation since 05/10. | 1. SR101462

## Jul
True Green Capital Management LLC |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 5342949.3 | 4565154.682 | 777794.618 | 17.04% | 5781982.91 | -439033.61 | -7.593%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 2543098 | 2734391.06 | -191293.06 | -6.996% | 2729078.1 | -185980.1 | -6.815% | 1. Inverter 33 was tripped offline on 07/30 at 16:00 and reporting “Bus Imbalance - Protect0070”. 2. Inverter 21 was tripped offline at 16:00 on 07/24 and inverter 21 powerhead being RMA'd. 3. Inverter 34 was offline from 13:15 on 07/23 to 10:15 on 07/24. 4. Inverter 52 was offline from 06:00 on 07/20 to 08:15 on 07/24 due to Permanent fault of power module - Fault0010. 5. Inverter 20 was offline from 13:15 on 07/09 to 07:00 on 07/18 due to Permanent fault of power module - Fault0010. 6. Inverter 24 was offline from 06:00 on 07/01 to 10:15 on 07/08 and 14:45 on 07/08 to 11:00 on 07/09 7. Inverter 45 tripped offline at 10:45 on 07/03 and reporting Internal Communicate Failed - CommErr. and back online at 11:15 on 07/08 8. Inverter 28 was offline from 11:00 on 07/03 to 07:00 on 07/08 due to grid under frequency. 9. Inverter 75 was offline from 11:15 on 07/03 to 08:30 on 07/08. 10. Inverter 64 was LOTO'd and was offline for whole month. 11. Most of the trackers required repair. | 1. SR105393 2. SR105006 3. SR104883 4. SR104670 5. SR104214 6. SR103975 7. SR104000 8. SR103977 9. SR103976 10. SR099221, SR103657 11. SR102147
Warsaw - Hemings | VA | 1224675.9 | 502250.43 | 722425.47 | 143.8% | 1149768.47 | 74907.43 | 6.515% | 1. Weather station was not communicated from 20:45 on 07/14 2. Inverter 17 was derating to 75kW from 10:30 on 07/29 and reporting External Fan Err - ExtFanerr 3. 8 trackers remained stuck for whole month.(motors need to be replaced) | 1. SR104941 2. SR105308 3. SR101583
Mount Jackson - Randolf | VA | 745429.4 | 781103.02 | -35673.62 | -4.567% | 830093.65 | -84664.25 | -10.2% | 1. Site was offline from 16:30 to 19:45 on 07/02 2. Multiple inverters experienced tripping events on 07/22 due to a technician being on site for preventive maintenance. | 1. SR103941 2. PM9485
Callands Gretna - Monroe | VA | 537642 | 547410.172 | -9768.172 | -1.784% | 512383.36 | 25258.64 | 4.93% | 1. Inverter 2 was tripped offline on 07/18 at 15:15 and back online on 07/21 at 08:00. 2. BPOA was not communicated for whole month. 3. Trackers were not communicating for the entire month, so it is not possible to confirm which tracker was offline. | 1. SR104630 2. SR099420 3. SR101449
Rockbridge Baths - Small Mouth Bass | VA | 292104 | 0 | 292104 |  | 560659.33 | -268555.33 | -47.9% | 1. Site was curtailed from 07/01 at 06:15 to 07/15 at 20:15 2. 4 trackers remained stuck for whole month 3. Weather station was not communicating from 12/18. | 1. SR101462 2. SR101580, SR100415 3. SR105397

## Aug
True Green Capital Management LLC |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 4554624.6 | 3387580.97 | 1167043.63 | 34.45% | 5239527.66 | -684903.06 | -13.07%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 2164221 | 2244634.71 | -80413.71 | -3.582% | 2394063.97 | -229842.97 | -9.601% | 1. Most of the trackers required repair. 2. Inverter 64 was LOTO'd. 3. Inverter 21 was offline from 06:00 on 08/07 to 09:45 on 08/14 Inverter 21 tripped offline at 15:30 on 08/27 and back online 08/28 at 06:00. 4. Inverter 69 tripped offline at 12:30 on 08/07 and back online at 09:00 on 08/14. 5. Inverter 70 was derated by 50kW from 09:00 on 08/11 to 08:00 on 08/14 6. Inverter 33 was offline from 05:45 to 09:00 on 08/01. | 1. SR102147 2. SR099221 3. SR105946, SR107054 4. SR105860 5. SR106166 6. SR105393 | SR099221 | SR105946 | SR107054 | SR105860 | SR106166 | SR105393
Warsaw - Hemings | VA | 790338.5 | 0 | 790338.5 |  | 1079860.17 | -289521.67 | -26.81% | 1. 8 trackers remained stuck for whole month.(motors need to be replaced). 2. Inverter 17 was derated at 75.2kW from 08/01 to 08/21 3. Inverter 16 was derated at 75.3kW from 08/01 to 08/21 4. Weather station was not communicated for whole month. | 1. SR101583 2. SR105308 3. SR105629 4. SR104941 | SR105308 | SR105629 | SR104941
Mount Jackson - Randolf | VA | 690534.5 | 702387.516 | -11853.016 | -1.688% | 760750.11 | -70215.61 | -9.23% | 1. NCU 1 all trackers stuck and reporting Wind stow, NCU 2 was not communicated from 5/15 2. 12 Modules being replced. | 1. SR103137 2. SR105402 | SR105402
Callands Gretna - Monroe | VA | 447651 | 440558.744 | 7092.256 | 1.61% | 476302.14 | -28651.14 | -6.015% | 1.Hukseflux SR15-D1-POA stopped communicating 03/16/25. Huskseflux SR15-D1-BPOA has intermittent comms. 2. Tracker system is not communicated for whole month. | 1. SR099420 2. SR101449 | SR101449
Rockbridge Baths - Small Mouth Bass | VA | 461879.6 | 0 | 461879.6 |  | 528551.27 | -66671.67 | -12.61% | 1. Trackers were not communicated for whole month 2. Weather station is not communicated from 12/18 to end of the month. 3. Inverter 14 was offline from 13:30 on 08/20 to 11:30 on 08/26. 4. All Inverters were tripped offline on 08/25 at 12:30 and back online on 08/26 at 11:00. | 1. SR101580, SR100415 2. SR105397 3. SR106590 4. SR106873 | SR100415 | SR105397 | SR106590 | SR106873

## Sep
True Green Capital Management LLC |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 3515868.7 | 2048734.3 | 1467134.4 | 71.61% | 4259688.4 | -743819.7 | -17.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW | MN | 1421436 | 1231101 | 190335 | 15.46% | 1880527 | -459091 | -24.41% | 1.Inverter 13 tripped offline at 07:30 on 09/04 and offline for whole month 2.Inverter 40 tripped offine at 12:30 on 09/08 and back online at 11:45 on 09/12 3. Inverter 64 was LOTO'd. 4. Most of the trackers required repairs. Whenever the trackers were getting stuck, it was also affecting the weather station. | 1.SR107451 2.SR107650 3. SR099221 4.SR102147 | SR107650 | SR099221 | SR102147
Warsaw - Hemings | VA | 756441.8 | 0 | 756441.8 |  | 903150 | -146708.2 | -16.24% | 1.Weather station was not communicated for whole month. 2.Site tripped offline at 08:00 on 09/15 and back online at 13:45 on 09/15. 3.8 trackers remained stuck for whole month.(motors need to be replaced). | 1.SR104941 2.SR107935 3.SR101583 | SR107935 | SR101583
Mount Jackson - Randolf | VA | 513321.6 | 472595.8 | 40725.8 | 8.617% | 629251.5 | -115929.9 | -18.42% | 1. 12 modules are replaced on 09/22 2. Site tripped offline at 07:00 on 09/23 and later back online at 09:30 on 09/27 | 1.SR105402 2.SR108406 | SR108406
Callands Gretna - Monroe | VA | 403870 | 345037.5 | 58832.5 | 17.05% | 405959.9 | -2089.9 | -0.5148% | 1.Hukseflux SR15-D1-POA stopped communicating 03/16/25. Huskseflux SR15-D1-BPOA has intermittent comms. Further Troubleshooting required need to run a new conduit to install replacement cable. 2. Tracker system is not communicated for whole month. | 1. SR099420, SR108512 2. SR101449 | SR108512 | SR101449
Rockbridge Baths - Small Mouth Bass | VA | 420799.3 | 0 | 420799.3 |  | 440800 | -20000.7 | -4.537% | 1.Weather station is not communicated from 12/18 to end of the month. 2. Trackers were not communicated for whole month | 1.SR105397 2.SR101580, SR100415 | SR101580 | SR100415

## Oct
True Green Capital Management LLC |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 3409621.5 | 2918121.5 | 491500 | 16.84% | 3339773.8 | 69847.7 | 2.091%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Rochester - 5516 Valleyhigh NW | MN | 1187198 | 1325631 | -138433 | -10.44% | 1337272 | -150074 | -11.22% | 1.Inverter 13 tripped offline at 07:30 on 09/04 and offline for whole month 2. Inverter 64 was being LOTO'd. 3. Most of the trackers required repairs. Whenever the trackers were getting stuck, it was also affecting the weather station. 4.Soltec trackers, T01: Motor 14, 22, 24, 55, 77, 127, 138 are stuck. T02: All motors are stuck. T03: Motor 10, 13, 52 are stuck. T04: Motor 1, 11, 27, 28, 29, 32, 39, 49, 51, 57, 65, 75, 78, 88, 89, 94, 112, 113 are stuck. 5. Inverter 24 is derating at 50kW on 10/24 and later resolved. 6.Inverter 35 offline on 10/10 and back online on 10/11 7. Meters LV2 and LV3, invs 29-80, Huskeflux L32, Weather stations 3, 4, & 6 stopped communicating. UPS 2 is in battery mode on 10/11. On 10/12 technician confirmed several inverters are showing no communications (13,32,34,39, 42,43,44,45 49,51 52, 59,62, 63, 66, 67, 72,74,77 and 80), tech said bad weather in the area is affecting the inverters and some of them are on standby | 1.SR107650 2.SR099221 3.SR102147 4. SR109898 5.SR109945 6.SR109354 7.SR109388 | 1.Pending 2.Closed 3.Closed 4.Pending 5.Closed 6.Closed 7.Closed | SR099221 | SR102147 | SR109898 | SR109945 | SR109354 | SR109388
Warsaw - Hemings | VA | 875509.9 | 861665.3 | 13844.6 | 1.607% | 723990 | 151519.9 | 20.93% | 1. Inverter 22 started derating by 50 kW at 14:00 on 10/01 looks like a fan fault. no alert reported. 2. Inverter 22 has been derating daily from 10/19 due to a fan error, usually starting around 11:00. Initial event occurred 10/16. | 1.SR108844 2.SR109883 | 1.Closed 2.Pending | SR109883
Mount Jackson - Randolf | VA | 590677.1 | 575691.1 | 14986 | 2.603% | 536959.2 | 53717.9 | 10% | 1. Site was producing as expected.
Callands Gretna - Monroe | VA | 376347 | 155134.1 | 221212.9 | 142.6% | 361097.6 | 15249.4 | 4.223% | 1.Hukseflux SR15-D1-POA started communicating on 10/20 at 10:30 | 1.SR108512 | 1.Closed
Rockbridge Baths - Small Mouth Bass | VA | 379889.5 | 0 | 379889.5 |  | 380455 | -565.5 | -0.1486% | 1.Weather station is not communicated from 12/18 to end of the month. 2. 7 trackers are currently stuck. Tracker 1 Group F motors 12 and target angle, & 14 Tracker 2 Group A motors 3, & 7 and target angle Tracker 2 Group C motors 12 and target angle, & 13 Tracker 2 Group D motor 7 | 1.SR105397 2. SR109931 | 1.Pending 2.Pending | SR109931

## Nov
True Green Capital Management LLC |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 2461452.649 | 2220880.3501 | 240572.2989 | 10.83% | 2364226.7 | 97225.949 | 4.112%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Rochester - 5516 Valleyhigh NW | MN | 868747.949 | 809870.4 | 58877.549 | 7.27% | 827046.8 | 41701.149 | 5.042% | 1. Inverter 24 is derating at 50kW on regular basis from 11/12 to end of the month. 2. Inverter 64 was being LOTO'd. 3. T01: Motor 14, 22, 24, 55, 77, 127, 138 are stuck. T02: All motors are stuck. T03: Motor 10, 13, 52 are stuck. T04: Motor 1, 11, 27, 28, 29, 32, 39, 49, 51, 57, 65, 75, 78, 88, 89, 94, 112, 113 are stuck. 4. Inverters 1 to 28 tripped offline at 09:00 on 11/07 and the site was offline from 16:30 on 11/07 to 10:00 on 11/10. 5. Inverter 14 was offline from 08:30 to 10:00 on 11/21. 6.Meter 2 was not communicating from 01:36 on 10/30 | 1. SR111820 2. SR099221 3. SR109898 4. SR110765 5. SR111456 6.SR110529 | 1. Pending 2. Closed 3. Pending 4. Closed 5. Closed 6.Pending | SR099221 | SR109898 | SR110765 | SR111456 | SR110529
Warsaw - Hemings | VA | 626241.8 | 620515.3 | 5726.5 | 0.9229% | 585025 | 41216.8 | 7.045% | 1. Inverter 22 fan being RMA'd. 2. A string was found offline from flyover. | 1. SR109883 2. SR110594 | 1. Pending 2. Pending | SR110594
Mount Jackson - Randolf | VA | 412573.4 | 389031.7 | 23541.7 | 6.051% | 390483.7 | 22089.7 | 5.657% | 1. Inverter 7 was offline from 11:00 to 17:00 on 11/05. Again inverter offline from 12:00 to 17:00 on 11/11 | 1. SR110898 | 1. Closed
Callands Gretna - Monroe | VA | 282204 | 400857.8 | -118653.8 | -29.6% | 278841.2 | 3362.8 | 1.206% | 1. Trackes were not communicated for whole month. | 1. SR101449 | 1. Closed
Rockbridge Baths - Small Mouth Bass | VA | 271685.5 | 605.1501 | 271080.3499 | 44796% | 282830 | -11144.5 | -3.94% | 1. 7 trackers are currently stuck. Tracker 1 Group F motors 12 and target angle, & 14 Tracker 2 Group A motors 3, & 7 and target angle Tracker 2 Group C motors 12 and target angle, & 13 Tracker 2 Group D motor 7 are stuck 2. Weather station parts being replaced | 1. SR109931 2. SR105397 | 1. Pending 2. Pending | SR105397
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As meter 2 was not communicating for whole month we have taken total inverters energy as actual energy.

## Dec
True Green Capital Management LLC |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 1784691.966 | 1776400.252 | 8291.714 | 0.4668% | 1866067.7 | -81375.734 | -4.361%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Rochester - 5516 Valleyhigh NW | MN | 679805.066 | 593312.1 | 86492.966 | 14.58% | 664670 | 15135.066 | 2.277% | 1.T01: Motor 14, 22, 24, 55, 77, 127, 138 are stuck. T02: All motors are stuck. T03: Motor 10, 13, 52 are stuck. T04: Motor 1, 11, 27, 28, 29, 32, 39, 49, 51, 57, 65, 75, 78, 88, 89, 94, 112, 113 are stuck. 2.Inverter 24 is derating at 50kW on regular basis from 11/12 to end of the month. 3.Meter 2 has regained its communication at 10:30 on 12/18 4.Inverter 64 was being LOTO'd. | 1.SR109898 2.SR111820 3.SR110529 4.SR099221 | 1.Pending 2.Pending 3.Closed 4.Closed | SR110529 | SR099221
Warsaw - Hemings | VA | 459760.4 | 477537.6 | -17777.2 | -3.723% | 441945 | 17815.4 | 4.031%
Mount Jackson - Randolf | VA | 297274.3 | 281935.9 | 15338.4 | 5.44% | 307798.1 | -10523.8 | -3.419%
Callands Gretna - Monroe | VA | 179336 | 273231.3 | -93895.3 | -34.36% | 226459.6 | -47123.6 | -20.81% | 1. Trackes were not communicated for whole month. 2.Inverter 17 has evening shading | 1. SR101449 | 1. Closed
Rockbridge Baths - Small Mouth Bass | VA | 168516.2 | 150383.352 | 18132.848 | 12.06% | 225195 | -56678.8 | -25.17% | 1. 7 trackers are currently stuck. Tracker 1 Group F motors 12 and target angle, & 14 Tracker 2 Group A motors 3, & 7 and target angle Tracker 2 Group C motors 12 and target angle, & 13 Tracker 2 Group D motor 7 are stuck | 1.SR109931 | 1.Closed
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As meter 2 has regained its communication at 10:30 on 12/18, actual energy is taken from total inverters energy

## Sites
Portfolio: | True Green Capital Management LLC
Site DAS Name | Site | State | Update | DAS
Fund IV - WestSide Solar MN | Rochester - 5516 Valleyhigh NW | MN | AEF | Powertrack
Fund IV - Hemings | Warsaw - Hemings | VA | AEF | Powertrack
Fund IV - Randolf | Mount Jackson - Randolf | VA | AEF | Powertrack
Fund IV - Monroe Solar | Callands Gretna - Monroe | VA | AEF | Powertrack
Fund IV - Smallmouth Bass | Rockbridge Baths - Small Mouth Bass | VA | AEF | Powertrack