## Year to Date
Valmont Industries |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 584249.128 | 552223.326 | 32025.802 | 5.799% | 683699.156 | -99450.028 | -14.55%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 584249.128 | 552223.326 | 32025.802 | 5.799% | 683699.156 | -250148.216 | -36.59%

## 1st Qtr
Valmont Industries |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 150698.188 | 112449.57 | 38248.618 | 34.01% | 0 | 150698.188 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 150698.188 | 112449.57 | 38248.618 | 34.01% | 0 | 0

## 2nd Qtr
Valmont Industries |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 229406.063 | 197246.691 | 32159.372 | 16.3% | 279873.354 | -50467.291 | -18.03%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 229406.063 | 197246.691 | 32159.372 | 16.3% | 279873.354 | -50467.291 | -18.03%

## 3rd Qtr
Valmont Industries |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 139098.126 | 165401.928 | -26303.802 | -15.9% | 269767.694 | -130669.568 | -48.44%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 139098.126 | 165401.928 | -26303.802 | -15.9% | 269767.694 | -130669.568 | -48.44%

## 4th Qtr
Valmont Industries |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 65046.751 | 77125.137 | -12078.386 | -15.66% | 134058.108 | -69011.357 | -51.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Valmont | IN | 65046.751 | 77125.137 | -12078.386 | -15.66% | 134058.108 | -69011.357 | -51.48%

## Jan
Valmont Industries |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 26968.676 | 22909.665 | 4059.011 | 17.72% | 0 | 26968.676 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 26968.676 | 22909.665 | 4059.011 | 17.72% | N/A |  |  | 1.All trackers were stuck since 12/19/24. | 1.SR092973

## Feb
Valmont Industries |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 41511.574 | 30572.197 | 10939.377 | 35.78% | 0 | 41511.574 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 41511.574 | 30572.197 | 10939.377 | 35.78% | N/A |  |  | 1.All trackers were stuck since 12/19/24. | 1.SR092973

## Mar
Valmont Industries |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 82217.938 | 58967.708 | 23250.23 | 39.43% | 0 | 82217.938 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 82217.938 | 58967.708 | 23250.23 | 39.43% | N/A |  |  | 1.Inverter 2 tripped offline at 16:00 on 03/02 due to Grid Line Voltage Out of Range and back online at 8:45AM on 03/03. Again tripped offline from 12:00PM to 12:45PM on 03/11 due to Grid Line Voltage Out of Range. 2.Site tripped offline at 17:00 on 03/30 due to storm and remained offline whole month. 3.All trackers were stuck since 12/19/24 and Volmont site team working on trackers. | 1.SR097973 2.SR099153 3.SR092973 | SR099153 | SR092973

## Apr
Valmont Industries |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 71050.125 | 53448.026 | 17602.099 | 32.93% | 84872.5 | -13822.375 | -16.29%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 71050.125 | 53448.026 | 17602.099 | 32.93% | 84872.5 | -13822.375 | -16.29% | 1. The site tripped offline at 17:00 on 03/30 and came back online at 14:15 on 04/07. 2. Inverter 4 tripped offline at 17:30 on 04/29 due to a 'Grid Line Voltage Out of Range' error. A technician was on-site on 04/30 and swapped the powerheads of Inverter 3 and Inverter 4 to check if the fault reoccurs. The inverter came back online at 09:00 on 04/30. 3. All trackers are not tracking. | 1. SR099153 2. SR100671 3. SR099992 | SR100671 | SR099992

## May
Valmont Industries |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 84285.875 | 69529.908 | 14755.967 | 21.22% | 96105.854 | -11819.979 | -12.3%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 84285.875 | 69529.908 | 14755.967 | 21.22% | 96105.854 | -11819.979 | -12.3% | 1. Inverter 2 tripped offline at 11:30 on 05/15 due to "Grid Line Voltage Out of Range - GridV.OutLim". A technician was on-site on 05/16 and reset the inverter, which came back online at 13:00 on 05/16. The inverter tripped offline again at 16:00 on 05/19. 2. Inverter 4 tripped offline at 16:00 on 05/15 due to "Grid Line Voltage Out of Range - GridV.OutLim", came back online at 12:00 on 05/16, and is currently being RMA’d. 3. All trackers are not tracking. | 1. SR101477 2. SR101551 3. SR099992 | SR101551 | SR099992

## Jun
Valmont Industries |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 74070.063 | 74268.757 | -198.694 | -0.2675% | 98895 | -24824.937 | -25.1%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 74070.063 | 74268.757 | -198.694 | -0.2675% | 98895 | -24824.937 | -25.1% | 1. Inverter 2 tripped offline at 16:00 from 05/19. inverter came back online on 06/06. And again inverter 2 tripped offline again 12:30 on 06/08 . Inverter was offline from 13:00 on 06/08 to 07:00 on 06/11 and again inverter was offline from 14:00 on 06/12 to 12:00 on 06/16 multiple days trough out the month 2.The site tripped offline from 15:45 to 16:15 on 06/20 due to a technician working on Inverter 2 3. Inverter 3 tripped offline from 13:45 on 06/21 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim" 4.Inverter 4 tripped offline from 16:45 on 06/25 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim". 5. All trackers are not tracking. | 1.SR101477 2.SR101551 3. SR103258 4.SR103554 5. SR099992 | SR101551 | SR103258 | SR103554 | SR099992

## Jul
Valmont Industries |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 57409.25 | 73218.471 | -15809.221 | -21.59% | 100560.774 | -43151.524 | -42.91%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 57409.25 | 73218.471 | -15809.221 | -21.59% | 100560.774 | -43151.524 | -42.91% | 1. Inverter 3 tripped offline from 13:45 on 06/21 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim" 2.Inverter 4 tripped offline from 16:45 on 06/25 to end of the month and reporting "Grid Line Voltage Out of Range - GridV.OutLim". 3.All trackers are not tracking from 04/18 | 1.SR103258 2.SR103554 3.SR099992 | SR103554 | SR099992

## Aug
Valmont Industries |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 66772.313 | 71299.581 | -4527.268 | -6.35% | 92052.42 | -25280.107 | -27.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 66772.313 | 71299.581 | -4527.268 | -6.35% | 92052.42 | -25280.107 | -27.46% | 1. Inverter 3 was back online at 15:15 on 08/05 2. Inverter 4 is back online at 15:15 on 08/05 3.Inverter 3 tripped offline at 16:00 on 08/06 and back online at 15:45 on 08/26, while tech on site the site was offline from 11:00 to 15:45 4.Site tripped offline at 16:45 on 08/27 and back online at 13:30 on 08/28. Again site tripped offline at 14:45 on 08/30. 5.All trackers are not tracking from 04/18. On 08/27 tech replaced the ethernet cable but not connected rained out. | 1.SR103258 2.SR103554 3.SR105771 4.SR107052 5.SR099992 | SR103554 | SR105771 | SR107052 | SR099992

## Sep
Valmont Industries |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 14916.563 | 20883.876 | -5967.313 | -28.57% | 77154.5 | -62237.937 | -80.67%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Valmont | IN | 14916.563 | 20883.876 | -5967.313 | -28.57% | 77154.5 | -62237.937 | -80.67% | 1. Site was back online at 09/02 at 12:30 2.Site tripped offline at 13:25 on 09/04 and back online at 04:30am on 09/05. 3.Site tripped offline on 09/06 at 12:15 and back online at 11:00 on 09/09 4. Site tripped offline on 09/10 at 14:45 and back online at 12:00 on 09/30 | 1.SR107052 2.SR107447 3.SR107555 4.SR107782 | SR107447 | SR107555 | SR107782

## Oct
Valmont Industries |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 29744.063 | 35308.43 | -5564.367 | -15.76% | 58522.098 | -28778.035 | -49.17%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Valmont | IN | 29744.063 | 35308.43 | -5564.367 | -15.76% | 58522.098 | -28778.035 | -49.17% | 1. The site tripped offline at 12:45 on 10/02 and came back online at 11:45 on 10/09. Additionally, Inverter 5 is offline due to site derating to 200 kW to prevent repeat tripping. | 1. SR108814 | 1. pending

## Nov
Valmont Industries |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 20617.25 | 23689.184 | -3071.934 | -12.97% | 41631 | -21013.75 | -50.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Valmont | IN | 20617.25 | 23689.184 | -3071.934 | -12.97% | 41631 | -21013.75 | -50.48% | 1. Inverter 5 is offline due to site derating to 200 kW to prevent repeat tripping. | 1. SR108814 | 1. pending

## Dec
Valmont Industries |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 14685.438 | 18127.523 | -3442.085 | -18.99% | 33905.01 | -19219.572 | -56.69%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Valmont | IN | 14685.438 | 18127.523 | -3442.085 | -18.99% | 33905.01 | -19219.572 | -56.69% | 1. Inverter 5 is offline due to site derating to 200 kW to prevent repeat tripping. 2.Multiple trackers are stuck and will need the manufacturer to troubleshoot the issue, as the software required for SCADA accessibility is proprietary in nature but may be granted software via waiver. | 1. SR108814 2.SR107446 | 1. pending 2.Pending | SR107446

## Sites
Portfolio: | Valmont Industries
Site DAS Name | Site | State | Update | DAS
Valmont Bristol | Valmont | IN |  | PowerTrack