## Littlefield Solar YTD
Walden Renewables Dev't LLC |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total
Site | Actual | Expected | Delta | % | Forecasted | Delta | %
ME: Wells - Littlefield Solar | 7540426 | 8669483.254 | -1129057.254 | -13.02% | 7895778.249 | -355352.249 | -4.501%
January | 306430 | 560571.1 | -254141.1 | -45.34% | 342243.7 | -35813.7 | -10.46% | 1.Low generation due to weather/snow.
February | 219588 | 601103.2 | -381515.2 | -63.47% | 451211.3 | -231623.3 | -51.33% | 1.Inverter 33 tripped offline at 11:45AM on 02/11. Technician found an alarm and cleared it. The inverterwas back online at 13:30 on 02/12. 2.Inverter 10 tripped offline at 12:00 PM on 02/25 due to an arc fault. It came back online at 9:45 AM on 02/26 after the technician cleared the grid unlock alarm by logging into the DAS. | 1.SR096699 2.SR097781 | SR097781
March | 681384 | 701424.143 | -20040.143 | -2.857% | 701755.12 | -20371.12 | -2.903% | 1. Inverter 32 did not start production due to Insolation resistance fault on 03/17 technician noted water pooling on the ground and inverter back online at 10:00 on 03/18. 2. Inverter 32 started late for the production at 13:00 on 03/31 | 1.SR098664 2.SR099174
April | 799664 | 805747.811 | -6083.811 | -0.7551% | 783489.13 | 16174.87 | 2.064% | 1. Inverter 32 started late for the production at 12:00pm on 04/22 due to "Alarm E34 - Insulation fault". Technician was dispatched to the site to replace the 4 solar modules on 04/25. And again inverte 32 tripped offline from 06:00 to 15:00 on 04/26. | 1.SR099174
May | 748850 | 748674.499 | 175.501 | 0.02344% | 895247.98 | -146397.98 | -16.35% | 1. Inverter 32 started late for the production on 05/04, 05/18, 05/20 and 05/31 due to "Alarm E34 - Insulation fault". | 1. SR099174
June | 868100 | 885732.198 | -17632.198 | -1.991% | 877072.6 | -8972.6 | -1.023% | 1.Inverter 32 started late for the production on 06/06 , 06/07 , 06/10 ,06/18 , 06/29 2. Inverter 20 was tripped offline multiple days | 1. SR099174 2. SR103744 | SR103744
July | 926000 | 960073.573 | -34073.573 | -3.549% | 932088.42 | -6088.42 | -0.6532% | 1. Site was offline at 9:15am on 07/01 due to utility outage and later utility power has been restored and back online at 13:00 on same day. 2. Invert 39 has tripped offline at 7:00am on 07/13 and later back online at 9:30am on 07/14 3. Inverter 20 tripped offline at 09:15am on 07/01 and reporting Alarm E34 - Insulation later back online at 11:15 on 07/14. Inverter 20 string 14 connector replaced. String 11 causing a ground fault, left unplugged. | 1. SR103827 2. SR104365 3. SR104443, SR104568, SR103827, SR103744, SR105336 | SR104365 | SR104443 | SR104568 | SR103827 | SR103744 | SR105336
August | 985740 | 1030575 | -44835 | -4.35% | 897662.9 | 88077.1 | 9.812% | 1.Inverter 32 started for production at 11:15 on 08/30 | 1. SR107227
September | 820410 | 865136.63 | -44726.63 | -5.17% | 738211.14 | 82198.86 | 11.13%
October | 634550 | 681943.016 | -47393.016 | -6.95% | 562223.76 | 72326.24 | 12.86% | 1.Inverter 31 is derating at 83kW from 10/09 and later resolved by replacing the fan on 10/17 | 1.SR109268 | 1.Closed
November | 347050 | 445930 | -98880 | -22.17% | 437000 | -89950 | -20.58% | 1. All inverters have heavy seasonal shading in the afternoon hours. 2. Inverter 32 was offline from 06:00 to 10:00 on 11/26.

## Year to Date (hidden)
Walden Renewables Dev't LLC |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 7540426 | 8669483.254 | -1129057.254 | -13.02% | 7895778.249 | -355352.249 | -4.501%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
ME: Wells - Littlefield Solar | MAINE | 7540426 | 8669483.254 | -1129057.254 | -13.02% | 7895778.249 | -355352.249 | -4.501%

## 1st Qtr
Walden Renewables Dev't LLC |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1207402 | 1863098.443 | -655696.443 | -35.19% | 1495210.12 | -287808.12 | -19.25%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
ME: Wells - Littlefield Solar | MAINE | 1207402 | 1863098.443 | -655696.443 | -35.19% | 1495210.12 | -287808.12 | -19.25%

## 2nd Qtr
Walden Renewables Dev't LLC |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 2416614 | 2440154.508 | -23540.508 | -0.9647% | 2555809.71 | -139195.71 | -5.446%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
ME: Wells - Littlefield Solar | MAINE | 2416614 | 2440154.508 | -23540.508 | -0.9647% | 2555809.71 | -139195.71 | -5.446%

## 3rd Qtr
Walden Renewables Dev't LLC |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 2732150 | 2855785.203 | -123635.203 | -4.329% | 2567962.46 | 164187.54 | 6.394%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
ME: Wells - Littlefield Solar | MAINE | 2732150 | 2855785.203 | -123635.203 | -4.329% | 2567962.46 | 164187.54 | 6.394%

## 4th Qtr
Walden Renewables Dev't LLC |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 1184260 | 1510445.1 | -326185.1 | -21.6% | 1276795.959 | -92535.959 | -7.248%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
ME: Wells - Littlefield Solar | MAINE | 1184260 | 1510445.1 | -326185.1 | -21.6% | 1276795.959 | -92535.959 | -7.248%

## Jan
Walden Renewables Dev't LLC |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 306430 | 560571.1 | -254141.1 | -45.34% | 342243.7 | -35813.7 | -10.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 306430 | 560571.1 | -254141.1 | -45.34% | 342243.7 | -35813.7 | -10.46% | 1.Low generation due to weather/snow.

## Feb
Walden Renewables Dev't LLC |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 219588 | 601103.2 | -381515.2 | -63.47% | 451211.3 | -231623.3 | -51.33%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 219588 | 601103.2 | -381515.2 | -63.47% | 451211.3 | -231623.3 | -51.33% | 1.Inverter 33 tripped offline at 11:45AM on 02/11. Technician found an alarm and cleared it. The inverterwas back online at 13:30 on 02/12. 2.Inverter 10 tripped offline at 12:00 PM on 02/25 due to an arc fault. It came back online at 9:45 AM on 02/26 after the technician cleared the grid unlock alarm by logging into the DAS. | 1.SR096699 2.SR097781 | SR097781

## Mar
Walden Renewables Dev't LLC |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 681384 | 701424.143 | -20040.143 | -2.857% | 701755.12 | -20371.12 | -2.903%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 681384 | 701424.143 | -20040.143 | -2.857% | 701755.12 | -20371.12 | -2.903% | 1. Inverter 32 did not start production due to Insolation resistance fault on 03/17 technician noted water pooling on the ground and inverter back online at 10:00 on 03/18. 2. Inverter 32 started late for the production at 13:00 on 03/31 | 1.SR098664 2.SR099174

## Apr
Walden Renewables Dev't LLC |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 799664 | 805747.811 | -6083.811 | -0.7551% | 783489.13 | 16174.87 | 2.064%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 799664 | 805747.811 | -6083.811 | -0.7551% | 783489.13 | 16174.87 | 2.064% | 1. Inverter 32 started late for the production at 12:00pm on 04/22 due to "Alarm E34 - Insulation fault". Technician was dispatched to the site to replace the 4 solar modules on 04/25. And again inverte 32 tripped offline from 06:00 to 15:00 on 04/26. | 1.SR099174

## May
Walden Renewables Dev't LLC |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 748850 | 748674.499 | 175.501 | 0.02344% | 895247.98 | -146397.98 | -16.35%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 748850 | 748674.499 | 175.501 | 0.02344% | 895247.98 | -146397.98 | -16.35% | 1. Inverter 32 started late for the production on 05/04, 05/18, 05/20 and 05/31 due to "Alarm E34 - Insulation fault". | 1. SR099174

## Jun
Walden Renewables Dev't LLC |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 868100 | 885732.198 | -17632.198 | -1.991% | 877072.6 | -8972.6 | -1.023%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 868100 | 885732.198 | -17632.198 | -1.991% | 877072.6 | -8972.6 | -1.023% | 1.Inverter 32 started late for the production on 06/06 , 06/07 , 06/10 ,06/18 , 06/29 2. Inverter 20 was tripped offline multiple days | 1. SR099174 2. SR103744 | SR103744

## Jul
Walden Renewables Dev't LLC |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 926000 | 960073.573 | -34073.573 | -3.549% | 932088.42 | -6088.42 | -0.6532%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 926000 | 960073.573 | -34073.573 | -3.549% | 932088.42 | -6088.42 | -0.6532% | 1. Site was offline at 9:15am on 07/01 due to utility outage and later utility power has been restored and back online at 13:00 on same day. 2. Invert 39 has tripped offline at 7:00am on 07/13 and later back online at 9:30am on 07/14 3. Inverter 20 tripped offline at 09:15am on 07/01 and reporting Alarm E34 - Insulation later back online at 11:15 on 07/14. Inverter 20 string 14 connector replaced. String 11 causing a ground fault, left unplugged. | 1. SR103827 2. SR104365 3. SR104443, SR104568, SR103827, SR103744, SR105336 | SR104365 | SR104443 | SR104568 | SR103827 | SR103744 | SR105336
s

## Aug
Walden Renewables Dev't LLC |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 985740 | 1030575 | -44835 | -4.35% | 897662.9 | 88077.1 | 9.812%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 985740 | 1030575 | -44835 | -4.35% | 897662.9 | 88077.1 | 9.812% | 1.Inverter 32 started for production at 11:15 on 08/30 | 1. SR107227

## Sep
Walden Renewables Dev't LLC |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 820410 | 865136.63 | -44726.63 | -5.17% | 738211.14 | 82198.86 | 11.13%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 820410 | 865136.63 | -44726.63 | -5.17% | 738211.14 | 82198.86 | 11.13%

## Oct
Walden Renewables Dev't LLC |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 634550 | 681943.016 | -47393.016 | -6.95% | 562223.76 | 72326.24 | 12.86%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
ME: Wells - Littlefield Solar | MAINE | 634550 | 681943.016 | -47393.016 | -6.95% | 562223.76 | 72326.24 | 12.86% | 1.Inverter 31 is derating at 83kW from 10/09 and later resolved by replacing the fan on 10/17 | 1.SR109268 | 1.Closed

## Nov
Walden Renewables Dev't LLC |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 347050 | 445930 | -98880 | -22.17% | 419856.12 | -72806.12 | -17.34%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
ME: Wells - Littlefield Solar | MAINE | 347050 | 445930 | -98880 | -22.17% | 419856.12 | -72806.12 | -17.34% | 1. All inverters have heavy seasonal shading in the afternoon hours. 2. Inverter 32 was offline from 06:00 to 10:00 on 11/26.

## Dec
Walden Renewables Dev't LLC |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 202660 | 382572.084 | -179912.084 | -47.03% | 294716.079 | -92056.079 | -31.24%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
ME: Wells - Littlefield Solar | MAINE | 202660 | 382572.084 | -179912.084 | -47.03% | 294716.079 | -92056.079 | -31.24% | 1.Site was offline at 12:45 on 12/19 and later back online at 08:15 on 12/21 2.Tech found that there is significant morning shading and spliced cable tray circuitry that may be causing faults during weather events. | 1.SR113330 2.SR114125 | 1.Closed 2.New | SR114125

## Sites
Portfolio: | Walden Renewables Dev't LLC
Site DAS Name | Site | State | Update | DAS
Littlefield Solar | ME: Wells - Littlefield Solar | MAINE | AEF | PowerTrack