## Year to Date
MN8 KEF |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1656300.064 | 2508449.514 | -852149.45 | -33.97% | 3542427.41 | -1886127.346 | -53.24%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Williamsburg A | MA | 71429.3597 | 149397.45 | -77968.0903 | -52.19% | 209068.03 | -137638.6703 | -65.83%
Orange A KB | MA | 91299.7043 | 119389.98 | -28090.2757 | -23.53% | 173726.81 | -82427.1057 | -47.45%
Goshen A | MA | 61153 | 133613.81 | -72460.81 | -54.23% | 104512.13 | -43359.13 | -41.49%
Phillipston A KB | MA | 61847 | 186327.53 | -124480.53 | -66.81% | 117312.95 | -55465.95 | -47.28%
Uxbridge D | MA | 109190 | 158353.06 | -49163.06 | -31.05% | 227349.1 | -118159.1 | -51.97%
West Bridgewater A&B | MA | 187584.5 | 276837.31 | -89252.81 | -32.24% | 370654.2 | -183069.7 | -49.39%
Sutton A | MA | 74736 | 127517.12 | -52781.12 | -41.39% | 208067.7 | -133331.7 | -64.08%
North Adams A | MA | 71943 | 116839.84 | -44896.84 | -38.43% | 216760.14 | -144817.14 | -66.81%
North Adams B | MA | 54882 | 26950.944 | 27931.056 | 103.6% | 216760.14 | -161878.14 | -74.68%
Clarksburg A | MA | 49031 | 103515.64 | -54484.64 | -52.63% | 215775.32 | -166744.32 | -77.28%
Swansea B | MA | 124174 | 168916.39 | -44742.39 | -26.49% | 117851.91 | 6322.09 | 5.364%
Wareham 2 | MA | 111349.5 | 129746.08 | -18396.58 | -14.18% | 226090.9 | -114741.4 | -50.75%
Kingston 1 KB | MA | 92890 | 134754.26 | -41864.26 | -31.07% | 174922.58 | -82032.58 | -46.9%
Kingston 2 KB | MA | 75074 | 83873.78 | -8799.78 | -10.49% | 140404.44 | -65330.44 | -46.53%
Holliston B | MA | 83988 | 139689.18 | -55701.18 | -39.88% | 218563.54 | -134575.54 | -61.57%
Fairhaven C | MA | 223864 | 300165.11 | -76301.11 | -25.42% | 386865.5 | -163001.5 | -42.13%
Plympton A-2 | MA | 111865 | 152562.03 | -40697.03 | -26.68% | 217742.02 | -105877.02 | -48.62%

## 1st Qtr
MN8 KEF |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1656300.064 | 2508449.514 | -852149.45 | -33.97% | 3542427.41 | -1886127.346 | -53.24%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Williamsburg A | MA | 71429.3597 | 149397.45 | -77968.0903 | -52.19% | 209068.03 | -137638.6703 | -65.83%
Orange A KB | MA | 91299.7043 | 119389.98 | -28090.2757 | -23.53% | 173726.81 | -82427.1057 | -47.45%
Goshen A | MA | 61153 | 133613.81 | -72460.81 | -54.23% | 104512.13 | -43359.13 | -41.49%
Phillipston A KB | MA | 61847 | 186327.53 | -124480.53 | -66.81% | 117312.95 | -55465.95 | -47.28%
Uxbridge D | MA | 109190 | 158353.06 | -49163.06 | -31.05% | 227349.1 | -118159.1 | -51.97%
West Bridgewater A&B | MA | 187584.5 | 276837.31 | -89252.81 | -32.24% | 370654.2 | -183069.7 | -49.39%
Sutton A | MA | 74736 | 127517.12 | -52781.12 | -41.39% | 208067.7 | -133331.7 | -64.08%
North Adams A | MA | 71943 | 116839.84 | -44896.84 | -38.43% | 216760.14 | -144817.14 | -66.81%
North Adams B | MA | 54882 | 26950.944 | 27931.056 | 103.6% | 216760.14 | -161878.14 | -74.68%
Clarksburg A | MA | 49031 | 103515.64 | -54484.64 | -52.63% | 215775.32 | -166744.32 | -77.28%
Swansea B | MA | 124174 | 168916.39 | -44742.39 | -26.49% | 117851.91 | 6322.09 | 5.364%
Wareham 2 | MA | 111349.5 | 129746.08 | -18396.58 | -14.18% | 226090.9 | -114741.4 | -50.75%
Kingston 1 KB | MA | 92890 | 134754.26 | -41864.26 | -31.07% | 174922.58 | -82032.58 | -46.9%
Kingston 2 KB | MA | 75074 | 83873.78 | -8799.78 | -10.49% | 140404.44 | -65330.44 | -46.53%
Holliston B | MA | 83988 | 139689.18 | -55701.18 | -39.88% | 218563.54 | -134575.54 | -61.57%
Fairhaven C | MA | 223864 | 300165.11 | -76301.11 | -25.42% | 386865.5 | -163001.5 | -42.13%
Plympton A-2 | MA | 111865 | 152562.03 | -40697.03 | -26.68% | 217742.02 | -105877.02 | -48.62%

## 2nd Qtr
MN8 KEF |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Williamsburg A | MA | 0 | 0 | 0 |  | 0 | 0
Orange A KB | MA | 0 | 0 | 0 |  | 0 | 0
Goshen A | MA | 0 | 0 | 0 |  | 0 | 0
Phillipston A KB | MA | 0 | 0 | 0 |  | 0 | 0
Uxbridge D | MA | 0 | 0 | 0 |  | 0 | 0
West Bridgewater A&B | MA | 0 | 0 | 0 |  | 0 | 0
Sutton A | MA | 0 | 0 | 0 |  | 0 | 0
North Adams A | MA | 0 | 0 | 0 |  | 0 | 0
North Adams B | MA | 0 | 0 | 0 |  | 0 | 0
Clarksburg A | MA | 0 | 0 | 0 |  | 0 | 0
Swansea B | MA | 0 | 0 | 0 |  | 0 | 0
Wareham 2 | MA | 0 | 0 | 0 |  | 0 | 0
Kingston 1 KB | MA | 0 | 0 | 0 |  | 0 | 0
Kingston 2 KB | MA | 0 | 0 | 0 |  | 0 | 0
Holliston B | MA | 0 | 0 | 0 |  | 0 | 0
Fairhaven C | MA | 0 | 0 | 0 |  | 0 | 0
Plympton A-2 | MA | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
MN8 KEF |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Williamsburg A | MA | 0 | 0 | 0 |  | 0 | 0
Orange A KB | MA | 0 | 0 | 0 |  | 0 | 0
Goshen A | MA | 0 | 0 | 0 |  | 0 | 0
Phillipston A KB | MA | 0 | 0 | 0 |  | 0 | 0
Uxbridge D | MA | 0 | 0 | 0 |  | 0 | 0
West Bridgewater A&B | MA | 0 | 0 | 0 |  | 0 | 0
Sutton A | MA | 0 | 0 | 0 |  | 0 | 0
North Adams A | MA | 0 | 0 | 0 |  | 0 | 0
North Adams B | MA | 0 | 0 | 0 |  | 0 | 0
Clarksburg A | MA | 0 | 0 | 0 |  | 0 | 0
Swansea B | MA | 0 | 0 | 0 |  | 0 | 0
Wareham 2 | MA | 0 | 0 | 0 |  | 0 | 0
Kingston 1 KB | MA | 0 | 0 | 0 |  | 0 | 0
Kingston 2 KB | MA | 0 | 0 | 0 |  | 0 | 0
Holliston B | MA | 0 | 0 | 0 |  | 0 | 0
Fairhaven C | MA | 0 | 0 | 0 |  | 0 | 0
Plympton A-2 | MA | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
MN8 KEF |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Williamsburg A | MA | 0 | 0 | 0 |  | 0 | 0
Orange A KB | MA | 0 | 0 | 0 |  | 0 | 0
Goshen A | MA | 0 | 0 | 0 |  | 0 | 0
Phillipston A KB | MA | 0 | 0 | 0 |  | 0 | 0
Uxbridge D | MA | 0 | 0 | 0 |  | 0 | 0
West Bridgewater A&B | MA | 0 | 0 | 0 |  | 0 | 0
Sutton A | MA | 0 | 0 | 0 |  | 0 | 0
North Adams A | MA | 0 | 0 | 0 |  | 0 | 0
North Adams B | MA | 0 | 0 | 0 |  | 0 | 0
Clarksburg A | MA | 0 | 0 | 0 |  | 0 | 0
Swansea B | MA | 0 | 0 | 0 |  | 0 | 0
Wareham 2 | MA | 0 | 0 | 0 |  | 0 | 0
Kingston 1 KB | MA | 0 | 0 | 0 |  | 0 | 0
Kingston 2 KB | MA | 0 | 0 | 0 |  | 0 | 0
Holliston B | MA | 0 | 0 | 0 |  | 0 | 0
Fairhaven C | MA | 0 | 0 | 0 |  | 0 | 0
Plympton A-2 | MA | 0 | 0 | 0 |  | 0 | 0

## Jan
MN8 KEF |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1276010.8373 | 1821502.574 | -545491.7367 | -29.95% | 1592252.09 | -316241.2527 | -19.86%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | 60069.5544 | 103795.4 | -43725.8456 | -42.13% | 95772.53 | -35702.9756 | -37.28% | 1.Low generation due to weather/snow.
Orange A KB | MA | 64320.283 | 86329.8 | -22009.517 | -25.49% | 78506.72 | -14186.437 | -18.07% | 1.Low generation due to weather/snow.
Goshen A | MA | 49163 | 93145.65 | -43982.65 | -47.22% | 45346.04 | 3816.96 | 8.417% | 1.Inverter 3.15 tripped offline at 02:00PM on 01/30 due to Arc warning key stop later self resolved at 07:00AM on 01/31. | 1.SR096163
Phillipston A KB | MA | 52361 | 133149.1 | -80788.1 | -60.67% | 48584.34 | 3776.66 | 7.773% | 1.Low generation due to weather/snow.
Uxbridge D | MA | 79311 | 118820.9 | -39509.9 | -33.25% | 102742.7 | -23431.7 | -22.81% | 1.Low generation due to weather/snow.
West Bridgewater A&B | MA | 140442 | 203218.3 | -62776.3 | -30.89% | 168220.8 | -27778.8 | -16.51% | 1.Inverter 1.03 has been RMA'd and offline since 12/18, and was brought back online at 2:45 PM on 01/27 by a technician after replacing the RMA'd inverter with a new inverter. 2.Inverter 5.04 has been RMA'd, and the inverter is currently operating with a string down. | 1.SR094920 2.SR094966 | SR094966
Sutton A | MA | 54236 | 92857.71 | -38621.71 | -41.59% | 92964.7 | -38728.7 | -41.66% | 1.Low generation due to weather/snow.
North Adams A | MA | 61430 | 85432.94 | -24002.94 | -28.1% | 97969.54 | -36539.54 | -37.3% | 1.Low generation due to weather/snow.
North Adams B | MA | 45389 | 3439.174 | 41949.826 | 1220% | 97969.54 | -52580.54 | -53.67% | 1.Weather station stopped communicating since 07/16/24, and the technician brought it back online at 12:45 PM on 01/30 by replacing the integrated weather station with an ambient temperature sensor by connecting to power logger port 1 and power logger port 2 is being RMA'd. | 1.SR087828
Clarksburg A | MA | 33591 | 74718.88 | -41127.88 | -55.04% | 97524.52 | -63933.52 | -65.56%
Swansea B | MA | 94569 | 125325.5 | -30756.5 | -24.54% | 51394 | 43175 | 84.01% | 1.Inverter 1.5 was offline and being RMA'd since 11/05/2024, and was brought back online at 02:00PM on 01/09/2025 by a technician after being replaced with a new inverter. | 1.SR092911
Wareham 2 | MA | 87644 | 97399.22 | -9755.22 | -10.02% | 102713.9 | -15069.9 | -14.67% | 1.Inverter 2.11 tripped offline at 09:45 AM on 01/08 due to an ARC Protection fault. A technician later cleared the fault and brought it back online at 09:15 AM on 01/09. 2.Site tripped offline at 06:00AM on 01/18 due to utility outage and back online at 12:15PM on 01/18. | 1.SR095394 2.SR095692 | SR095692
Kingston 1 KB | MA | 71770 | 101770 | -30000 | -29.48% | 78160.59 | -6390.59 | -8.176% | 1.Inverter 2.5 tripped offline on 01/01 due to 'Insulation Resistance Low - Isolation Error' and later back online at 10:28 AM on 01/02. | 1. SR095225
Kingston 2 KB | MA | 57696 | 63140.3 | -5444.3 | -8.623% | 62736.91 | -5040.91 | -8.035%
Holliston B | MA | 61173 | 103746 | -42573 | -41.04% | 97654.44 | -36481.44 | -37.36% | 1.Inverters 17, 19, 14, 27, 11, 15, 25, 26, 9, 20, 24 & 18 are underperforming approximately 44KW down due to shading. | 1.SR094409
Fairhaven C | MA | 176084 | 223072.8 | -46988.8 | -21.06% | 175840.8 | 243.2 | 0.1383% | 1.Inverter 8 was offline on 01/03, 01/05, 01/06, 01/08, 01/11 and 01/15 due to Bus sum high fault and technician stated that inverter should be RMA'D from 01/16. 2.Inverter 10 was being RMA'd from 11/04/24 and was offline on 01/03, 01/08, 01/14 due to bus sum high fault and on 01/16 technician checked- in and replaced RMA'd inverter with New stock, voltages tested good and production was restored. 3.Inverter 19 has not communicating since 11/19/24, production cannot be confirmed at meter. On 01/15 technician checked in and stated that inverter was dropped offline due to a thermal event within the powerhead and communication board is being RMA'd and on 01/16, technician replaced faulty communications board and get the inverter to begin communicating again via the DAS platform. | 1.SR088896 2.SR092913 3.SR093031 | SR092913 | SR093031
Plympton A-2 | MA | 86762 | 112140.9 | -25378.9 | -22.63% | 98150.02 | -11388.02 | -11.6% | 1.Site tripped offline at 10:15AM due to SEL relay open and back online at 10:30AM after remote reset on attempted on 01/02. 2.Inverter 1 was offline due to hardware overcurrent fault following brief site outage from 10:15AM to 10:30AM on 01/02 where the site was closed remotely and on 01/03 inverter has self-resolved. | 1.SR095226 2.SR095230 | SR095230

## Feb
MN8 KEF |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 380289.2267 | 686946.94 | -306657.7133 | -44.64% | 1950175.32 | -1569886.0933 | -80.5%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | 11359.8053 | 45602.05 | -34242.2447 | -75.09% | 113295.5 | -101935.6947 | -89.97% | 1. Low generation due to weather/snow.
Orange A KB | MA | 26979.4213 | 33060.18 | -6080.7587 | -18.39% | 95220.09 | -68240.6687 | -71.67% | 1. Low generation due to weather/snow.
Goshen A | MA | 11990 | 40468.16 | -28478.16 | -70.37% | 59166.09 | -47176.09 | -79.74% | 1. The site tripped offline at 15:45 on 02/04. The technician found that the main breaker was open and reset it. The site came back online on 02/05. | 1. SR096304
Phillipston A KB | MA | 9486 | 53178.43 | -43692.43 | -82.16% | 68728.61 | -59242.61 | -86.2% | 1. Site tripped offline at 17:02 on 02/03. VBZ voltages dropped from 8159 to 7033. Technician found Grounding Transformer breaker tripped, preventing the SEL recloser from closing. After resetting it and verifying balanced voltages, the recloser was closed, and the site resumed to its normal operation on 02/04. | 1. SR096266
Uxbridge D | MA | 29879 | 39532.16 | -9653.16 | -24.42% | 124606.4 | -94727.4 | -76.02% | 1. Low generation due to weather/snow.
West Bridgewater A&B | MA | 47142.5 | 73619.01 | -26476.51 | -35.96% | 202433.4 | -155290.9 | -76.71% | 1. Inverter 5.04 didn't started for poduction on 12/06. Technican investigated and replaced MPPT but issue was exist. Inverter is being RMA'd. | 1. SR094966
Sutton A | MA | 20500 | 34659.41 | -14159.41 | -40.85% | 115103 | -94603 | -82.19% | 1. Low generation due to weather/snow.
North Adams A | MA | 10513 | 31406.9 | -20893.9 | -66.53% | 118790.6 | -108277.6 | -91.15% | 1. Low generation due to weather/snow.
North Adams B | MA | 9493 | 23511.77 | -14018.77 | -59.62% | 118790.6 | -109297.6 | -92.01% | 1. Low generation due to weather/snow.
Clarksburg A | MA | 15440 | 28796.76 | -13356.76 | -46.38% | 118250.8 | -102810.8 | -86.94% | 1. Low generation due to weather/snow.
Swansea B | MA | 29605 | 43590.89 | -13985.89 | -32.08% | 66457.91 | -36852.91 | -55.45% | 1. Low generation due to weather/snow.
Wareham 2 | MA | 23705.5 | 32346.86 | -8641.36 | -26.71% | 123377 | -99671.5 | -80.79% | 1. Low generation due to weather/snow.
Kingston 1 KB | MA | 21120 | 32984.26 | -11864.26 | -35.97% | 96761.99 | -75641.99 | -78.17% | 1. The site tripped offline at 4:27 AM and auto-reclosed. However, it tripped again at 11:25 AM and closed back at 12:15 on 02/13. | 1. SR096847
Kingston 2 KB | MA | 17378 | 20733.48 | -3355.48 | -16.18% | 77667.53 | -60289.53 | -77.63% | 1. Site tripped offline at 4:24AM on 02/13. Technican found the SEL recloser unresponsive and the Vista controller stuck cycling. The S&C Motor Switch Operator was preventing manual closure. After removing it, the Vista was manually closed, and SEL trip functions were verified. The site is operating safely but requires manual resets until the motor is replaced. | 1. SR096848
Holliston B | MA | 22815 | 35943.18 | -13128.18 | -36.52% | 120909.1 | -98094.1 | -81.13% | 1.Inverters 17, 19, 14, 27, 11, 15, 25, 26, 9, 20, 24 & 18 are underperforming approximately 44KW down due to shading. | 1. SR094409
Fairhaven C | MA | 47780 | 77092.31 | -29312.31 | -38.02% | 211024.7 | -163244.7 | -77.36% | 1. Technician was dispatched on 02/05 and 02/07 for inverter 8. Technicians replaced inverter 8, but startup faults persisted despite troubleshooting AC/DC voltages, ground faults, and wiring. Further tests failed to isolate the issue, and the problem was reassigned to a site outage. | 1. SR088896
Plympton A-2 | MA | 25103 | 40421.13 | -15318.13 | -37.9% | 119592 | -94489 | -79.01% | 1. Low generation due to weather/snow.

## Mar
MN8 KEF |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Apr
MN8 KEF |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | [7 empty] | 1. Inverter 1.3 tripped offline on 04/05 at 10:24 and back online at 14:17 | 1. SR083119
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## May
MN8 KEF |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Jun
MN8 KEF |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | [7 empty] | 1. Site was offline from 18:45 on 06/19 and back online at 22:15 on 06/19 | 1. SR086454
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Jul
MN8 KEF |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | [7 empty] | 1.Site tripped offline from 7/7 at 07:45 and back online on 7/9 at 13:15. 2.Site tripped offline from 15:30 to 16:00 on 7/24. | 1.SR087437 2.SR088137
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Aug
MN8 KEF |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | [7 empty] | 1.Site tripped offline on 08/08 at 18:45 and back online on 08/09 at 08:30 | 1.SR088809
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Sep
MN8 KEF |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Oct
MN8 KEF |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | [7 empty] | 1.Site tripped offline at 9:45 AM on 10/17 and back online at 15:00 PM. | 1.SR092241
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Nov
MN8 KEF |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | [7 empty] | 1.Inverter 3.5 (58%), Inverter 1.1 (78.6%), Inverter 3.4 (87%), Inverter 1.2 (89%), Inverter 1.4 (94%), Inverter 2.3 (94%), Inverter 3.3 (95%) are having large underperformance possibilly due to heavy seasonal shading | 1.SR093598
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Dec
MN8 KEF |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Williamsburg A | MA | [7 empty] | 1. Inverter 3.5 began late for production at 10:30AM. | 1. SR095173
Orange A KB | MA
Goshen A | MA
Phillipston A KB | MA
Uxbridge D | MA
West Bridgewater A&B | MA
Sutton A | MA
North Adams A | MA
North Adams B | MA
Clarksburg A | MA
Swansea B | MA
Wareham 2 | MA
Kingston 1 KB | MA
Kingston 2 KB | MA
Holliston B | MA
Fairhaven C | MA
Plympton A-2 | MA

## Sites
Portfolio: | MN8 KEF
Site DAS Name | Site | State | Update | DAS
MA-11-001 - Williamsburg A #1058 | Williamsburg A | MA | AEF | PowerTrack
MA-11-002 - Orange A KB | Orange A KB | MA | AEF | PowerTrack
MA-11-003 - Goshen A #1052 | Goshen A | MA | AEF | PowerTrack
MA-11-004 - Phillipston A KB | Phillipston A KB | MA | AEF | PowerTrack
MA-11-005 - Uxbridge D | Uxbridge D | MA | AEF | PowerTrack
MA-11-006 - West Bridgewater A&B #1063 | West Bridgewater A&B | MA | AEF | PowerTrack
MA-11-007 - Sutton A #1054 | Sutton A | MA | AEF | PowerTrack
MA-11-008 - North Adams A #1079 | North Adams A | MA | AEF | PowerTrack
MA-11-009 - North Adams B #1080 | North Adams B | MA | AEF | PowerTrack
MA-11-010 - Clarksburg A #1081 | Clarksburg A | MA | AEF | PowerTrack
MA-11-011 - Swansea B #1098 | Swansea B | MA | AEF | PowerTrack
MA-11-012 - Wareham 2 | Wareham 2 | MA | AEF | PowerTrack
MA-11-013 - Kingston 1 KB | Kingston 1 KB | MA | AEF | PowerTrack
MA-11-014 - Kingston 2 KB | Kingston 2 KB | MA | AEF | PowerTrack
MA-11-015 - Holliston B | Holliston B | MA | AEF | PowerTrack
MA-11-016 - Fairhaven C | Fairhaven C | MA | AEF | PowerTrack
MA-11-017 - Plympton A | Plympton A-2 | MA | AEF | PowerTrack