## Year to Date
Amergy Solar |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1063911.5 | 935580.221 | 128331.279 | 13.72% | 1181117.911 | -117206.411 | -9.923%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Farmingdale - Howell Ice Arena | NJ | 440284.2 | 447974.94 | -7690.74 | -1.717% | 558357.195 | -118072.995 | -21.15%
Mount Laurel - Igloo Ice Rink | NJ | 623627.3 | 487605.281 | 136022.019 | 27.9% | 622760.716 | 866.584 | 0.1392%

## 1st Qtr
Amergy Solar |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 330546.6 | 360979.011 | -30432.411 | -8.431% | 351260.761 | -20714.161 | -5.897%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Farmingdale - Howell Ice Arena | NJ | 136545.1 | 138174.27 | -1629.17 | -1.179% | 185557.845 | -49012.745 | -26.41%
Mount Laurel - Igloo Ice Rink | NJ | 194001.5 | 222804.741 | -28803.241 | -12.93% | 165702.916 | 28298.584 | 17.08%

## 2nd Qtr
Amergy Solar |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 524729.3 | 411049.59 | 113679.71 | 27.66% | 609183.7 | -84454.4 | -13.86%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Farmingdale - Howell Ice Arena | NJ | 217734.5 | 222436.1 | -4701.6 | -2.114% | 275917 | -58182.5 | -21.09%
Mount Laurel - Igloo Ice Rink | NJ | 306994.8 | 188613.49 | 118381.31 | 62.76% | 333266.7 | -26271.9 | -7.883%

## 3rd Qtr
Amergy Solar |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 208635.6 | 163551.62 | 45083.98 | 27.57% | 220673.45 | -12037.85 | -5.455%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Farmingdale - Howell Ice Arena | NJ | 86004.6 | 87364.57 | -1359.97 | -1.557% | 96882.35 | -10877.75 | -11.23%
Mount Laurel - Igloo Ice Rink | NJ | 122631 | 76187.05 | 46443.95 | 60.96% | 123791.1 | -1160.1 | -0.9371%

## 4th Qtr
Amergy Solar |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Farmingdale - Howell Ice Arena | NJ | 0 | 0 | 0 |  | 0 | 0
Mount Laurel - Igloo Ice Rink | NJ | 0 | 0 | 0 |  | 0 | 0

## Jan
Amergy Solar |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 62843.3 | 86823.505 | -23980.205 | -27.62% | 87326.428 | -24483.128 | -28.04%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ | 27760 | 30103.183 | -2343.183 | -7.784% | 49684.402 | -21924.402 | -44.13% | 1. Low generation due to snow/rain.
Mount Laurel - Igloo Ice Rink | NJ | 35083.3 | 56720.322 | -21637.022 | -38.15% | 37642.026 | -2558.726 | -6.798% | 1. Inverter 8 tripped offline at 12:1PM on 01/26 and self resolved and started for production at 7:45AM on 01/27. 2. Low generation due to snow/rain. | 1. SR095995

## Feb
Amergy Solar |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 101062.8 | 103326.061 | -2263.261 | -2.19% | 106702.659 | -5639.859 | -5.286%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ | 41249.4 | 40885.518 | 363.882 | 0.89% | 58474.985 | -17225.585 | -29.46% | 1. Low generation due to snow/rain.
Mount Laurel - Igloo Ice Rink | NJ | 59813.4 | 62440.543 | -2627.143 | -4.207% | 48227.674 | 11585.726 | 24.02%

## Mar
Amergy Solar |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 166640.5 | 170829.445 | -4188.945 | -2.452% | 157231.674 | 9408.826 | 5.984%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ | 67535.7 | 67185.569 | 350.131 | 0.5211% | 77398.458 | -9862.758 | -12.74% | 1. Considering the fluctuating irradiance and weather throughout the month, actual values is reporting lower than the forecasted values.
Mount Laurel - Igloo Ice Rink | NJ | 99104.8 | 103643.876 | -4539.076 | -4.379% | 79833.216 | 19271.584 | 24.14%

## Apr
Amergy Solar |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 167794.1 | 127938.35 | 39855.75 | 31.15% | 191379.95 | -23585.85 | -12.32%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ | 69895.1 | 70676.85 | -781.75 | -1.106% | 89306.95 | -19411.85 | -21.74% | 1. Inverter 2 is underperforming by 10KW down compared to peer inverter. | 1. SR100595
Mount Laurel - Igloo Ice Rink | NJ | 97899 | 57261.5 | 40637.5 | 70.97% | 102073 | -4174 | -4.089% | 1. Inverter 4 tripped offline at 14:45 on 04/08 and later self-resolved at 11:00 on 04/09. 2. Actual vs expected delta is showing 71% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1. SR099525

## May
Amergy Solar |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 169852.9 | 135384.81 | 34468.09 | 25.46% | 204867.79 | -35014.89 | -17.09%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ | 70707.3 | 72770.5 | -2063.2 | -2.835% | 91904.89 | -21197.59 | -23.06% | 1. Inverter 2 is underperforming by 10kW down compared to peer inverter. | 1. SR100595
Mount Laurel - Igloo Ice Rink | NJ | 99145.6 | 62614.31 | 36531.29 | 58.34% | 112962.9 | -13817.3 | -12.23% | 1. Actual vs expected delta is showing 58% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years).

## Jun
Amergy Solar |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 187082.3 | 147726.43 | 39355.87 | 26.64% | 212935.96 | -25853.66 | -12.14%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ | 77132.1 | 78988.75 | -1856.65 | -2.351% | 94705.16 | -17573.06 | -18.56% | 1. Inverter 2 is underperforming by 10kW down compared to peer inverter. | 1.SR100595
Mount Laurel - Igloo Ice Rink | NJ | 109950.2 | 68737.68 | 41212.52 | 59.96% | 118230.8 | -8280.6 | -7.004% | 1. Inverter 6 has tripped offline at 14:30 on 06/02 and reporting "Waiting for grid voltage > Installation failure grid connection and came back online at 13:45 on 06/04 2. Inverter 6 has tripped offline at 13:45 on 06/23 and came back online at 07:30 on 06/25 3. Actual vs expected delta is showing 60% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1.SR102313 2. SR103325 | SR103325

## Jul
Amergy Solar |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 208635.6 | 163551.62 | 45083.98 | 27.57% | 220673.45 | -12037.85 | -5.455%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ | 86004.6 | 87364.57 | -1359.97 | -1.557% | 96882.35 | -10877.75 | -11.23% | 1. Inverter 2 is underperforming by 10kW down compared to peer inverter. The quote was expired. | 1. SR100595
Mount Laurel - Igloo Ice Rink | NJ | 122631 | 76187.05 | 46443.95 | 60.96% | 123791.1 | -1160.1 | -0.9371% | 1. Inverter 6 tripped offline at 15:15 on 07/02 and back online at 8:15 on 07/04. and again inverter 6 was offline from 12:15 to 15:45 on 07/12. The inverter again went offline at 13:00 on 07/31 and remained offline. 2. Inverter 13 was offline from 13:30 to 16:00 on 07/09. 3. Actual vs expected delta is showing 60% due to expected energy recording low possibly due to data glitch (similar event observe last 2 years). | 1. SR103325 2. SR104216 | SR104216

## Aug
Amergy Solar |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ
Mount Laurel - Igloo Ice Rink | NJ

## Sep
Amergy Solar |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ
Mount Laurel - Igloo Ice Rink | NJ

## Oct
Amergy Solar |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ
Mount Laurel - Igloo Ice Rink | NJ

## Nov
Amergy Solar |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ
Mount Laurel - Igloo Ice Rink | NJ

## Dec
Amergy Solar |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Farmingdale - Howell Ice Arena | NJ
Mount Laurel - Igloo Ice Rink | NJ

## Sites
Portfolio: | Amergy Solar
Site DAS Name | Site | State | Update | DAS
Howell Ice Arena | Farmingdale - Howell Ice Arena | NJ | AEF | PowerTrack
Igloo | Mount Laurel - Igloo Ice Rink | NJ | AEF | PowerTrack