## Sites
Monthly Site Performance Summary
Account: | Ameresco
Report Period: | From 7/1/24 to 7/31/24
Sites: | Manually selected sites
Number of Sites: | 11
Generated on: | 8/7/25, 11:30 PM
Site Information | [7 empty] | Open Alerts | Current Month |  | Previous Month |  | Same Month Last Year |  | Previous Twelve Months
| Site Name | Site ID | Country | State | City | Installation Date | Peak Power (kWp) | Highest Alert Impact | kWh | kWh/kWp | kWh | kWh/kWp | kWh | kWh/kWp | kWh | kWh/kWp
1 | NBHA Adams st | 2484387 | United States | Massachusetts | New Bedford | 12/1/20 | 69.26 | 5 | 6,225.64 | 89.89 | 7,318.25 | 105.67 | 9,640.26 | 139.2 | 58,793.56 | 848.94
2 | NBHA Ben Rose | 2752799 | United States | Massachusetts | New Bedford | 3/3/22 | 152.43 | 2 | 19,144.65 | 125.6 | 23,061.14 | 151.3 | 17,161.94 | 112.59 | 160,883.9 | 1,055.5
3 | NBHA Brickenwood | 2747637 | United States | Massachusetts | New Bedford | 3/1/22 | 572.33 | 6 | 69,558.61 | 121.54 | 80,920.22 | 141.39 | 74,490.74 | 130.15 | 635,334 | 1,110.09
4 | NBHA Chaffee Fairfield | 1735612 | United States | Massachusetts | New Bedford | 7/29/20 | 49.4 | 2 | 6,265.36 | 126.83 | 7,248.28 | 146.73 | 6,718.82 | 136.01 | 58,126.1 | 1,176.64
5 | NBHA DeMedeiros | 2660184 | United States | Massachusetts | New Bedford | 1/10/22 | 64.35 | 2 | 7,465.85 | 116.02 | 5,376.11 | 83.54 | 9,314.72 | 144.75 | 57,419.31 | 892.3
6 | NBHA Dottin Place 1 | 1735791 | United States | Massachusetts | New Bedford | 7/29/20 | 88.4 | 2 | 10,209.74 | 115.49 | 11,945.24 | 135.13 | 11,576.45 | 130.96 | 93,252.06 | 1,054.89
7 | NBHA Hillside | 2331864 | United States | Massachusetts | New Bedford | 6/28/21 | 117 | 2 | 14,788.51 | 126.4 | 17,289.27 | 147.77 | 16,096.26 | 137.57 | 135,318.23 | 1,156.57
8 | NBHA Presidential | 2457881 | United States | Massachusetts | New Bedford | 9/12/21 | 468.65 | 6 | 46,524.71 | 99.27 | 54,714.36 | 116.75 | 46,582.98 | 99.4 | 427,209.6 | 911.57
9 | NBHA Satellite | 2597872 | United States | Massachusetts | New Bedford | 11/18/21 | 169 | 2 | 15,800.63 | 93.49 | 17,179.53 | 101.65 | 20,824.08 | 123.22 | 174,952.36 | 1,035.22
10 | NBHA Shawmut Village | 2382372 | United States | Massachusetts | New Bedford | 10/21/20 | 443.63 | 2 | 35,457.75 | 79.93 | 51,736.77 | 116.62 | 53,103.41 | 119.7 | 437,383.75 | 985.93
11 | NBHA Westlawn | 2753485 | United States | Massachusetts | New Bedford | 3/3/22 | 267.8 | 2 | 28,611.36 | 106.84 | 36,585.88 | 136.62 | 35,485 | 132.51 | 277,262.62 | 1,035.33
Total | [6 empty] | 2,462.23 |  | 260,052.81 |  | 313,375.04 |  | 300,994.66 |  | 2,515,935.48

## Service request
Customer | Asset | Site Equipment | kW Down | Date | Description | Account Manager | Pending | Priority | Summary | Request | D365 Project
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 42 Yale - Inverter 39 | 7.6 | 2025-08-07 13:07 | 08/07/25 - Inverter 39 tripped offline at 11am on 7/28. Reporting internal error. | Amanda Harper |  | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR105843
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Dottin Place 1 - Amanda Ave Bldg 7 (82) - Inverter 9 | 10 | 2025-07-30 14:08 | 07/30/25 - Inverter 9 stopped communicating 7/21. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR105365
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 132 Hathaway - Inverter 8 | 7.5 | 2025-07-30 13:51 | 07/30/25 - Inverter 8 stopped communicating 7/25 | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR105362
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Satellite - 100 Libra Dr - Inverter 12 | 5 | 2025-07-09 12:19 | 07/09/25 - Inverter 12 stopped communicating 7/3. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR104196
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Satellite - 65 Saturn Dr - Inverter 4 | 5 | 2025-07-02 13:11 | 07/07/25 - Issue still exists. 07/02/25 - Inverter 4 stopped communicating 6/25. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR103916
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Satellite - 106 Aries Dr - Inverter 14 | 6 | 2025-06-26 13:10 | 07/07/25 - Issue still exists. 06/26/25 - Inverter 14 stopped communicating 6/15. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR103606
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Satellite - 85 Libra Dr - Inverter 9 | 6 | 2025-06-26 13:10 | 07/07/25 - Issue still exists. 06/26/25 - Inverter 9 stopped communicating 6/15. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR103605
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 5 - Inverter 3 | 8 | 2025-06-26 12:49 | 07/07/25 - Issue still exists. 06/26/25 - Inverter 3 stopped communicating 6/15. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR103603
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 219 Harvard - Inverter 53 | 5 | 2025-06-16 12:31 | 07/07/25 - Issue still exists. 06/16/25 - Inverter 53 stopped communicating 6/8. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR103023
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 159 Gay Head CT - Inverter 44 | 8 | 2025-06-09 15:29 | 07/07/25 - Issue still exists. 06/09/25 - Inverter 44 stopped communicating 6/1. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR102722
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 141 Dakota CT - Inverter 43 | 6 | 2025-06-09 14:24 | 07/07/25 - Issue still exists. 06/09/25 - Inverter 43 stopped communicating 6/1. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR102708
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 55 Cherokee CT - Inverter 39 | 5 | 2025-06-09 14:22 | 07/07/25 - Issue still exists. 06/09/25 - Inverter 39 stopped communicating. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR102707
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 59 Apache CT - Inverter 32 | 5 | 2025-06-09 14:18 | 07/07/25 - Issue still exists. 06/09/25 - Inverter 32 stopped communicating 6/1. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR102706
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 20 Shawnee CT - Inverter 4 | 5 | 2025-06-09 12:53 | 07/07/25 - Issue still exists. 06/09/25 - Inverter 4 stopped communicating 6/1. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR102701
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 35 Yale - Inverter 58 | 8 | 2025-06-09 12:46 | 07/07/25 - Issue still exists. 06/10/25 - Still an issue. 06/09/25 - Inverter 58 stopped communicating on 6/3. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR102700
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 61 Apache CT - Inverter 50 | 5 | 2025-06-03 12:48 | 07/07/25 - Issue still exists. 06/04/25 - Still an issue. 06/03/25 - Inverter 50 stopped communicating 5/26. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR102390
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Chaffee/Fairfield - 975 Fairfield St 1E - Inverter 3 | 6 | 2025-05-19 14:54 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/19/25 - Inverter 3 tripped offline 5/12. Reporting internal error. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR101683
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 13 Yale - Inverter 48 | 5 | 2025-05-13 14:39 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/13/25 - Inverter 48 stopped communicating 5/10. Production not confirmed. Reporting Power Limitation. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR101400
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 83 Pawnee CT - Inverter 26 | 5 | 2025-04-28 13:28 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists 05/09/25 - Issue still exists 04/28/25 - Inverter 26 stopped communicating 4/22. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR100557
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 13 - Inverter 17 | 7 | 2025-04-28 13:15 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/28/25 - Inverter 17 stopped communicating 4/23. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR100543
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Satellite - 2 Gemini Dr - Inverter 24 | 5 | 2025-03-19 14:58 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25-Issue still exists 03/19/25 Inverter 24 stopped communicating on 3/16. Production not confirmed. Reporting AC voltage surge. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR098772
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 185 Harvard - Inverter 28 | 6 | 2025-03-11 11:49 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25- Issue still exists 04/09/25- Issue still exists 03/11/25 - Inverter 28 stopped communicating 2/28. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR098386
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 30 - Inverter 6 | 4 | 2025-02-28 14:27 | 07/07/25 - Issue still exists. 06/26/25 - Inverter 6 stopped communicating on 6/15. Production not confirmed. 03/31/25 - Inverter resumed production on 3/17. 03/17/25 - Inverter tripped offline on 3/13, reporting locked_inverter_arc_detected. 03/05/25 - Inverter is back online on 03/05. 02/28/25 - Inverter tripped offline on 2/25 reporting locked_inverter_arc_detected. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR097923
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 235 Harvard - Inverter 56 | 7 | 2025-02-25 13:06 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25- Issue still exists. 04/09/25- Issue still exists. 03/05/25 - Issue still exists. 02/25/25 - Inverter 56 stopped communicating 2/19. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR097766
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Dottin Place 1 - Amanda Ave Bldg 12 (92) - Inverter 6 | 5 | 2025-02-18 14:46 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 -Issue still exists. 03/05/25 -Issue still exists. 02/18/25 Inverter 6 stopped communicating 2/10/25, production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco - Inverter Troubleshooting | SR097346
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 21 - Inverter 11 | 7 | 2025-01-02 14:55 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25- Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/02/25 Inverter 11 stopped communicating 12/24. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR095246 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 23 - Inverter 10 | 7 | 2025-01-02 14:53 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists 01/02/25 Inverter 10 stopped communicating 12/24. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco Production Not Confirmed - Site Outage | SR095244 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Adams St - 14 Adams St - Inverter 2 | 14.4 | 2024-11-17 12:32 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists 01/08/25 - Issue still exists 12/02/24 - Issue still exists 11/17/24 Inverter 2 tripped offline 11/5 | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR093350
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Adams St - 14 Adams St - Inverter 1 | 14.4 | 2024-11-17 12:31 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists 01/08/25 - Issue still exists. 12/02/24 - Issue still exists. 11/17/24 Inverter 1 tripped offline 11/5 | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR093349
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 113 Mashpee CT - Inverter 45 | 7 | 2024-10-29 13:34 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists 01/08/25 - Issue still exists. 10/29/24 Inv 45 stopped communicating 10/22. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR092738
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Presidential - 28 Monroe Dr Bldg 16 - Inverter 17 | 9 | 2024-10-16 13:04 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists 01/08/25 - Issue still exists. 10/16/24 Inverter 17 tripped offline at 4pm on 10/8. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR092211
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 150 Hathaway - Inverter 5 | 7 | 2024-10-15 13:09 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - issue still exists. 10/15/24 Inverter 5 stopped communicating 10/7. Production not confirmed | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR092164
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 99 Navaho CT - Inverter 24 | 6 | 2024-08-12 12:41 | 07/07/25 - Issue still exists. 06/26/25 - Inverter 24 stopped communicating 06/18/25. Production not confirmed. 04/10/25 - Inverter 24 resumed communicating 04/05/25. 03/31/25 - Inverter 24 stopped communicating 03/23/25. Production not confirmed. 08/12/24 - Inverter 24 stopped communicating 08/05/24. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR088926
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 109 Navaho CT - Inverter 40 | 5 | 2024-07-26 15:15 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 06/03/25 - Inverter 40 stopped communicating 5/21. Production not confirmed. 05/09/25 - Inverter 40 back online on 05/07. 04/09/25 - Issue still exists 03/31/25 - Inverter 40 stopped communicating 3/18, production not confirmed. 01/24/25 - Inverter resumed communication 1/22. 01/08/25 - Still an issue. 07/26/24 - Inverter 40 stopped communicating on 7/19. Production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR088285
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 22 - Inverter 12 | 7 | 2024-07-16 13:22 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 7/16/24 Inverter 12 stopped communicating on 7/6/24. Production is not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR087778
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 131 Dakota CT - Inverter 38 | 7 | 2024-07-15 15:29 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 7/15/24 Inverter 38 stopped communicating on 7/6/24, production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR087728
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 155 Gay Head CT - Inverter 33 | 7 | 2024-07-15 15:27 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 7/15/24 Inverter 33 stopped communicating on 7/6/24, production not confirmed. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR087727
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 7 - Inverter 4 | 7 | 2024-07-02 13:00 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - issue still exists. 7/2/24: Inverter 4 stopped communicating on 5/2, cannot confirm production. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR087282
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Satellite - 83 Libra Dr - Inverter 8 | 6 | 2024-06-27 14:37 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/19/24 - Inv 8 has stopped communicating 3/15. Possibly offline. 06/27/24 - Inv 8 is not communicating, possibly offline. Last data 5/12. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR087049
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 58 Yale - Inverter 49 | 5 | 2024-06-03 12:37 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 6/3/24 - inverter 49 stopped communicating on 5/25/24; possibly offline. | Amanda Harper | EPC Completion | PV Monitoring - Minor | Ameresco UM - Inverter Troubleshooting | SR085484 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring |  | 23.4 | 2024-05-17 12:41 | 08/06/25 - Inverter 18 resumed communicating on 8/1 at 8pm. Inverter 27 still not communicating. 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/09/25 - Issue still exists. 01/08/25 - Issue still exists. 5/17/24 - Presidential inverters 18, 27 have stopped communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR084807 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring |  | 21.8 | 2024-05-11 13:39 | 07/08/25 - Issue still exists. 06/05/25 - Inverter 5 resolved & Inverter 4 still an issue. 05/09/25 - Issue still exists. 04/09/25 - Inverter 4,5 still an issue. 03/05/25 - Issue still exists. 02/09/25 - Inverter 4 still an issue. 01/08/25 - Inverters 6,15 and 16 resolved & Inverter 4 still an issue. 06/03/24 - invs 15 and 16 regained comms, invs 4 and 6 still have no comms. 05/11/24 - Westlawn inverters 4, 6, 15, 16 stopped communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure | SR084580 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 105 Navaho CT - Inverter 46 | 5 | 2024-04-19 12:51 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 4/19 - Inverter 46 is not communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR083627 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 88 Malden - Inverter 27 | 7 - inverter comms ? | 2024-03-21 12:45 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 12/02/24 - Issue still exists. 11/7/24 - Inverter 27 stopped communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR082331 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Presidential - 310 Mt-Pleasant St Bldg 2 - Inverter 1 | 14.4 | 2024-03-04 12:57 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Still an issue. 01/08/25 - Inverter 1 is still in offline. 3/4 - Inverter 1 is offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR081556 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 240 Harvard - Inverter 46 | 6 | 2024-03-04 12:55 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 3/4 - Inverter 46 at Brickenwood is offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR081555 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 33 - Inverter 26 | 3 - Inverter comms ? | 2024-03-01 14:54 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 12/01/24 - Inverter last communicated 10/03/24. 03/01/24 - Inverter 26 is not communicating. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR081504 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Westlawn - 197 Liberty St Bldg 45 - Inverter 23 | 10 | 2024-02-20 14:04 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 2/20/24 - Inverter 23 stopped communicating; cannot confirm production. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure / Production Not Confirmed | SR081129 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Adams St - 14 Adams St - Inverter 3 | 14.4 | 2023-12-31 04:44 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 12/02/24 - Inverter 3 is offline (re-occurring issue). 12/31/23 - Inverter 3 is offline and reporting "Isolation Fault". | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR079845 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 21 Mohawk CT - Inverter 8 | 7 - inverter comms ? | 2023-11-07 12:49 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 12/02/24 - Inverter 8 last communicated 7/6/24 11/07/23 - Inverter 8 stopped communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR078119 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 111 Mashpee CT - Inverter 49 | 6 | 2023-10-17 03:39 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 10/17/23 - Inverter 49 is not communicating from 07/09, possibly offline | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR077517 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Satellite - 90 Libra Dr - Inverter 11 | 6 | 2023-10-05 14:16 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists. 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 10/5/23 - Inverter 11 stopped communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure | SR077287 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 161 Gay Head CT - Inverter 54 | 6 - ? | 2023-09-08 12:40 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 7/3/2024 - Inverter stopped communicating 6/26/24 10/17/2023 - Inverter is communicating from 10/03 9/8 - Inverter stopped communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR075876 | 1006999.001
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Adams St - 14 Adams St - Inverter 4 | 14.4 | 2023-08-31 14:53 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 -Issue still exists 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 12/02/24 - Inverter is offline (re-occurring issue). 10/16/23 - Inverter is still offline. 08/31/23 - Inverter 4 tripped offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR075642 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 121 Mashpee CT - Inverter 25 | 7.6 | 2023-08-09 12:46 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/2025 - Issue still exists. 01/08/2025 - Issue still exists. 10/17/2023 - Inverter is still not reporting, possibly offline 8/9 - Inverter 25 stopped communicating. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR074887 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 45 Cherokee CT - Inverter 37 | 6 | 2023-07-13 12:37 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/2025 - Issue still exists. 01/08/2025 - Issue still exists. 10/17/2023 - Inverter is still not communicating from 07/10, possibly offline 7/13 - Inverter 37 stopped communicating, possibly offline. S/N: 73086310-EE | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Communications Failure | SR073825 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 190 Harvard - Inverter 35 | 10 | 2023-07-11 13:59 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 - Issue still exists 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 10/17/23 - Inverter 35 is still offline 07/11/23 - Inverter 35 tripped offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR073743 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Brickenwood - 240 Harvard - Inverter 46 | 7.6 | 2023-05-22 14:23 | 07/07/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 -Issue still exists 04/09/25 -Issue still exists 03/05/25 - Issue still exists. 02/08/25 - Issue still exists. 01/08/25 - Issue still exists. 05/22/23 - Inverter 46 tripped offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR071782 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 63 Apache CT - Inverter 42 | 5 | 2023-05-09 14:11 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 - Issue still exists 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/2025 - Issue still exists. 01/08/2025 - Issue still exists. 10/17/2023 - Inverter is still not communicating from 05/07, possibly offline 5/9 - Inverter 42 stopped communicating, possibly offline. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR071467 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 157 Gay Head CT - Inverter 51 | 7 | 2023-04-25 14:19 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 -Issue still exists 04/09/25 -ssue still exists 03/05/25 - Issue still exists. 02/08/2025 - Issue still exists. 01/08/2025 - Issue still exists. 4/25 - Shawmut Village inverter 51 no comms today. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR071089
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Shawmut Village - 67 Apache CT - Inverter 48 | 7.6 | 2023-04-21 12:34 | 07/07/25 - Issue still exists. 06/04/25 - Issue still exists. 05/09/25 -Issue still exists 04/09/25 - Issue still exists 03/05/25 - Issue still exists. 02/08/2025 - Issue still exists. 01/08/2025 - Issue still exists. 10/17/2023 - Inverter is still not communicating from 04/11, possibly offline 4/21 - Inverter 48 stopped communicating. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR070992 | 1006999
New Bedford Housing Authority | MA: New Bedford – HA Monitoring | Presidential - 119 Fillmore St Bldg 9 - Inverter 21 | 9 - approximately | 2023-01-03 12:33 | 07/08/25 - Issue still exists. 06/05/25 - Issue still exists. 05/09/25 -Issue still exists 04/09/25 - Issue still exists. 03/05/25 - Issue still exists. 02/08/25 - Issue still exists 01/08/25 - Issue still exists 10/17/23 - Issue still exists 04/03/23 - Issue still exists. 01/03/23 - Inverter 21 lost communications on 8/23/22. | Amanda Harper | Pending Subcontractor Completion | PV-Monitoring-ROC | Ameresco UM - Inverter Troubleshooting | SR068143 | 1006999
Total