## Year to Date
Silicon Ranch |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 25096475.68 | 16114847 | 8981628.68 | 55.74% | 29580593.091 | -4484117.411 | -15.16%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Iron Mountain - Windsor | CT | 182137 | 181378 | 759 | 0.4185% | 191986.83 | -9849.83 | -5.13% | -9849.83
Kohls - Auburn | NY | 184737 | 183453 | 1284 | 0.6999% | 206463.82 | -21726.82 | -10.52% | -21726.82
Kohls - Bensalem | PA | 97605 | 93259 | 4346 | 4.66% | 215033.4 | -117428.4 | -54.61% | -117428.4
Kohls - Brick | NJ | 259913 | 252555 | 7358 | 2.913% | 257957.77 | 1955.23 | 0.758% | 1955.23
Kohls - Buffalo | NY | 195119 | 0 | 195119 |  | 252940.17 | -57821.17 | -22.86% | -57821.17
Kohls - Canton | CT | 88302 | 87340 | 962 | 1.101% | 85582.5 | 2719.5 | 3.178% | 2719.5
Kohls - East Amherst | NY | 100710 | 99444 | 1266 | 1.273% | 229743.65 | -129033.65 | -56.16% | -129033.65
Kohls - East Brunswick | NJ | 272020 | 265508 | 6512 | 2.453% | 333976.49 | -61956.49 | -18.55% | -61956.49
Kohls - Edgewood | MD | 1455431 | 1437422 | 18009 | 1.253% | 1780152.44 | -324721.44 | -18.24% | -324721.44
Kohls - Granite Run | PA | 207585 | 205741 | 1844 | 0.8963% | 214421.27 | -6836.27 | -3.188% | -6836.27
Kohls - Greece | NY | 178022 | 176442 | 1580 | 0.8955% | 242869.23 | -64847.23 | -26.7% | -64847.23
Kohls - Hanover | PA | 233646 | 232073 | 1573 | 0.6778% | 242148.21 | -8502.21 | -3.511% | -8502.21
Kohls - Horsehead | NY | 170772 | 132155 | 38617 | 29.22% | 191051.94 | -20279.94 | -10.61% | -20279.94
Kohls - Hudson | NY | 198812 | 138345 | 60467 | 43.71% | 209685.03 | -10873.03 | -5.185% | -10873.03
Kohls - Ithaca | NY | 172812 | 171726 | 1086 | 0.6324% | 215424.01 | -42612.01 | -19.78% | -42612.01
Kohls - Kingston | NY | 255433 | 241006 | 14427 | 5.986% | 324362.5 | -68929.5 | -21.25% | -68929.5
Kohls - Mechanicsburg | PA | 215759 | 213936 | 1823 | 0.8521% | 281110.85 | -65351.85 | -23.25% | -65351.85
Kohls - Middletown | NJ | 240073 | 234211 | 5862 | 2.503% | 392460.16 | -152387.16 | -38.83% | -152387.16
Kohls - North Amherst | NY | 100313 | 99916 | 397 | 0.3973% | 213915.21 | -113602.21 | -53.11% | -113602.21
Kohls - Staten Island | NY | 184824 | 0 | 184824 |  | 235496.46 | -46160.84 | -19.6% | -50672.46
Kohls - Warminster | PA | 272866 | 264479 | 8387 | 3.171% | 255185.1 | 9720.87 | 3.809% | 17680.9
Kohls - Waterbury | CT | 209660 | 207471 | 2189 | 1.055% | 225317.21 | -15657.21 | -6.949% | -15657.21
Mojave Water Agency - Headquarters | CA | 247735 | 236308 | 11427 | 4.836% | 329554.37 | 1314.49 | 0.3989% | -81819.37
CSU - Bakersfield | CA | 1018342 | 1027920 | -9578 | -0.9318% | 961965.75 | 56376.25 | 5.861% | 56376.25
Greenfield USD - Fairfield ES | CA | 71659 | 70613 | 1046 | 1.481% | 109873.03 | -20019.26 | -18.22% | -38214.03
Greenfield USD - Granite Point ES | CA | 234475 | 232105 | 2370 | 1.021% | 242067.55 | -7592.55 | -3.137% | -7592.55
Greenfield USD - Greenfield MS | CA | 135452 | 119338 | 16114 | 13.5% | 166974.971 | -21421.409 | -12.83% | -31522.971
Greenfield USD - Horizon ES | CA | 213262 | 211559 | 1703 | 0.805% | 250550.25 | -37288.25 | -14.88% | -37288.25
Greenfield USD - McKee MS | CA | 117794 | 116951 | 843 | 0.7208% | 147803.99 | -35258.4 | -23.85% | -30009.99
Greenfield USD - Plantation ES | CA | 113038 | 112738 | 300 | 0.2661% | 109508.41 | 3529.59 | 3.223% | 3529.59
Greenfield USD - Planz ES | CA | 44174 | 43927 | 247 | 0.5623% | 141951.55 | -79660.91 | -56.12% | -97777.55
Greenfield USD - Raffaello Palla ES | CA | 213899 | 211201 | 2698 | 1.277% | 270913.79 | -57014.79 | -21.05% | -57014.79
Greenfield USD - Valle Verde ES | CA | 277234 | 275871 | 1363 | 0.4941% | 234277.39 | 24040.3 | 10.26% | 42956.61
Greenfield USD - W.A. Kendrick ES | CA | 9316 | 0 | 9316 |  | 97619.21 | -88303.21 | -90.46% | -88303.21
Muroc Joint USD - Boron HS | CA | 0 | 0 | 0 |  | 217056.15 | -239294.02 | -110.2% | -217056.15
Muroc Joint USD - W. Boron ES | CA | 88638 | 88453 | 185 | 0.2092% | 88349.36 | 288.64 | 0.3267% | 288.64
Colusa - WTP | CA | 0 | 0 | 0 |  | 441658.79 | -334687.35 | -75.78% | -441658.79
CDCR-North Kern State Prision | CA | 737884 | 734471 | 3413 | 0.4647% | 1328927.78 | -591043.78 | -44.48% | -591043.78
Muroc Joint USD - District Office | CA | 48848 | 60095 | -11247 | -18.72% | 72310.63 | -13429.75 | -18.57% | -23462.63
Whole Foods - Manhattan Beach | CA | 105279 | 105593 | -314 | -0.2974% | 138017 | -32738 | -23.72% | -32738
Pioneer USD - Frontier ES | CA | 175596 | 0 | 175596 |  | 214874.04 | -38487.84 | -17.91% | -39278.04
Pioneer USD - Pioneer ES | CA | 85441 | 0 | 85441 |  | 218084.3 | -132643.3 | -60.82% | -132643.3
Pioneer USD - Pioneer MS | CA | 295900 | 0 | 295900 |  | 310459.07 | 3133.44 | 1.009% | -14559.07
Kingsburg Joint UHSD - Kingsburg HS | CA | 346330 | 273862 | 72468 | 26.46% | 503734.46 | -157404.46 | -31.25% | -157404.46
CADRB | CA | 0 | 0 | 0 |  | 4842210.78 | -5127976 | -105.9% | -4842210.78
CDCR-CA State Prison LA County | CA | 1760774 | 1747634 | 13140 | 0.7519% | 3149867.93 | -1389093.93 | -44.1% | -1389093.93
Central USD Akers ES | CA | 256492 | 38998 | 217494 | 557.7% | 227290.19 | 22140.05 | 9.741% | 29201.81
CUSD - District Office | CA | 140479 | 139775 | 704 | 0.5037% | 194547.68 | -54068.68 | -27.79% | -54068.68
Parlier - WTP | CA | 246421 | 290601 | -44180 | -15.2% | 411558.94 | -194395.36 | -47.23% | -165137.94
Snowline SD - Quail Valley MS | CA | 255877 | 249894 | 5983 | 2.394% | 277815.42 | -21938.42 | -7.897% | -21938.42
Snowline SD - Serrano HS - Middle Lot | CA | 162018 | 212740 | -50722 | -23.84% | 255973.9 | -116819.67 | -45.64% | -93955.9
Snowline SD - Pinon Hills ES | CA | 83152 | 83821 | -669 | -0.7981% | 156269.02 | -73117.02 | -46.79% | -73117.02
Ramona - Santa Maria WTP | CA | 456456 | 456719 | -263 | -0.05758% | 472789.58 | -62584.3 | -13.24% | -16333.58
Kohls - Redding | CA | 190294 | 222 | 190072 | 85618% | 201194.63 | -10900.63 | -5.418% | -10900.63
Kohls - Salinas | CA | 227720 | 226806 | 914 | 0.403% | 401583.63 | -74076.89 | -18.45% | -173863.63
Kohls - San Bernardino - Central | CA | 517235 | 514171 | 3064 | 0.5959% | 1041913.48 | -524678.48 | -50.36% | -524678.48
Kohls - Sonora | CA | 187413 | 168026 | 19387 | 11.54% | 203517.57 | -24172.96 | -11.88% | -16104.57
CUSD - Stratford ES | CA | 161753 | 161805 | -52 | -0.03214% | 145499.29 | 16253.71 | 11.17% | 16253.71
Taft - City Hall | CA | 7126 | 540 | 6586 | 1220% | 64610.72 | -52853.55 | -81.8% | -57484.72
Taft - Federal Prison | CA | 101207 | 102132 | -925 | -0.9057% | 95337.69 | 5869.31 | 6.156% | 5869.31
Taft - Police Department | CA | 78743 | 79299 | -556 | -0.7011% | 93104.31 | 10065.38 | 10.81% | -14361.31
Taft - WTP | CA | 224493 | 309515 | -85022 | -27.47% | 317181.77 | -92688.77 | -29.22% | -92688.77
CDCR - CA Correctional Institution | CA | 1254260 | 1255778 | -1518 | -0.1209% | 1418789.16 | -104447.96 | -7.362% | -164529.16
CDCR - CA Correctional Institution II | CA | 1270510.68 | 1134835 | 135675.68 | 11.96% | 2039660.19 | -769149.51 | -37.71% | -769149.51
Snowline SD - Vista Verde ES | CA | 83365 | 84659 | -1294 | -1.528% | 176061.12 | -120798.03 | -68.61% | -92696.12
North Stonington | CT | 7373840 | 18012 | 7355828 |  | 0 | 4544320

## 1st Qtr
Silicon Ranch |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 8848504 | 5445782 | 3402722 | 62.48% | 8534815.99 | 313688.01 | 3.675%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Iron Mountain - Windsor | CT | 49256 | 48997 | 259 | 0.5286% | 54649.74 | -5393.74 | -9.87%
Kohls - Auburn | NY | 38514 | 38129 | 385 | 1.01% | 39136.03 | -622.03 | -1.589%
Kohls - Bensalem | PA | 72426 | 68354 | 4072 | 5.957% | 65202.38 | 7223.62 | 11.08%
Kohls - Brick | NJ | 91939 | 90004 | 1935 | 2.15% | 74753.88 | 17185.12 | 22.99%
Kohls - Buffalo | NY | 29451 | 0 | 29451 |  | 54344.28 | -24893.28 | -45.81%
Kohls - Canton | CT | 22796 | 22526 | 270 | 1.199% | 23886.67 | -1090.67 | -4.566%
Kohls - East Amherst | NY | 38997 | 38434 | 563 | 1.465% | 51187.85 | -12190.85 | -23.82%
Kohls - East Brunswick | NJ | 100414 | 100690 | -276 | -0.2741% | 99741.6 | 672.4 | 0.6741%
Kohls - Edgewood | MD | 500770 | 496013 | 4757 | 0.959% | 540853.2 | -40083.2 | -7.411%
Kohls - Granite Run | PA | 65152 | 64562 | 590 | 0.9139% | 65257.14 | -105.14 | -0.1611%
Kohls - Greece | NY | 33497 | 33004 | 493 | 1.494% | 51595.13 | -18098.13 | -35.08%
Kohls - Hanover | PA | 74462 | 73824 | 638 | 0.8642% | 73222.49 | 1239.51 | 1.693%
Kohls - Horsehead | NY | 44770 | 44242 | 528 | 1.193% | 53409.39 | -8639.39 | -16.18%
Kohls - Hudson | NY | 55206 | 54849 | 357 | 0.6509% | 60860.77 | -5654.77 | -9.291%
Kohls - Ithaca | NY | 43855 | 43541 | 314 | 0.7212% | 56649.12 | -12794.12 | -22.58%
Kohls - Kingston | NY | 71928 | 71217 | 711 | 0.9984% | 88222.68 | -16294.68 | -18.47%
Kohls - Mechanicsburg | PA | 84942 | 84174 | 768 | 0.9124% | 83857.58 | 1084.42 | 1.293%
Kohls - Middletown | NJ | 130027 | 128071 | 1956 | 1.527% | 118223.06 | 11803.94 | 9.984%
Kohls - North Amherst | NY | 0 | 0 | 0 |  | 44245.55 | -44245.55 | -100%
Kohls - Staten Island | NY | 58874 | 0 | 58874 |  | 72887.91 | -9502.29 | -13.04%
Kohls - Warminster | PA | 86449 | 86782 | -333 | -0.3837% | 72227.48 | 6261.49 | 8.669%
Kohls - Waterbury | CT | 52627 | 51880 | 747 | 1.44% | 63024.39 | -10397.39 | -16.5%
Mojave Water Agency - Headquarters | CA | 98584 | 92436 | 6148 | 6.651% | 169730.46 | 11987.4 | 7.063%
CSU - Bakersfield | CA | 290309 | 288798 | 1511 | 0.5232% | 257127.57 | 33181.43 | 12.9%
Greenfield USD - Fairfield ES | CA | 31004 | 30796 | 208 | 0.6754% | 44355.33 | 4843.44 | 10.92%
Greenfield USD - Granite Point ES | CA | 85429 | 85217 | 212 | 0.2488% | 68700.23 | 16728.77 | 24.35%
Greenfield USD - Greenfield MS | CA | 46320 | 32166 | 14154 | 44% | 49111.12 | 7310.442 | 14.89%
Greenfield USD - Horizon ES | CA | 77999 | 77925 | 74 | 0.09496% | 70247.88 | 7751.12 | 11.03%
Greenfield USD - McKee MS | CA | 37769 | 37672 | 97 | 0.2575% | 37725.43 | -5204.84 | -13.8%
Greenfield USD - Plantation ES | CA | 36700 | 36583 | 117 | 0.3198% | 30727.23 | 5972.77 | 19.44%
Greenfield USD - Planz ES | CA | 14100 | 14007 | 93 | 0.664% | 52884.98 | -20668.34 | -39.08%
Greenfield USD - Raffaello Palla ES | CA | 78218 | 76905 | 1313 | 1.707% | 77136.54 | 1081.46 | 1.402%
Greenfield USD - Valle Verde ES | CA | 94530 | 93825 | 705 | 0.7514% | 53460.28 | 22153.41 | 41.44%
Greenfield USD - W.A. Kendrick ES | CA | 9316 | 0 | 9316 |  | 27900.95 | -18584.95 | -66.61%
Muroc Joint USD - Boron HS | CA | 0 | 0 | 0 |  | 61204.34 | -83442.21 | -136.3%
Muroc Joint USD - W. Boron ES | CA | 32769 | 32760 | 9 | 0.02747% | 30870.4 | 1898.6 | 6.15%
Colusa - WTP | CA | 0 | 0 | 0 |  | 190622.74 | -83651.3 | -43.88%
CDCR-North Kern State Prision | CA | 237075 | 235320 | 1755 | 0.7458% | 335883.02 | -98808.02 | -29.42%
Muroc Joint USD - District Office | CA | 16393 | 27687 | -11294 | -40.79% | 31773.82 | -5347.94 | -16.83%
Whole Foods - Manhattan Beach | CA | 39546 | 39678 | -132 | -0.3327% | 48623.56 | -9077.56 | -18.67%
Pioneer USD - Frontier ES | CA | 69193 | 0 | 69193 |  | 61922.17 | 8061.03 | 13.02%
Pioneer USD - Pioneer ES | CA | 41281 | 0 | 41281 |  | 62281.26 | -21000.26 | -33.72%
Pioneer USD - Pioneer MS | CA | 95802 | 0 | 95802 |  | 101766.18 | 11728.33 | 11.52%
Kingsburg Joint UHSD - Kingsburg HS | CA | 154011 | 133941 | 20070 | 14.98% | 144517.65 | 9493.35 | 6.569%
CADRB | CA | 0 | 0 | 0 |  | 1265150.78 | -1550916 | -122.6%
CDCR-CA State Prison LA County | CA | 572550 | 571486 | 1064 | 0.1862% | 956201.86 | -383651.86 | -40.12%
Central USD Akers ES | CA | 125312 | 0 | 125312 |  | 60014.97 | 58235.27 | 97.03%
CUSD - District Office | CA | 49223 | 49053 | 170 | 0.3466% | 51733.5 | -2510.5 | -4.853%
Parlier - WTP | CA | 96610 | 97173 | -563 | -0.5794% | 104445.94 | -37093.36 | -35.51%
Snowline SD - Quail Valley MS | CA | 73141 | 71547 | 1594 | 2.228% | 86517.26 | -13376.26 | -15.46%
Snowline SD - Serrano HS - Middle Lot | CA | 67117 | 67726 | -609 | -0.8992% | 77710.38 | -33457.15 | -43.05%
Snowline SD - Pinon Hills ES | CA | 30706 | 31037 | -331 | -1.066% | 52493.94 | -21787.94 | -41.51%
Ramona - Santa Maria WTP | CA | 166769 | 166654 | 115 | 0.06901% | 142213.79 | -21695.51 | -15.26%
Kohls - Redding | CA | 65082 | 33 | 65049 | 197118% | 56668.39 | 8413.61 | 14.85%
Kohls - Salinas | CA | 79266 | 79173 | 93 | 0.1175% | 195379.35 | -16326.61 | -8.356%
Kohls - San Bernardino - Central | CA | 325957 | 324477 | 1480 | 0.4561% | 373996.89 | -48039.89 | -12.84%
Kohls - Sonora | CA | 58428 | 39838 | 18590 | 46.66% | 53636.64 | -3277.03 | -6.11%
CUSD - Stratford ES | CA | 58757 | 59149 | -392 | -0.6627% | 44456.07 | 14300.93 | 32.17%
Taft - City Hall | CA | 5032 | 298 | 4734 | 1589% | 21141.25 | -11478.08 | -54.29%
Taft - Federal Prison | CA | 40100 | 40585 | -485 | -1.195% | 28186.64 | 11913.36 | 42.27%
Taft - Police Department | CA | 25316 | 25528 | -212 | -0.8305% | 43385.41 | 6357.28 | 14.65%
Taft - WTP | CA | 31622 | 65419 | -33797 | -51.66% | 76600.94 | -44978.94 | -58.72%
CDCR - CA Correctional Institution | CA | 350805 | 345262 | 5543 | 1.605% | 383758.33 | 27127.87 | 7.069%
CDCR - CA Correctional Institution II | CA | 333370 | 375609 | -42239 | -11.25% | 510212.31 | -176842.31 | -34.66%
Snowline SD - Vista Verde ES | CA | 42481 | 42714 | -233 | -0.5455% | 34899.89 | -20520.8 | -58.8%
North Stonington | CT | 2918160 | 18012 | 2900148 | 16101% | 0 | 2918160

## 2nd Qtr
Silicon Ranch |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 13481488.68 | 8136235 | 5345253.68 | 65.7% | 15646884.415 | -2165395.735 | -13.84%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Iron Mountain - Windsor | CT | 95082 | 94682 | 400 | 0.4225% | 101635.19 | -6553.19 | -6.448%
Kohls - Auburn | NY | 101667 | 100904 | 763 | 0.7562% | 123082.24 | -21415.24 | -17.4%
Kohls - Bensalem | PA | 25179 | 24905 | 274 | 1.1% | 110297.53 | -85118.53 | -77.17%
Kohls - Brick | NJ | 119185 | 113844 | 5341 | 4.692% | 134065.61 | -14880.61 | -11.1%
Kohls - Buffalo | NY | 107073 | 0 | 107073 |  | 146084.38 | -39011.38 | -26.7%
Kohls - Canton | CT | 46827 | 46338 | 489 | 1.055% | 45416.5 | 1410.5 | 3.106%
Kohls - East Amherst | NY | 61713 | 61010 | 703 | 1.152% | 130330 | -68617 | -52.65%
Kohls - East Brunswick | NJ | 150001 | 143257 | 6744 | 4.708% | 173248.83 | -23247.83 | -13.42%
Kohls - Edgewood | MD | 771694 | 759216 | 12478 | 1.644% | 917243.32 | -145549.32 | -15.87%
Kohls - Granite Run | PA | 102790 | 101830 | 960 | 0.9427% | 109968.7 | -7178.7 | -6.528%
Kohls - Greece | NY | 102523 | 101620 | 903 | 0.8886% | 141215.53 | -38692.53 | -27.4%
Kohls - Hanover | PA | 121035 | 120271 | 764 | 0.6352% | 124902.24 | -3867.24 | -3.096%
Kohls - Horsehead | NY | 88669 | 87913 | 756 | 0.8599% | 100894.67 | -12225.67 | -12.12%
Kohls - Hudson | NY | 94516 | 82808 | 11708 | 14.14% | 107216.78 | -12700.78 | -11.85%
Kohls - Ithaca | NY | 90462 | 89824 | 638 | 0.7103% | 116723.1 | -26261.1 | -22.5%
Kohls - Kingston | NY | 119745 | 118724 | 1021 | 0.86% | 174584.81 | -54839.81 | -31.41%
Kohls - Mechanicsburg | PA | 127633 | 126599 | 1034 | 0.8168% | 145854.93 | -18221.93 | -12.49%
Kohls - Middletown | NJ | 110046 | 106140 | 3906 | 3.68% | 203869.26 | -93823.26 | -46.02%
Kohls - North Amherst | NY | 76647 | 76320 | 327 | 0.4285% | 124961.29 | -48314.29 | -38.66%
Kohls - Staten Island | NY | 90434 | 0 | 90434 |  | 121926.54 | -31492.54 | -25.83%
Kohls - Warminster | PA | 135109 | 126573 | 8536 | 6.744% | 134631.76 | 477.24 | 0.3545%
Kohls - Waterbury | CT | 113090 | 111918 | 1172 | 1.047% | 120488.88 | -7398.88 | -6.141%
Mojave Water Agency - Headquarters | CA | 145076 | 141271 | 3805 | 2.693% | 120572.59 | 24503.41 | 20.32%
CSU - Bakersfield | CA | 537324 | 548831 | -11507 | -2.097% | 511178.47 | 26145.53 | 5.115%
Greenfield USD - Fairfield ES | CA | 33786 | 33007 | 779 | 2.36% | 48421.33 | -14635.33 | -30.22%
Greenfield USD - Granite Point ES | CA | 102224 | 100377 | 1847 | 1.84% | 128079.4 | -25855.4 | -20.19%
Greenfield USD - Greenfield MS | CA | 63918 | 61974 | 1944 | 3.137% | 87099.575 | -23181.575 | -26.62%
Greenfield USD - Horizon ES | CA | 102864 | 101299 | 1565 | 1.545% | 133131.09 | -30267.09 | -22.73%
Greenfield USD - McKee MS | CA | 60201 | 59465 | 736 | 1.238% | 81290.48 | -21089.48 | -25.94%
Greenfield USD - Plantation ES | CA | 56565 | 56404 | 161 | 0.2854% | 58155.24 | -1590.24 | -2.734%
Greenfield USD - Planz ES | CA | 22412 | 22293 | 119 | 0.5338% | 65857.79 | -43445.79 | -65.97%
Greenfield USD - Raffaello Palla ES | CA | 96313 | 95257 | 1056 | 1.109% | 143205.08 | -46892.08 | -32.74%
Greenfield USD - Valle Verde ES | CA | 137214 | 136630 | 584 | 0.4274% | 133645.83 | 3568.17 | 2.67%
Greenfield USD - W.A. Kendrick ES | CA | 0 | 0 | 0 |  | 51528.09 | -51528.09 | -100%
Muroc Joint USD - Boron HS | CA | 0 | 0 | 0 |  | 117409.55 | -117409.55 | -100%
Muroc Joint USD - W. Boron ES | CA | 41715 | 41580 | 135 | 0.3247% | 43295.7 | -1580.7 | -3.651%
Colusa - WTP | CA | 0 | 0 | 0 |  | 183174.9 | -183174.9 | -100%
CDCR-North Kern State Prision | CA | 396377 | 395084 | 1293 | 0.3273% | 727441.61 | -331064.61 | -45.51%
Muroc Joint USD - District Office | CA | 23980 | 23941 | 39 | 0.1629% | 30541.73 | -6561.73 | -21.48%
Whole Foods - Manhattan Beach | CA | 49009 | 49223 | -214 | -0.4348% | 65936.39 | -16927.39 | -25.67%
Pioneer USD - Frontier ES | CA | 96136 | 0 | 96136 |  | 113460.21 | -17324.21 | -15.27%
Pioneer USD - Pioneer ES | CA | 36948 | 0 | 36948 |  | 115391.59 | -78443.59 | -67.98%
Pioneer USD - Pioneer MS | CA | 156330 | 0 | 156330 |  | 154503.46 | 1826.54 | 1.182%
Kingsburg Joint UHSD - Kingsburg HS | CA | 168904 | 139921 | 28983 | 20.71% | 265959.78 | -97055.78 | -36.49%
CADRB | CA | 0 | 0 | 0 |  | 2644174 | -2644174 | -100%
CDCR-CA State Prison LA County | CA | 963570 | 951914 | 11656 | 1.224% | 1643365.15 | -679795.15 | -41.37%
Central USD Akers ES | CA | 128056 | 38998 | 89058 | 228.4% | 124828.92 | 3227.08 | 2.585%
CUSD - District Office | CA | 60411 | 59938 | 473 | 0.7891% | 106279.6 | -45868.6 | -43.16%
Parlier - WTP | CA | 149811 | 145507 | 4304 | 2.958% | 307113 | -157302 | -51.22%
Snowline SD - Quail Valley MS | CA | 131088 | 126744 | 4344 | 3.427% | 142768.54 | -11680.54 | -8.181%
Snowline SD - Serrano HS - Middle Lot | CA | 94901 | 93658 | 1243 | 1.327% | 178263.52 | -83362.52 | -46.76%
Snowline SD - Pinon Hills ES | CA | 39131 | 39477 | -346 | -0.8765% | 78321.9 | -39190.9 | -50.04%
Ramona - Santa Maria WTP | CA | 209793 | 210295 | -502 | -0.2387% | 246362.38 | -36569.38 | -14.84%
Kohls - Redding | CA | 82046 | 56 | 81990 | 146411% | 105690.63 | -23644.63 | -22.37%
Kohls - Salinas | CA | 112979 | 112392 | 587 | 0.5223% | 154446.4 | -41467.4 | -26.85%
Kohls - San Bernardino - Central | CA | 21438 | 21386 | 52 | 0.2431% | 485649.98 | -464211.98 | -95.59%
Kohls - Sonora | CA | 94299 | 93666 | 633 | 0.6758% | 110287.21 | -15988.21 | -14.5%
CUSD - Stratford ES | CA | 76753 | 76453 | 300 | 0.3924% | 75667.06 | 1085.94 | 1.435%
Taft - City Hall | CA | 1918 | 154 | 1764 | 1145% | 32089.61 | -30171.61 | -94.02%
Taft - Federal Prison | CA | 54259 | 54707 | -448 | -0.8189% | 49740.81 | 4518.19 | 9.083%
Taft - Police Department | CA | 39375 | 39732 | -357 | -0.8985% | 36705.26 | 2669.74 | 7.273%
Taft - WTP | CA | 129399 | 180831 | -51432 | -28.44% | 163119.56 | -33720.56 | -20.67%
CDCR - CA Correctional Institution | CA | 687973 | 695409 | -7436 | -1.069% | 754641.53 | -66668.53 | -8.834%
CDCR - CA Correctional Institution II | CA | 738589.68 | 560994 | 177595.68 | 31.66% | 1114079.6 | -375489.92 | -33.7%
Snowline SD - Vista Verde ES | CA | 31603 | 32671 | -1068 | -3.269% | 105367.78 | -73764.78 | -70.01%
North Stonington | CT | 4455680 | 0 | 4455680 |  | 0 | 1626160

## 3rd Qtr
Silicon Ranch |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 2766483 | 2532830 | 233653 | 9.225% | 5398892.686 | -2632409.686 | -48.76%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Iron Mountain - Windsor | CT | 37799 | 37699 | 100 | 0.2653% | 35701.9 | 2097.1 | 5.874%
Kohls - Auburn | NY | 44556 | 44420 | 136 | 0.3062% | 44245.55 | 310.45 | 0.7017%
Kohls - Bensalem | PA | 0 | 0 | 0 |  | 39533.49 | -39533.49 | -100%
Kohls - Brick | NJ | 48789 | 48707 | 82 | 0.1684% | 49138.28 | -349.28 | -0.7108%
Kohls - Buffalo | NY | 58595 | 0 | 58595 |  | 52511.51 | 6083.49 | 11.59%
Kohls - Canton | CT | 18679 | 18476 | 203 | 1.099% | 16279.33 | 2399.67 | 14.74%
Kohls - East Amherst | NY | 0 | 0 | 0 |  | 48225.8 | -48225.8 | -100%
Kohls - East Brunswick | NJ | 21605 | 21561 | 44 | 0.2041% | 60986.06 | -39381.06 | -64.57%
Kohls - Edgewood | MD | 182967 | 182193 | 774 | 0.4248% | 322055.92 | -139088.92 | -43.19%
Kohls - Granite Run | PA | 39643 | 39349 | 294 | 0.7472% | 39195.43 | 447.57 | 1.142%
Kohls - Greece | NY | 42002 | 41818 | 184 | 0.44% | 50058.57 | -8056.57 | -16.09%
Kohls - Hanover | PA | 38149 | 37978 | 171 | 0.4503% | 44023.48 | -5874.48 | -13.34%
Kohls - Horsehead | NY | 37333 | 0 | 37333 |  | 36747.88 | 585.12 | 1.592%
Kohls - Hudson | NY | 49090 | 688 | 48402 | 7035% | 41607.48 | 7482.52 | 17.98%
Kohls - Ithaca | NY | 38495 | 38361 | 134 | 0.3493% | 42051.79 | -3556.79 | -8.458%
Kohls - Kingston | NY | 63760 | 51065 | 12695 | 24.86% | 61555.01 | 2204.99 | 3.582%
Kohls - Mechanicsburg | PA | 3184 | 3163 | 21 | 0.6639% | 51398.34 | -48214.34 | -93.81%
Kohls - Middletown | NJ | 0 | 0 | 0 |  | 70367.84 | -70367.84 | -100%
Kohls - North Amherst | NY | 23666 | 23596 | 70 | 0.2967% | 44708.37 | -21042.37 | -47.07%
Kohls - Staten Island | NY | 35516 | 0 | 35516 |  | 40682.01 | -5166.01 | -12.7%
Kohls - Warminster | PA | 51308 | 51124 | 184 | 0.3599% | 48325.86 | 2982.14 | 6.171%
Kohls - Waterbury | CT | 43943 | 43673 | 270 | 0.6182% | 41803.94 | 2139.06 | 5.117%
Mojave Water Agency - Headquarters | CA | 4075 | 2601 | 1474 | 56.67% | 39251.32 | -35176.32 | -89.62%
CSU - Bakersfield | CA | 190709 | 190291 | 418 | 0.2197% | 193659.71 | -2950.71 | -1.524%
Greenfield USD - Fairfield ES | CA | 6869 | 6810 | 59 | 0.8664% | 17096.37 | -10227.37 | -59.82%
Greenfield USD - Granite Point ES | CA | 46822 | 46511 | 311 | 0.6687% | 45287.92 | 1534.08 | 3.387%
Greenfield USD - Greenfield MS | CA | 25214 | 25198 | 16 | 0.0635% | 30764.276 | -5550.276 | -18.04%
Greenfield USD - Horizon ES | CA | 32399 | 32335 | 64 | 0.1979% | 47171.28 | -14772.28 | -31.32%
Greenfield USD - McKee MS | CA | 19824 | 19814 | 10 | 0.05047% | 28788.08 | -8964.08 | -31.14%
Greenfield USD - Plantation ES | CA | 19773 | 19751 | 22 | 0.1114% | 20625.94 | -852.94 | -4.135%
Greenfield USD - Planz ES | CA | 7662 | 7627 | 35 | 0.4589% | 23208.78 | -15546.78 | -66.99%
Greenfield USD - Raffaello Palla ES | CA | 39368 | 39039 | 329 | 0.8427% | 50572.17 | -11204.17 | -22.15%
Greenfield USD - Valle Verde ES | CA | 45490 | 45416 | 74 | 0.1629% | 47171.28 | -1681.28 | -3.564%
Greenfield USD - W.A. Kendrick ES | CA | 0 | 0 | 0 |  | 18190.17 | -18190.17 | -100%
Muroc Joint USD - Boron HS | CA | 0 | 0 | 0 |  | 38442.26 | -38442.26 | -100%
Muroc Joint USD - W. Boron ES | CA | 14154 | 14113 | 41 | 0.2905% | 14183.26 | -29.26 | -0.2063%
Colusa - WTP | CA | 0 | 0 | 0 |  | 67861.15 | -67861.15 | -100%
CDCR-North Kern State Prision | CA | 104432 | 104067 | 365 | 0.3507% | 265603.15 | -161171.15 | -60.68%
Muroc Joint USD - District Office | CA | 8475 | 8467 | 8 | 0.09448% | 9995.08 | -1520.08 | -15.21%
Whole Foods - Manhattan Beach | CA | 16724 | 16692 | 32 | 0.1917% | 23457.05 | -6733.05 | -28.7%
Pioneer USD - Frontier ES | CA | 10267 | 0 | 10267 |  | 39491.66 | -29224.66 | -74%
Pioneer USD - Pioneer ES | CA | 7212 | 0 | 7212 |  | 40411.45 | -33199.45 | -82.15%
Pioneer USD - Pioneer MS | CA | 43768 | 0 | 43768 |  | 54189.43 | -10421.43 | -19.23%
Kingsburg Joint UHSD - Kingsburg HS | CA | 23415 | 0 | 23415 |  | 93257.03 | -69842.03 | -74.89%
CADRB | CA | 0 | 0 | 0 |  | 932886 | -932886 | -100%
CDCR-CA State Prison LA County | CA | 224654 | 224234 | 420 | 0.1873% | 550300.92 | -325646.92 | -59.18%
Central USD Akers ES | CA | 3124 | 0 | 3124 |  | 42446.3 | -39322.3 | -92.64%
CUSD - District Office | CA | 30845 | 30784 | 61 | 0.1982% | 36534.58 | -5689.58 | -15.57%
Parlier - WTP | CA | 0 | 47921 | -47921 | -100% | 0 | 0
Snowline SD - Quail Valley MS | CA | 51648 | 51603 | 45 | 0.0872% | 48529.62 | 3118.38 | 6.426%
Snowline SD - Serrano HS - Middle Lot | CA | 0 | 51356 | -51356 | -100% | 0 | 0
Snowline SD - Pinon Hills ES | CA | 13315 | 13307 | 8 | 0.06012% | 25453.18 | -12138.18 | -47.69%
Ramona - Santa Maria WTP | CA | 79894 | 79770 | 124 | 0.1554% | 84213.41 | -4319.41 | -5.129%
Kohls - Redding | CA | 43166 | 133 | 43033 | 32356% | 38835.61 | 4330.39 | 11.15%
Kohls - Salinas | CA | 35475 | 35241 | 234 | 0.664% | 51757.88 | -16282.88 | -31.46%
Kohls - San Bernardino - Central | CA | 169840 | 168308 | 1532 | 0.9102% | 182266.61 | -12426.61 | -6.818%
Kohls - Sonora | CA | 34686 | 34522 | 164 | 0.4751% | 39593.72 | -4907.72 | -12.4%
CUSD - Stratford ES | CA | 26243 | 26203 | 40 | 0.1527% | 25376.16 | 866.84 | 3.416%
Taft - City Hall | CA | 176 | 88 | 88 | 100% | 11379.86 | -11203.86 | -98.45%
Taft - Federal Prison | CA | 6848 | 6840 | 8 | 0.117% | 17410.24 | -10562.24 | -60.67%
Taft - Police Department | CA | 14052 | 14039 | 13 | 0.0926% | 13013.64 | 1038.36 | 7.979%
Taft - WTP | CA | 63472 | 63265 | 207 | 0.3272% | 77461.27 | -13989.27 | -18.06%
CDCR - CA Correctional Institution | CA | 215482 | 215107 | 375 | 0.1743% | 280389.3 | -64907.3 | -23.15%
CDCR - CA Correctional Institution II | CA | 198551 | 198232 | 319 | 0.1609% | 415368.28 | -216817.28 | -52.2%
Snowline SD - Vista Verde ES | CA | 9281 | 9274 | 7 | 0.07548% | 35793.45 | -26512.45 | -74.07%
North Stonington | CT

## 4th Qtr
Silicon Ranch |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Iron Mountain - Windsor | CT | 0 | 0 | 0 |  | 0 | 0
Kohls - Auburn | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Bensalem | PA | 0 | 0 | 0 |  | 0 | 0
Kohls - Brick | NJ | 0 | 0 | 0 |  | 0 | 0
Kohls - Buffalo | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Canton | CT | 0 | 0 | 0 |  | 0 | 0
Kohls - East Amherst | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - East Brunswick | NJ | 0 | 0 | 0 |  | 0 | 0
Kohls - Edgewood | MD | 0 | 0 | 0 |  | 0 | 0
Kohls - Granite Run | PA | 0 | 0 | 0 |  | 0 | 0
Kohls - Greece | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Hanover | PA | 0 | 0 | 0 |  | 0 | 0
Kohls - Horsehead | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Hudson | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Ithaca | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Kingston | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Mechanicsburg | PA | 0 | 0 | 0 |  | 0 | 0
Kohls - Middletown | NJ | 0 | 0 | 0 |  | 0 | 0
Kohls - North Amherst | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Staten Island | NY | 0 | 0 | 0 |  | 0 | 0
Kohls - Warminster | PA | 0 | 0 | 0 |  | 0 | 0
Kohls - Waterbury | CT | 0 | 0 | 0 |  | 0 | 0
Mojave Water Agency - Headquarters | CA | 0 | 0 | 0 |  | 0 | 0
CSU - Bakersfield | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Fairfield ES | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Granite Point ES | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Greenfield MS | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Horizon ES | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - McKee MS | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Plantation ES | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Planz ES | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Raffaello Palla ES | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - Valle Verde ES | CA | 0 | 0 | 0 |  | 0 | 0
Greenfield USD - W.A. Kendrick ES | CA | 0 | 0 | 0 |  | 0 | 0
Muroc Joint USD - Boron HS | CA | 0 | 0 | 0 |  | 0 | 0
Muroc Joint USD - W. Boron ES | CA | 0 | 0 | 0 |  | 0 | 0
Colusa - WTP | CA | 0 | 0 | 0 |  | 0 | 0
CDCR-North Kern State Prision | CA | 0 | 0 | 0 |  | 0 | 0
Muroc Joint USD - District Office | CA | 0 | 0 | 0 |  | 0 | 0
Whole Foods - Manhattan Beach | CA | 0 | 0 | 0 |  | 0 | 0
Pioneer USD - Frontier ES | CA | 0 | 0 | 0 |  | 0 | 0
Pioneer USD - Pioneer ES | CA | 0 | 0 | 0 |  | 0 | 0
Pioneer USD - Pioneer MS | CA | 0 | 0 | 0 |  | 0 | 0
Kingsburg Joint UHSD - Kingsburg HS | CA | 0 | 0 | 0 |  | 0 | 0
CADRB | CA | 0 | 0 | 0 |  | 0 | 0
CDCR-CA State Prison LA County | CA | 0 | 0 | 0 |  | 0 | 0
Central USD Akers ES | CA | 0 | 0 | 0 |  | 0 | 0
CUSD - District Office | CA | 0 | 0 | 0 |  | 0 | 0
Parlier - WTP | CA | 0 | 0 | 0 |  | 0 | 0
Snowline SD - Quail Valley MS | CA | 0 | 0 | 0 |  | 0 | 0
Snowline SD - Serrano HS - Middle Lot | CA | 0 | 0 | 0 |  | 0 | 0
Snowline SD - Pinon Hills ES | CA | 0 | 0 | 0 |  | 0 | 0
Ramona - Santa Maria WTP | CA | 0 | 0 | 0 |  | 0 | 0
Kohls - Redding | CA | 0 | 0 | 0 |  | 0 | 0
Kohls - Salinas | CA | 0 | 0 | 0 |  | 0 | 0
Kohls - San Bernardino - Central | CA | 0 | 0 | 0 |  | 0 | 0
Kohls - Sonora | CA | 0 | 0 | 0 |  | 0 | 0
CUSD - Stratford ES | CA | 0 | 0 | 0 |  | 0 | 0
Taft - City Hall | CA | 0 | 0 | 0 |  | 0 | 0
Taft - Federal Prison | CA | 0 | 0 | 0 |  | 0 | 0
Taft - Police Department | CA | 0 | 0 | 0 |  | 0 | 0
Taft - WTP | CA | 0 | 0 | 0 |  | 0 | 0
CDCR - CA Correctional Institution | CA | 0 | 0 | 0 |  | 0 | 0
CDCR - CA Correctional Institution II | CA | 0 | 0 | 0 |  | 0 | 0
Snowline SD - Vista Verde ES | CA | 0 | 0 | 0 |  | 0 | 0
North Stonington | CT

## Jan
Silicon Ranch |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 2371481 | 1432232 | 939249 | 65.58% | 2199066.06 | 172414.94 | 7.84%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT | 13219 | 13132 | 87 | 0.6625% | 12931.18 | 287.82 | 2.226%
Kohls - Auburn | NY | 5600 | 5498 | 102 | 1.855% | 4748.53 | 851.47 | 17.93%
Kohls - Bensalem | PA | 16129 | 16813 | -684 | -4.068% | 15644.12 | 484.88 | 3.099%
Kohls - Brick | NJ | 22439 | 22404 | 35 | 0.1562% | 16579.62 | 5859.38 | 35.34% | 1.Inverter tripped offline at 12:25PM on 01/20 due to Asymetrical Array fault and back online on 01/21. | 1.SR094211
Kohls - Buffalo | NY | 4465 | N/A |  |  | 7988.27 | -3523.27 | -44.11% | 1.Inverters 7 and 8 are offline from 12/03, due to Grid contactor Open fault and after reset done by technician inverter 7 was back online at 14:25 and inverter 8 was back online at 15:40 on 01/31/25. 2.Inverter 4 tripped offline from 13:35 on 12/30, due to Grid contactor Open fault through out the month. | 1.SR093917, SR096145 2.SR095177 | SR096145 | SR095177
Kohls - Canton | CT | 5915 | 5837 | 78 | 1.336% | 5796.5 | 118.5 | 2.044%
Kohls - East Amherst | NY | 5604 | 5462 | 142 | 2.6% | 8423.32 | -2819.32 | -33.47% | 1.Low generation due to weather/snow.
Kohls - East Brunswick | NJ | 21858 | 22691 | -833 | -3.671% | 23131.39 | -1273.39 | -5.505%
Kohls - Edgewood | MD | 95387 | 94530 | 857 | 0.9066% | 135284.96 | -39897.96 | -29.49% | 1.Low generation due to weather/snow.
Kohls - Granite Run | PA | 12350 | 12178 | 172 | 1.412% | 15908.81 | -3558.81 | -22.37% | 1.Low generation due to weather/snow.
Kohls - Greece | NY | 5278 | 5111 | 167 | 3.267% | 9358.21 | -4080.21 | -43.6% | 1.Low generation due to weather/snow.
Kohls - Hanover | PA | 13440 | 13266 | 174 | 1.312% | 18746.47 | -5306.47 | -28.31% | 1.Inverter was offline on 01/22 and back online on 01/23. | 1.SR095860
Kohls - Horsehead | NY | 10616 | 10428 | 188 | 1.803% | 12681.26 | -2065.26 | -16.29% | 1.Inverter started late for its production at 12:15PM on 01/17 due to Idle State fault. | 1.SR095654
Kohls - Hudson | NY | 11567 | 11484 | 83 | 0.7227% | 12764.56 | -1197.56 | -9.382%
Kohls - Ithaca | NY | 9275 | 9191 | 84 | 0.9139% | 11829.67 | -2554.67 | -21.6% | 1.Low generation due to weather/snow.
Kohls - Kingston | NY | 18271 | 18012 | 259 | 1.438% | 22224.6 | -3953.6 | -17.79% | 1.Low generation due to weather/snow.
Kohls - Mechanicsburg | PA | 15891 | 15725 | 166 | 1.056% | 21467.31 | -5576.31 | -25.98% | 1.Low generation due to weather/snow.
Kohls - Middletown | NJ | 26770 | 26078 | 692 | 2.654% | 29428.37 | -2658.37 | -9.033%
Kohls - North Amherst | NY | 0 | N/A |  |  | 6479.47 | -6479.47 | -100% | 1. Site tripped offline at 09:30am from 08/12/24, due to system removal for roof repair and to start rebuilding the roof. | 1.SR093440,SR093861 | SR093861
Kohls - Staten Island | NY | 10433 | N/A |  |  | 15368.35 | -4935.35 | -32.11% | 1. Site tripped offline at 09:05Am on 08/17/24 due to roof replacement and back online at 14:25 on 01/09/25 after technician site walkthrough. 2. Inverter 7 tripped offline at 15:20 from 01/10. Inverter 8 was offline due to Internal hardware “Error E018” fault till date. Inverter 20 was offline from 07/22/24 due to Internal Error -E018 fault. Inverter 21 was tripped offline at 09:05Am on 08/17/24 due to Internal Error - E018 fault. | 1.SR089189 2.SR095623,SR078720 &SR087994 | SR095623 | SR078720 | SR087994
Kohls - Warminster | PA | 16958 | 17898 | -940 | -5.252% | 19404.55 | -2446.55 | -12.61% | 1.Site was offline on 01/30, 01/31 technician checked-in and confirmed that cell modem is offline due to error and need to be replaced. | 1.SR093127
Kohls - Waterbury | CT | 15637 | 15269 | 368 | 2.41% | 15296.56 | 340.44 | 2.226%
Mojave Water Agency - Headquarters | CA | 26762 | 26680 | 82 | 0.3073% | 25853.48 | 908.52 | 3.514%
CSU - Bakersfield | CA | 78098 | 77683 | 415 | 0.5342% | 60631.17 | 17466.83 | 28.81%
Greenfield USD - Fairfield ES | CA | 9460 | 9393 | 67 | 0.7133% | 6747.91 | 2712.09 | 40.19%
Greenfield USD - Granite Point ES | CA | 26793 | 26796 | -3 | -0.0112% | 17651.94 | 9141.06 | 51.79%
Greenfield USD - Greenfield MS | CA | 14901 | 12967 | 1934 | 14.91% | 3998.76 | 10902.24 | 272.6% | 1. Inverter 1 is still not communicating, and as of 01/27/25, production is not being recorded at the meter. It may be offline due to the need for a new MOXA device | 1. SR089763
Greenfield USD - Horizon ES | CA | 22359 | 22521 | -162 | -0.7193% | 17883.35 | 4475.65 | 25.03% | 1. Inverter 2 Pad B back online at 12:50 on 01/02/25 after the technician replaced the faulty capacitors. 2. Inverter 1 Pad A started production late at 11:10 AM on 01/30/25 due to an AC overvoltage fault. | 1. SR089669 2. SR096157 | SR096157
Greenfield USD - McKee MS | CA | 10808 | 10786 | 22 | 0.204% | 10950.31 | -142.31 | -1.3%
Greenfield USD - Plantation ES | CA | 10716 | 10694 | 22 | 0.2057% | 7840.16 | 2875.84 | 36.68%
Greenfield USD - Planz ES | CA | 3658 | 3633 | 25 | 0.6881% | 8710.27 | -5052.27 | -58% | 1.Low generation due to weather/snow.
Greenfield USD - Raffaello Palla ES | CA | 25273 | 24777 | 496 | 2.002% | 19790.17 | 5482.83 | 27.7%
Greenfield USD - Valle Verde ES | CA | 27972 | 27847 | 125 | 0.4489% | 18660.89 | 9311.11 | 49.9%
Greenfield USD - W.A. Kendrick ES | CA | 4765 | N/A |  |  | 7201.47 | -2436.47 | -33.83% | 1.Meter reporting half of inverter production since 6/11/22 further repairs are requried. | 1. SR094440
Muroc Joint USD - Boron HS | CA | 0 | N/A |  |  | 23613.12 | -23613.12 | -100% | 1. Site back communication at 9:15AM on 12/30/2024 and Inverter remains offline because of Inverter down hard - Power supply critical failure. 2. Weather station began reporting erroneous values on 12/30/2024, and the POA sensor needed to be replaced along with additional repairs. | 1. SR092023, SR089707 2. SR093065 | SR089707 | SR093065
Muroc Joint USD - W. Boron ES | CA | 9827 | 9883 | -56 | -0.5666% | 8755.78 | 1071.22 | 12.23%
Colusa - WTP | CA | 0 | N/A |  |  | 17962.44 | -17962.44 | -100% | 1.No communication to DAS, need a replacement for meter and modem. | 1.SR089464, SR093180, SR093174 & SR095356 | SR093180 | SR093174 | SR095356
CDCR-North Kern State Prision | CA | 70021 | 69496 | 525 | 0.7554% | 80319.85 | -10298.85 | -12.82% | 1. Inverter 3 is offline on 01/01/25 and back online on 01/02, again tripped offline at 8:10AM on 01/05/25 and came back online on 01/06/25 due to a fan 5 and asymmetrical array fault beacuse of array is covered with damaged DC equipment. | 1. SR095083
Muroc Joint USD - District Office | CA | 4886 | 4880 | 6 | 0.123% | 6179.15 | -1293.15 | -20.93% | 1.Low generation due to weather/snow.
Whole Foods - Manhattan Beach | CA | 11385 | 11590 | -205 | -1.769% | 13787.4 | -2402.4 | -17.42% | 1.Inverters 3 & 8 are offline through out the month due to additional parts needed. | 1. SR089461, SR090375 | SR090375
Pioneer USD - Frontier ES | CA | 21344 | N/A |  |  | 11836.7 | 9507.3 | 80.32% | 1. Weather station is not communicating through out the month because the entire station needs to be replaced. | 1. SR092276
Pioneer USD - Pioneer ES | CA | 11680 | N/A |  |  | 11671.1 | 8.9 | 0.07626% | 1. Weather station is not communicating through out the month because the entire station needs to be replaced. 2. Pad 1 inverter 1 is offline through the month due to cantacted bold and Pad 1 inverter 2 regained its communication at 10:50 on 01/10/25 and pad 2 the inverter 1 is not communicating but production is at the meter because of bold on possible comms card issues. | 1. SR085968 2. SR092256, SR090090 & SR095592 | SR092256 | SR090090 | SR095592
Pioneer USD - Pioneer MS | CA | 29750 | N/A |  |  | 15852.46 | 13897.54 | 87.67% | 1. Weather station is not communicating through out the month, It was found that the pyranometer is not installed on-site. The installation of a new pyranometer will be required. | 1. SR089470, SR092603 | SR092603
Kingsburg Joint UHSD - Kingsburg HS | CA | 49408 | 32540 | 16868 | 51.84% | 35650.53 | 13757.47 | 38.59% | 1. Inverters A back online on 01/03/25 after the technician replacement of 2 badpower supplies and ac surge protectors found MOXA is not working. 24v being supplied but moxa needs to be replaced. also wire managed low hanging wires. 2. Meter B regulary capturing data from 7:20AM to 10:00AM rescpective with Inverter B, but Inverter B capturing data from 10:05AM to 4:45PM due to MOXA is not working. | 1.SR089612, SR095339 2. SR089612 | SR095339 | SR089612
CADRB | CA | 0 | N/A |  |  | 406484 | -406484 | -100% | 1. Site back online on 01/09/25 after the technician re-energized it, we cannot confirm as silicon ranch only has access to site. 2.Inverter 3 was back online on 11/15/2024 but we cannot confirm through SCADA since site is not communicating 3.Pyranometer has been giving bad readings. Prior to 9/25, the pyranometer read at most 450 W/m2. Since then, readings are between 950 and 400 W/m2 | 1. SR092166 2. SR086220 3. SR091312 | SR086220 | SR091312
CDCR-CA State Prison LA County | CA | 150767 | 150432 | 335 | 0.2227% | 268670.39 | -117903.39 | -43.88% | 1.Low generation due to weather/snow.
Central USD Akers ES | CA | 78098 | N/A |  |  | 13113.65 | 64984.35 | 495.5% | 1. Weather station is reporting 0w/m2 | 1. SR090370
CUSD - District Office | CA | 14514 | 14455 | 59 | 0.4082% | 10069.4 | 4444.6 | 44.14% | 1. Inverter 1 is tripped offline at 16:05 on 12/30/2024 and back online at 10:00AM on 01/06/25 after the technician power-cycled the inverter. | 1. SR095191
Parlier - WTP | CA | 23899 | 23840 | 59 | 0.2475% | 24216.44 | -317.44 | -1.311%
Snowline SD - Quail Valley MS | CA | 16364 | 16319 | 45 | 0.2758% | 23575.7 | -7211.7 | -30.59% | 1.Inverter trips on and offline through out the month frequently due to company chip replacement needed and Wires are all hanging and in poor condition. | 1.SR090965, SR094547 & SR094545 | SR094547 | SR094545
Snowline SD - Serrano HS - Middle Lot | CA | 16158 | 16819 | -661 | -3.93% | 26660.72 | -10502.72 | -39.39% | 1.Low generation due to weather/snow.
Snowline SD - Pinon Hills ES | CA | 8792 | 9144 | -352 | -3.85% | 15043.89 | -6251.89 | -41.56% | 1. 23 Modules need to be replace. | 1. SR090734
Ramona - Santa Maria WTP | CA | 53256 | 53678 | -422 | -0.7862% | 57557.78 | -4301.78 | -7.474%
Kohls - Redding | CA | 18846 | N/A |  |  | 12772.68 | 6073.32 | 47.55% | 1. Weather station does not report irradiance during the day. Likely a faulty pyranometer through out the month. | 1. SR090293, SR095854 | SR095854
Kohls - Salinas | CA | 23064 | 22605 | 459 | 2.031% | 24339.35 | -1275.35 | -5.24% | 1.Inverters 3, 7, 10, 11, 14, and 21 are offline. Inverter 2 may have a string down through out the month and parts are needed to bring these inverters back online. | 1. SR095449, SR089474, SR090381 & SR090380 | SR089474 | SR090381 | SR090380
Kohls - San Bernardino - Central | CA | 95820 | 95529 | 291 | 0.3046% | 110379.13 | -14559.13 | -13.19%
Kohls - Sonora | CA | 18576 | N/A |  |  | 14667.03 | 3908.97 | 26.65% | 1.Inverter 3 back online at 10:15AM on 01/27/25 and again offline on 01/28/25, remaind offline through out the month due to additional parts needed. 2. Inverter 7 is offline through out the month and parts needed to bring these inverter back online. 3. Inverter 12 is back online on 01/27/25 after technician tightening the terminals and but remained offline again from 01/30/25 and parts are needed to bring these inverter back online. | 1. SR089477 2. SR089477 3. SR089477 | SR089477 | SR089477
CUSD - Stratford ES | CA | 18529 | 18432 | 97 | 0.5263% | 8792.68 | 9736.32 | 110.7%
Taft - City Hall | CA | 1973 | 145 | 1828 | 1261% | 4140.82 | -2167.82 | -52.35% | 1.Low generation due to weather/snow.
Taft - Federal Prison | CA | 12852 | 12831 | 21 | 0.1637% | 7409.35 | 5442.65 | 73.46%
Taft - Police Department | CA | 7664 | 7639 | 25 | 0.3273% | 4765.84 | 2898.16 | 60.81%
Taft - WTP | CA | 0 | N/A |  |  | 4140.82 | -4140.82 | -100% | 1.Inverter 2 is offline and parts needed to bring these inverter back online. | 1. SR089732, SR094323 | SR094323
CDCR - CA Correctional Institution | CA | 128121 | 127640 | 481 | 0.3768% | 106071.03 | 22049.97 | 20.79% | 1. Inverter 1 is offline on 01/19/25 due to AE Solaron Fault Coolant Flow and back online on 01/20/25. 2. Inverter 1 production is being affected in the morning hours due to stuck trackers. | 1. SR095705 2. SR092170, SR092456 | SR092170 | SR092456
CDCR - CA Correctional Institution II | CA | 110462 | 104576 | 5886 | 5.628% | 166152.23 | -55690.23 | -33.52% | 1. Inverter 2's production being affected in the afternoon hours possibly due to stuck trackers. 2. Inverter 1 is underperforming and needs to have its surge protectors replaced. | 1. SR092171, SR092455 2. SR090296 | SR092455 | SR090296
Snowline SD - Vista Verde ES | CA | 16688 | 16963 | -275 | -1.621% | 17008.64 | -320.64 | -1.885%
North Stonington | CT | 730070 | 18012 | 712058 |  | 0 | 730070 |  | 1. Inverter A.02.08 tripped offline at 10:00AM on 01/30/25 and remained offline throught the month. | 1. SR096146

## Feb
Silicon Ranch |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2644477 | 1594440 | 1050037 | 65.86% | 2618498.26 | 25978.74 | 0.9921%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT | 8815 | 8784 | 31 | 0.3529% | 16828.12 | -8013.12 | -47.62% | 1. Low generation due to weather/snow.
Kohls - Auburn | NY | 5678 | 5604 | 74 | 1.32% | 10737.42 | -5059.42 | -47.12% | 1. Low generation due to weather/snow.
Kohls - Bensalem | PA | 21559 | 21314 | 245 | 1.149% | 19869.12 | 1689.88 | 8.505%
Kohls - Brick | NJ | 26427 | 26353 | 74 | 0.2808% | 22576.31 | 3850.69 | 17.06% | 1.Inverter was offline on 02/20 due to Asymmetrical Array fault and back online on 02/21. | 1.SR097572
Kohls - Buffalo | NY | 0 | N/A |  |  | 15384.12 | -15384.12 | -100% | 1.Site stopped communicating on 02/01 at 2:55 AM and remained throughout the month due to a faulty modem, which needs to be replaced | 1.SR093917, SR096145 | SR096145
Kohls - Canton | CT | 3054 | 3024 | 30 | 0.9921% | 6988.56 | -3934.56 | -56.3% | 1. Low generation due to weather/snow.
Kohls - East Amherst | NY | 2866 | 2809 | 57 | 2.029% | 14254.84 | -11388.84 | -79.89% | 1. Low generation due to weather/snow.
Kohls - East Brunswick | NJ | 30213 | 29916 | 297 | 0.9928% | 30775.12 | -562.12 | -1.827%
Kohls - Edgewood | MD | 154536 | 152366 | 2170 | 1.424% | 168198.51 | -13662.51 | -8.123%
Kohls - Granite Run | PA | 19693 | 19475 | 218 | 1.119% | 20063.53 | -370.53 | -1.847%
Kohls - Greece | NY | 2104 | 2081 | 23 | 1.105% | 14838 | -12734 | -85.82% | 1. Low generation due to weather/snow.
Kohls - Hanover | PA | 23392 | 23170 | 222 | 0.9581% | 22286.93 | 1105.07 | 4.958%
Kohls - Horsehead | NY | 8908 | 8781 | 127 | 1.446% | 16013.56 | -7105.56 | -44.37% | 1. Low generation due to weather/snow.
Kohls - Hudson | NY | 13755 | 13674 | 81 | 0.5924% | 18577.58 | -4822.58 | -25.96% | 1. Low generation due to weather/snow.
Kohls - Ithaca | NY | 9593 | 9513 | 80 | 0.841% | 17763.02 | -8170.02 | -45.99% | 1. Low generation due to weather/snow.
Kohls - Kingston | NY | 14849 | 14753 | 96 | 0.6507% | 24603.49 | -9754.49 | -39.65% | 1. Low generation due to weather/snow.
Kohls - Mechanicsburg | PA | 26048 | 25759 | 289 | 1.122% | 25206.74 | 841.26 | 3.337%
Kohls - Middletown | NJ | 39815 | 39153 | 662 | 1.691% | 36153.03 | 3661.97 | 10.13%
Kohls - North Amherst | NY | 0 | N/A |  |  | 12403.57 | -12403.57 | -100% | 1. Site tripped offline at 09:30am from 08/12/24, due to system removal for roof repair and to start rebuilding the roof. | 1.SR093440,SR093861 | SR093861
Kohls - Staten Island | NY | 18864 | N/A |  |  | 21195.82 | -2331.82 | -11% | 1.Inverter 7 tripped offline at 1:20 on 01/10 and powerfactors was onsite on 02/19 RMA'd inverer 21 got inverter 7 back online at 14:50 on 02/19. Inverter 8 was offline due to Internal hardware “Error E018” fault till date. Inverter 20 was offline from 07/22/24 due to Internal Error -E018 fault. Inverter 21 was tripped offline at 09:05Am on 08/17/24 due to Internal Error - E018 fault and was being RMA'd. Inverter 10 was offline from 02/04 due to Standby mode fault and back online at 11:55 on 02/20 after technician check-in. | 1.SR095623
Kohls - Warminster | PA | 25644 | 25329 | 315 | 1.244% | 24459.22 | 1184.78 | 4.844%
Kohls - Waterbury | CT | 5561 | 5527 | 34 | 0.6152% | 19364.12 | -13803.12 | -71.28% | 1. Meter reporting no production since 02/17, required health check. | 1. SR097907
Mojave Water Agency - Headquarters | CA | 30686 | 30622 | 64 | 0.209% | 25387.84 | 5298.16 | 20.87%
CSU - Bakersfield | CA | 84513 | 83948 | 565 | 0.673% | 78007.26 | 6505.74 | 8.34%
Greenfield USD - Fairfield ES | CA | 9238 | 9174 | 64 | 0.6976% | 8281.63 | 956.37 | 11.55%
Greenfield USD - Granite Point ES | CA | 26786 | 26688 | 98 | 0.3672% | 21722.5 | 5063.5 | 23.31%
Greenfield USD - Greenfield MS | CA | 10577 | N/A |  |  | 14936.35 | -4359.35 | -29.19% | 1. Inverter PAD 1 was still not communicating, and as of 01/27/25, production is not being recorded at the meter. The issue may be due to the need for a new MOXA device, and serial port 2 of the data logger is malfunctioning. To restore functionality, the data logger needs to be replaced, or an Nport 2 device can be installed to isolate this equipment from the data logger. | 1.SR089763
Greenfield USD - Horizon ES | CA | 23654 | 23552 | 102 | 0.4331% | 22188.52 | 1465.48 | 6.605%
Greenfield USD - McKee MS | CA | 11221 | 11188 | 33 | 0.295% | 13575.99 | -2354.99 | -17.35% | 1. Low generation due to weather/snow.
Greenfield USD - Plantation ES | CA | 10887 | 10842 | 45 | 0.4151% | 9687.94 | 1199.06 | 12.38%
Greenfield USD - Planz ES | CA | 4344 | 4317 | 27 | 0.6254% | 11305.56 | -6961.56 | -61.58% | 1. Low generation due to weather/snow.
Greenfield USD - Raffaello Palla ES | CA | 25408 | 24947 | 461 | 1.848% | 24477.22 | 930.78 | 3.803%
Greenfield USD - Valle Verde ES | CA | 28417 | 28235 | 182 | 0.6446% | 22933.04 | 5483.96 | 23.91%
Greenfield USD - W.A. Kendrick ES | CA | 4551 | N/A |  |  | 8833.13 | -4282.13 | -48.48% | 1.Meter reporting half of inverter production since 6/11/22 waiting for client approval for investigation | 1. SR094440
Muroc Joint USD - Boron HS | CA | 0 | N/A |  |  | 24557.19 | -24557.19 | -100% | 1. Site back communication at 9:15AM on 12/30/2024 and Inverter remains offline because of Inverter down hard - Power supply critical failure. 2. Weather station began reporting erroneous values on 12/30/2024, and the POA sensor needed to be replaced along with additional repairs. | 1. SR095163, SR092023 & SR089707 2. SR093065 | SR092023 | SR089707 | SR093065
Muroc Joint USD - W. Boron ES | CA | 10005 | 9979 | 26 | 0.2605% | 9080.59 | 924.41 | 10.18%
Colusa - WTP | CA | 0 | N/A | 0 |  | 22973.3 | -22973.3 | -100% | 1. Site came back online at 09:40 AM on 02/11/25 after the technician replaced four air filters in the central inverter. Meter replacement is required. 2. Site has been offline since 02/13/25 and the site was under water may not self-resolve. On 02/28/25, the technician found the inverter displaying a 0020 fault code (Delta High Temp Warning). The manual advises contacting the manufacturer for this code. Emailed Bold Renewables for guidance and will update once they respond with a solution. | 1.SR089464, SR093180, SR093174 & SR095356 2. SR096916 | SR093180 | SR093174 | SR095356 | SR096916
CDCR-North Kern State Prision | CA | 73603 | 73023 | 580 | 0.7943% | 105876.17 | -32273.17 | -30.48% | 1. Inverter 2 was taken offline from 09:15 AM to 12:25 PM on 02/05/25. The technician met with a BOLD technician to refill the coolant. 2. Inverter 1 was taken offline from 08:45 AM to 11:30 AM on 02/06/25. The technician met with a BOLD technician to refill the coolant, and all other inverters have been filled to normal limits 3. Inverter 2 was derating by 50kW due to two non-working fans. On 02/28/25, the technician restored expected production by replacing fans 6 and 9. 4. 43 Damaged (Thermal) SF 290-36-P Modules onsite, needed replacement. | 1. SR092739 2. SR092739 3. SR096514 4. SR092753 | SR092739 | SR096514
Muroc Joint USD - District Office | CA | 5000 | 16305 | -11305 | -69.33% | 6384.23 | -1384.23 | -21.68% | 1. Low generation due to weather/snow.
Whole Foods - Manhattan Beach | CA | 12818 | 12781 | 37 | 0.2895% | 15625.72 | -2807.72 | -17.97% | 1. Inverters 3 & 8 are offline through out the month due to additional parts needed. On 02/26/25, FIMER tested replacement logic boards, but they failed their internal bench tests. They have not been able to address our needs, and no ETA is available yet. 2. Inverter 9 has been offline since 02/25. | 1. SR089461, SR090375 2. SR098018 | SR090375 | SR098018
Pioneer USD - Frontier ES | CA | 20603 | N/A |  |  | 18600.14 | 2002.86 | 10.77% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. Waiting for approval to dispatch. | 1. SR092276
Pioneer USD - Pioneer ES | CA | 13168 | N/A |  |  | 19124.83 | -5956.83 | -31.15% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. 2. Pad 1 inverter 1 was offline through the month and pad 2 the inverter 1 is not communicating but production is at the meter. Waiting for approval to dive into auxiliary equipment installed and fault logs with BOLD. 3. Site was taken offline from 09:00 AM to 12:55 PM on 02/26/25. The technician worked on the PM and confirmed that we cannot gather data normally. We will need to perform a deep dive with BOLD on the power flow through the distribution card. | 1. SR085968 2. SR092256, SR090090 & SR095592 3. SR095592 | SR092256 | SR090090 | SR095592 | SR095592
Pioneer USD - Pioneer MS | CA | 28036 | N/A |  |  | 25858.58 | 2177.42 | 8.42% | 1. Weather station is not communicating through out the month, It was found that the pyranometer is not installed on-site. The installation of a new pyranometer will be required. | 1. SR089470, SR092603 | SR092603
Kingsburg Joint UHSD - Kingsburg HS | CA | 45118 | 42299 | 2819 | 6.664% | 48811.98 | -3693.98 | -7.568% | 1. Inverter A and Meter A have faulty MOXAs, which need to be replaced. Additionally, the low-hanging wires were managed and secured. 2. Meter B regulary capturing data from 7:20AM to 10:00AM respective with Inverter B, but Inverter B capturing data from 10:05AM to 4:45PM due to MOXA is not working. | 1.SR089612, SR095339 & SR095385, SR097012 2. SR089612, SR095385 | SR095339 | SR095385 | SR097012 | SR089612 | SR095385
CADRB | CA | 0 | N/A |  |  | 443850 | -443850 | -100% | 1. Site back online on 01/09/25 after the technician re-energized it, we cannot confirm as silicon ranch only has access to site. 2.Inverter 3 was back online on 11/15/2024 but we cannot confirm through SCADA since site is not communicating 3.Pyranometer has been giving bad readings. Prior to 9/25, the pyranometer read at most 450 W/m2. Since then, readings are between 950 and 400 W/m2 | 1. SR092166, SR097558 2. SR086220 3. SR091312 | SR097558 | SR086220 | SR091312
CDCR-CA State Prison LA County | CA | 176892 | 176553 | 339 | 0.192% | 272714.69 | -95822.69 | -35.14% | 1. Low generation due to weather/snow.
Central USD Akers ES | CA | 19588 | N/A |  |  | 21273.81 | -1685.81 | -7.924% | 1. Weather station is reporting 0w/m2 | 1. SR090370
CUSD - District Office | CA | 16350 | 16305 | 45 | 0.276% | 16036.59 | 313.41 | 1.954% | 1. Inverter 1 has been offline since 02/27/25 due to an watchdog timer fault and remained offline through out the month. | 1. SR097912
Parlier - WTP | CA | 28581 | 28488 | 93 | 0.3265% | 41703.35 | -13122.35 | -31.47% | 1. Low generation due to weather/snow.
Snowline SD - Quail Valley MS | CA | 25219 | 25156 | 63 | 0.2504% | 24415.41 | 803.59 | 3.291% | 1. Inverter trips on and offline through out the month frequently due to company chip replacement needed and Wires are all hanging and in poor condition. | 1.SR090965, SR094547 & SR094545 | SR094547 | SR094545
Snowline SD - Serrano HS - Middle Lot | CA | 21035 | 21014 | 21 | 0.09993% | 28500.77 | -7465.77 | -26.19% | 1. Low generation due to weather/snow.
Snowline SD - Pinon Hills ES | CA | 9673 | 9665 | 8 | 0.08277% | 14901.16 | -5228.16 | -35.09% | 1. 23 Modules need to be replace. | 1. SR090734
Ramona - Santa Maria WTP | CA | 53315 | 52951 | 364 | 0.6874% | 56951.14 | -3636.14 | -6.385%
Kohls - Redding | CA | 19554 | N/A |  |  | 16190.84 | 3363.16 | 20.77% | 1. Weather station does not report irradiance during the day. Likely a faulty pyranometer through out the month. Waiting for approval | 1. SR090293, SR095854 | SR095854
Kohls - Salinas | CA | 23764 | 23421 | 343 | 1.464% | 26628.06 | -2864.06 | -10.76% | 1.Inverters 3, 7, 10, 11, 14, and 21 are offline. Inverter 2 may have a string down through out the month and parts are needed to bring these inverters back online. | 1. SR095449, SR093474, SR089474, SR090381 & SR090380 | SR093474 | SR089474 | SR090381 | SR090380
Kohls - San Bernardino - Central | CA | 104632 | 104199 | 433 | 0.4156% | 119205.82 | -14573.82 | -12.23%
Kohls - Sonora | CA | 17057 | 16889 | 168 | 0.9947% | 17675.44 | -618.44 | -3.499% | 1.Inverter 3 has been offline since 01/28/25, remained offline through out the month due to additional parts needed. 2. Inverter 7 was offline through out the month and parts needed to bring these inverter back online. 3. Inverter 12 has been offline since 01/30/25, remaind offline through out the month and parts are needed to bring these inverter back online. | 1. SR089477, SR096348 2. SR089477, SR096348 3. SR089477, SR096348 | SR096348 | SR089477 | SR096348 | SR089477 | SR096348
CUSD - Stratford ES | CA | 17954 | 17907 | 47 | 0.2625% | 14369.22 | 3584.78 | 24.95% | 1. Low generation due to weather/snow.
Taft - City Hall | CA | 2255 | 133 | 2122 | 1595% | 5204.36 | -2949.36 | -56.67% | 1. Low generation due to weather/snow.
Taft - Federal Prison | CA | 12088 | 12046 | 42 | 0.3487% | 8981.22 | 3106.78 | 34.59% | 1. Low generation due to weather/snow.
Taft - Police Department | CA | 7698 | 7558 | 140 | 1.852% | 5975.61 | 1722.39 | 28.82% | 1. Low generation due to weather/snow.
Taft - WTP | CA | 12661 | 12626 | 35 | 0.2772% | 39816.16 | -27155.16 | -68.2% | 1. Inverter 2 was brought back online at 11:20 AM on 02/21/25 after the technician replaced 5 filters inside the inverter and swapped the logic board with a new one received from Bold. | 1. SR089732, SR094323 | SR094323
CDCR - CA Correctional Institution | CA | 94563 | 94052 | 511 | 0.5433% | 111535.07 | -16972.07 | -15.22% | 1. Site has been offline since 07:40 AM on 02/25/25 and may remain offline throughout the month, possibly due to issues with the arrays at the switchgear. 2. Inverter 1 production is being affected in the morning hours due to stuck trackers. | 1. SR097774 2. SR092170, SR092456 | SR092170 | SR092456
CDCR - CA Correctional Institution II | CA | 112446 | 109184 | 3262 | 2.988% | 177907.85 | -65461.85 | -36.8% | 1. Inverter 2's production being affected in the afternoon hours possibly due to stuck trackers. 2. Inverter 1 was underperforming and needs to have its surge protectors replaced. | 1. SR092171, SR092455 2. SR090296 | SR092455 | SR090296
Snowline SD - Vista Verde ES | CA | 21035 | 21008 | 27 | 0.1285% | 17891.25 | 3143.75 | 17.57%
North Stonington | CT | 908110 | N/A |  |  | 0 | 908110 |  | 1. Inverter A.02.08 back online at 14:10 on 02/03/25, after technician Re-energized the inverter by closing the Combiner handle. | 1. SR096146

## Mar
Silicon Ranch |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3832546 | 2419110 | 1413436 | 58.43% | 3740512.198 | 92033.802 | 2.46%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT | 27222 | 27081 | 141 | 0.5207% | 24890.44 | 2331.56 | 9.367%
Kohls - Auburn | NY | 27236 | 27027 | 209 | 0.7733% | 23650.08 | 3585.92 | 15.16%
Kohls - Bensalem | PA | 34738 | 30227 | 4511 | 14.92% | 29689.14 | 5048.86 | 17.01% | 1. Site has been intermittently communicating throught the month and later data will backfill, due to a faulty modem, which needs replacement. The last update was on 03/30/25 | 1. SR098590
Kohls - Brick | NJ | 43073 | 41247 | 1826 | 4.427% | 35597.95 | 7475.05 | 21%
Kohls - Buffalo | NY | 24986 | N/A |  |  | 30971.89 | -5985.89 | -19.33% | 1. Inverter 4 is offline throught the month due to an INV 4 was thermally damaged in the DC box. 2. Inverter 7 back online at 13:25 on 03/13/25, after the technician isolated the strings, reset the system, and conducted a thorough inspection using thermal imaging, addressing any visible issues, which led to the inverter being brought back online. 3. Inverter 5 derating to about 19kw, most operating around 22Kw since 03/11/25. | 1. SR096145, SR096237 2. SR095177, SR096145 3. SR095177 | SR096237 | SR095177 | SR096145 | SR095177
Kohls - Canton | CT | 13827 | 13665 | 162 | 1.186% | 11101.61 | 2725.39 | 24.55%
Kohls - East Amherst | NY | 30527 | 30163 | 364 | 1.207% | 28509.69 | 2017.31 | 7.076%
Kohls - East Brunswick | NJ | 48343 | 48083 | 260 | 0.5407% | 45835.09 | 2507.91 | 5.472%
Kohls - Edgewood | MD | 250847 | 249117 | 1730 | 0.6945% | 237369.73 | 13477.27 | 5.678%
Kohls - Granite Run | PA | 33109 | 32909 | 200 | 0.6077% | 29284.8 | 3824.2 | 13.06%
Kohls - Greece | NY | 26115 | 25812 | 303 | 1.174% | 27398.92 | -1283.92 | -4.686%
Kohls - Hanover | PA | 37630 | 37388 | 242 | 0.6473% | 32189.09 | 5440.91 | 16.9%
Kohls - Horsehead | NY | 25246 | 25033 | 213 | 0.8509% | 24714.57 | 531.43 | 2.15%
Kohls - Hudson | NY | 29884 | 29691 | 193 | 0.65% | 29518.63 | 365.37 | 1.238%
Kohls - Ithaca | NY | 24987 | 24837 | 150 | 0.6039% | 27056.43 | -2069.43 | -7.649%
Kohls - Kingston | NY | 38808 | 38452 | 356 | 0.9258% | 41394.59 | -2586.59 | -6.249%
Kohls - Mechanicsburg | PA | 43003 | 42690 | 313 | 0.7332% | 37183.53 | 5819.47 | 15.65%
Kohls - Middletown | NJ | 63442 | 62840 | 602 | 0.958% | 52641.66 | 10800.34 | 20.52%
Kohls - North Amherst | NY | 0 | N/A |  |  | 25362.51 | -25362.51 | -100% | 1. Site tripped offline at 09:30am from 08/12/24, due to system removal for roof repair and to start rebuilding the roof. | 1.SR093440,SR093861 | SR093861
Kohls - Staten Island | NY | 29577 | N/A |  |  | 31812.12 | -2235.12 | -7.026% | 1. Inverter 8 was offline due to Internal hardware “Error E018” fault till date. Inverter 20 was offline from 07/22/24 due to Internal Error -E018 fault. Inverter 21 was tripped offline at 09:05Am on 08/17/24 due to Internal Error - E018 fault and was being RMA'd. 2. Site was offline from 03/05/25 due to a defective DAS mini transformer and blown in-line fuses. On 03/10/25, the technician temporarily powered the DAS for site visibility but required a quote for the replacement transformer and fuses. The site was brought back online at 13:20 the same day. It went offline again on 03/17/25 at 19:50, came back online on 03/19/25, went offline on 03/20/25, returned on 03/24/25, and went offline again on 03/27/25, remaining offline throughout the rest of the month. | 1. SR095623 2. SR098185 | SR098185
Kohls - Warminster | PA | 43847 | 43555 | 292 | 0.6704% | 36323.74 | 7523.26 | 20.71%
Kohls - Waterbury | CT | 31429 | 31084 | 345 | 1.11% | 28363.71 | 3065.29 | 10.81% | 1. Meter has been reporting no production since 02/17/25. On 03/03/25, the technician power-cycled the inverter to restore production, but communication was not regained. However, the meter regained communication and confirmed production. | 1. SR097907
Mojave Water Agency - Headquarters | CA | 41136 | 35134 | 6002 | 17.08% | 35355.28 | 5780.72 | 16.35% | 1. Meter lost communication on 03/25/25 but production confirmed at Inverter level. | 1. SR098973
CSU - Bakersfield | CA | 127698 | 127167 | 531 | 0.4176% | 118489.14 | 9208.86 | 7.772%
Greenfield USD - Fairfield ES | CA | 12306 | 12229 | 77 | 0.6297% | 11131.02 | 1174.98 | 10.56%
Greenfield USD - Granite Point ES | CA | 31850 | 31733 | 117 | 0.3687% | 29325.79 | 2524.21 | 8.607%
Greenfield USD - Greenfield MS | CA | 20842 | 19199 | 1643 | 8.558% | 20074.448 | 767.552 | 3.824% | 1. Inverter PAD 1 was still not communicating, but as of 13:20 on 03/03/25, production is being recorded at the meter. The issue may be related to the need for a new MOXA device to restore communication with the inverter. | 1. 1.SR089763
Greenfield USD - Horizon ES | CA | 31986 | 31852 | 134 | 0.4207% | 30176.01 | 1809.99 | 5.998%
Greenfield USD - McKee MS | CA | 15740 | 15698 | 42 | 0.2676% | 18447.54 | -2707.54 | -14.68% | 1. Site production was low on 03/06, 03/13, 03/14, 03/17, due to rain.
Greenfield USD - Plantation ES | CA | 15097 | 15047 | 50 | 0.3323% | 13199.13 | 1897.87 | 14.38%
Greenfield USD - Planz ES | CA | 6098 | 6057 | 41 | 0.6769% | 14752.51 | -8654.51 | -58.66% | 1. Inverter 1 meter has been down for a while. On 03/14, the technician replaced the modem and power cable but faced issues requiring GPM IT escalation. Further meter investigation is scheduled for 04/04/25. | 1. SR092298
Greenfield USD - Raffaello Palla ES | CA | 27537 | 27181 | 356 | 1.31% | 32869.15 | -5332.15 | -16.22% | 1. Meter reporting zero from 03/30, production can be confirmed at inverter level. | 1. SR099206
Greenfield USD - Valle Verde ES | CA | 38141 | 37743 | 398 | 1.055% | 30782.66 | 7358.34 | 23.9%
Greenfield USD - W.A. Kendrick ES | CA | 0 | N/A |  |  | 11866.35 | -11866.35 | -100% | 1.Meter reporting half of inverter production since 6/11/22 waiting for client approval for investigation | 1. SR094440
Muroc Joint USD - Boron HS | CA | 0 | N/A |  |  | 35271.9 | -35271.9 | -100% | 1. Site back communication at 9:15AM on 12/30/2024 and Inverter remains offline because of Inverter down hard - Power supply critical failure. 2. Weather station began reporting erroneous values on 12/30/2024, and the POA sensor needed to be replaced along with additional repairs. | 1. SR095163, SR092023 & SR089707 2. SR093065 | SR092023 | SR089707 | SR093065
Muroc Joint USD - W. Boron ES | CA | 12937 | 12898 | 39 | 0.3024% | 13034.03 | -97.03 | -0.7444%
Colusa - WTP | CA | 0 | N/A |  |  | 42715.56 | -42715.56 | -100% | 1. Site came back online at 09:40 AM on 02/11/25 after the technician replaced four air filters in the central inverter. Meter replacement is required. 2. Site has been offline since 02/13/25 and the site was under water may not self-resolve. On 02/28/25, the technician found the inverter displaying a 0020 fault code (Delta High Temp Warning). The manual advises contacting the manufacturer for this code. Emailed Bold Renewables for guidance and will update once they respond with a solution and remained offline throught the month. | 1.SR089464, SR093180, SR093174 & SR095356 2. SR096916 | SR093180 | SR093174 | SR095356 | SR096916
CDCR-North Kern State Prision | CA | 93451 | 92801 | 650 | 0.7004% | 149687 | -56236 | -37.57% | 1. Inverter 1 tripped offline on 03/02/25 due to an "Asymetrical Array Fault" and back online on 03/03/25. 2. Inverter 3 has been offline since 03/13/25 due to an "Asymetrical Array Fault" and self resolved on 03/17/25. 3. Inverter 2 has been offline since 03/14/25 due to an "Ground Overcurrent Fault" and self resolved at 10:05AM on 03/17/25. 4. 43 Damaged (Thermal) SF 290-36-P Modules onsite are needed for replacement. | 1. SR097976 2. SR098524 3. SR098586 4. SR092753 | SR098524 | SR098586 | SR092753
Muroc Joint USD - District Office | CA | 6507 | 6502 | 5 | 0.0769% | 9177.56 | -2670.56 | -29.1% | 1. Site production was low on 03/12 to 03/14 and 03/17 due to rain.
Whole Foods - Manhattan Beach | CA | 15343 | 15307 | 36 | 0.2352% | 19210.44 | -3867.44 | -20.13% | 1. Inverters 3 & 8 are offline through out the month due to additional parts needed. On 02/26/25, FIMER tested replacement logic boards, but they failed their internal bench tests. They have not been able to address our needs, and no ETA is available yet. 2. Inverter 9 has been offline since 02/25/25, remaind offline through out the month and parts are needed to bring these inverter back online. | 1. SR089461, SR090375 2. SR098018 | SR090375 | SR098018
Pioneer USD - Frontier ES | CA | 27246 | N/A |  |  | 30695.13 | -3449.13 | -11.24% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. Waiting for approval to dispatch. | 1. SR092276
Pioneer USD - Pioneer ES | CA | 16433 | N/A |  |  | 31485.33 | -15052.33 | -47.81% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. 2. Pad 1 Inverter 1 was offline throughout the month, and on Pad 2, Inverter 1 is not communicating, although production data is being captured at the meter. On 03/13/25, it was approved to investigate the auxiliary equipment installed and the fault logs, with BOLD. | 1. SR085968 2. SR092256, SR090090 & SR095592 | SR092256 | SR090090 | SR095592
Pioneer USD - Pioneer MS | CA | 38016 | N/A |  |  | 42362.63 | -4346.63 | -10.26% | 1. Weather station is not communicating through out the month, It was found that the pyranometer is not installed on-site. The installation of a new pyranometer will be required. | 1. SR089470, SR092603 | SR092603
Kingsburg Joint UHSD - Kingsburg HS | CA | 59485 | 59102 | 383 | 0.648% | 60055.14 | -570.14 | -0.9494% | 1. Inverter A and Meter A have faulty MOXAs, which need to be replaced. Additionally, the low-hanging wires were managed and secured. 2. Meter B is regularly capturing data from 7:20 AM to 10:00 AM, in sync with Inverter B. However, Inverter B is capturing data from 10:05 AM to 4:45 PM due to the MOXA not functioning. On 04/01/25, the technician installed the MOXA (datalogger), but the communication failed, and additional troubleshooting is required.. | 1.SR089612, SR095339 & SR095385, SR097012 2. SR089612, SR095385 | SR095339 | SR095385 | SR097012 | SR089612 | SR095385
CADRB | CA | 0 | N/A |  |  | 700582 | -700582 | -100% | 1. Site back online on 01/09/25 after the technician re-energized it, we cannot confirm as silicon ranch only has access to site. 2.Inverter 3 was back online on 11/15/2024 but we cannot confirm through SCADA since site is not communicating 3.Pyranometer has been giving bad readings. Prior to 9/25, the pyranometer read at most 450 W/m2. Since then, readings are between 950 and 400 W/m2 | 1. SR092166, SR097558 2. SR086220 3. SR091312 | SR097558 | SR086220 | SR091312
CDCR-CA State Prison LA County | CA | 244891 | 244501 | 390 | 0.1595% | 414816.78 | -169925.78 | -40.96% | 1. Inverter 1 is not communicating, and according to the meter data, it is offline due to a breaker issue. A case was raised on 03/24/25 to request support for the breaker replacement. | 1. SR098397
Central USD Akers ES | CA | 27626 | N/A |  |  | 32689.27 | -5063.27 | -15.49% | 1. Meter loses communications intermittently. Inverter is reporting production 2. Weather station is reporting 0w/m2 | 1. SR098178 2. SR090370 | SR090370
CUSD - District Office | CA | 18359 | 18293 | 66 | 0.3608% | 25627.51 | -7268.51 | -28.36% | 1. Inverter 1 was back online at 12:55 on 03/04/25 after the technician pulled log files. It tripped offline again on 03/18/25 due to a watchdog timer fault and remained offline for the rest of the month. 2. Inverter 3 tripped offline at 13:45 on 03/04/25 during repairs for a burnt feeder cable, with a power distribution card failure. It was down until 03/09/25, then tripped offline again at 09:55 on 03/10/25, and was back online on 03/11/25. | 1. SR097912, SR098713 2. SR097912, SR098177 | SR098713 | SR097912 | SR098177
Parlier - WTP | CA | 44130 | 44845 | -715 | -1.594% | 67783.57 | -23653.57 | -34.9% | 1. Site production was low on 03/05, 03/12 to 03/14, 03/17 and 03/31 due to rain.
Snowline SD - Quail Valley MS | CA | 31558 | 30072 | 1486 | 4.941% | 38526.15 | -6968.15 | -18.09% | 1.Inverter trips frequently. On 03/17/25, the technician replaced the comms card at 11:30, connected to the inverter, and pulled log files. The manufacturer requires a full day of operation to diagnose the issue. The inverter was back online by 13:05 but lost communication. Production can be verified at the meter, and further troubleshooting is needed to restore communication and resolve the intermittent tripping | 1. SR094545
Snowline SD - Serrano HS - Middle Lot | CA | 29924 | 29893 | 31 | 0.1037% | 45412.66 | -15488.66 | -34.11% | 1. Site production was low on 03/05 and 03/11 due to rain.
Snowline SD - Pinon Hills ES | CA | 12241 | 12228 | 13 | 0.1063% | 22548.89 | -10307.89 | -45.71% | 1. 23 modules need replacement; quote declined by client on 11/07/24 | 1. SR090734
Ramona - Santa Maria WTP | CA | 60198 | 60025 | 173 | 0.2882% | 73955.59 | -13757.59 | -18.6% | 1. Inverter 1 offline from 10:20 to 12:35 on 03/17 for surge trap replacement by technician | 1. SR095418
Kohls - Redding | CA | 26682 | 33 | 26649 | 80755% | 27704.87 | -1022.87 | -3.692% | 1. Weather station does not report irradiance during the day. Likely a faulty pyranometer through out the month. Waiting for approval 2. Inverter 1 tripped offline at 13:15 on 03/31 due to a Xantrex fault (state 592: "contactor open") and remained offline for the rest of the month. | 1. SR090293, SR095854 2. SR099225 | SR095854 | SR099225
Kohls - Salinas | CA | 32438 | 33147 | -709 | -2.139% | 44625.2 | -12187.2 | -27.31% | 1.Inverters 3, 7, 10, 11, 14, and 21 are offline. Inverter 2 may have a string down through out the month and parts are needed to bring these inverters back online. | 1. SR098183, SR095449, SR093474, SR090380 & SR089474. | SR095449 | SR093474 | SR090380 | SR089474
Kohls - San Bernardino - Central | CA | 125505 | 124749 | 756 | 0.606% | 144411.94 | -18906.94 | -13.09% | 1. Inverter 1 has been underperforming by 90kW since 11:40 on 08/21/24. During the Annual Preventative Maintenance on 03/24/25, the technician found poor filters and a potential hazard with the AC switch. New filters are needed to restore performance. 2. Site was offline from 09:35 to 13:15 on 03/24/25 for the Full Annual Preventative Maintenance Inspection. | 1. SR098826, PM11103 2. PM11103
Kohls - Sonora | CA | 22795 | 22949 | -154 | -0.6711% | 29362.56 | -6567.56 | -22.37% | 1.Inverter 3 has been offline since 01/28/25, remained offline through out the month due to additional parts needed. 2. Inverter 7 was offline through out the month and parts needed to bring these inverter back online. 3. Inverter 12 has been offline since 01/30/25, remaind offline through out the month and parts are needed to bring these inverter back online. | 1. SR089477, SR096348 2. SR089477, SR096348 3. SR089477, SR096348 | SR096348 | SR089477 | SR096348 | SR089477 | SR096348
CUSD - Stratford ES | CA | 22274 | 22810 | -536 | -2.35% | 21294.17 | 979.83 | 4.601%
Taft - City Hall | CA | 804 | 20 | 784 | 3920% | 7164.9 | -6360.9 | -88.78% | 1. Metering Energy values are much lower than expected vs meter Power. | 1. SR097948
Taft - Federal Prison | CA | 15160 | 15708 | -548 | -3.489% | 11796.07 | 3363.93 | 28.52%
Taft - Police Department | CA | 9954 | 10331 | -377 | -3.649% | 8217.27 | 1736.73 | 21.14%
Taft - WTP | CA | 18961 | 52793 | -33832 | -64.08% | 32643.96 | -13682.96 | -41.92% | 1. Meter was not communicating production at the inverters. so we considered inverter productionas site production. | 1. SR095559
CDCR - CA Correctional Institution | CA | 128121 | 123570 | 4551 | 3.683% | 106071.03 | 22049.97 | 20.79% | 1. Site was back online at 14:00 on 03/03/25 after the technician reset the breaker 2. Inverter 1 production is being affected in the morning hours due to stuck trackers. 3. Site was taken offline from 07:40 on 03/25/25 for generator testing and was brought back online at 09:30 on 03/27/25 after the technician re-energized it. | 1. SR097774 2. SR092170, SR092456 3. SR098476, SR096410 | SR092170 | SR092456 | SR098476 | SR096410
CDCR - CA Correctional Institution II | CA | 110462 | 161849 | -51387 | -31.75% | 166152.23 | -55690.23 | -33.52% | 1. Inverter 2's production being affected in the afternoon hours possibly due to stuck trackers. 2. Inverter 1's production increased slightly on 03/18/25 after the technician replaced the faulty surge protectors with new ones. 3. Inverter 2 tripped offline at 09:15 AM on 03/17/25 due to a FAN 5 FAULT and returned online at 07:45 AM on 03/18/25. It tripped again at 10:50 AM and came back online at 12:20 PM after the technician cleared the fault. The inverter continued to trip offline on 03/28, 03/29,03/30 and 03/31 around 09:00 AM due to the same issue. FAN 5 needs to be replaced to restore expected production. 4. Inverter 3 is underperforming by approximately 200 kW. On 03/27/25, the technician found two faulty fuses and burnt negative homeruns at combiner box 3.3. These were isolated, and the inverter was power-cycled and brought back online at 14:15. Additional troubleshooting is required to restore expected production. | 1.SR092171, SR092455 2. SR090296 3. SR098666 4. SR098778 | SR092455 | SR090296 | SR098666 | SR098778
Snowline SD - Vista Verde ES | CA | 4758 | 4743 | 15 | 0.3163% | 28101.91 | -23343.91 | -83.07% | 1. Inverter 1 has been offline since 03/08/25 due to a watchdog timer fault and remained offline throughout the month. | 1. SR098343
North Stonington | CT | 1279980 | N/A |  |  | 0 | 1279980 |  | 1. The site experienced an outages on 03/02/25 from 08:00AM to 03:30PM, On 03/10/25 from 02:00PM to 04:30PM due to PG&E curtailments. 2. Block A01 tripped offline at 7:20 AM on 03/11/25. On 03/12/25, the technician found that transformer 1 had a blown B-phase bayonet fuse. After replacing the fuse, all equipment on Pad 1 was restored at 08:50AM the same day. 3. The technician inspected the transformer 2, took a DGA sample for testing, and confirmed all gauges are within the acceptable range. The transformer appears to be in great condition. | 1.SR097960, SR098350 2.SR098382 3.SR098434 | SR098350 | SR098382 | SR098434

## Apr
Silicon Ranch |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 4382595.68 | 2627220 | 1755375.68 | 66.81% | 4664869.299 | -282273.619 | -6.051%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT | 31293 | 31163 | 130 | 0.4172% | 30934.86 | 358.14 | 1.158%
Kohls - Auburn | NY | 32335 | 32105 | 230 | 0.7164% | 33859.88 | -1524.88 | -4.504%
Kohls - Bensalem | PA | 25179 | 24905 | 274 | 1.1% | 33628.71 | -8449.71 | -25.13% | 1. Site has communicated intermittently throughout the month due to a faulty modem, with data expected to backfill later. On 04/17/2024, the technician found the inverter online and producing, but the cell modem's indicator lights were not flashing, indicating no data transmission. DAS was power cycled with no change. Multiple attempts to contact Green Power Monitor for support went unanswered. The modem had been previously replaced and updated with a new IP address, suggesting a possible SIM card or data issue. The site last update was on 04/24/25. | 1.SR098590
Kohls - Brick | NJ | 43757 | 38574 | 5183 | 13.44% | 40857.57 | 2899.43 | 7.096%
Kohls - Buffalo | NY | 35454 | N/A |  |  | 43977.12 | -8523.12 | -19.38% | 1. Inverter 4 is offline throught the month due to an INV 4 was thermally damaged in the DC box. 2. Inverter 5 derating to about 19kw, most operating around 22Kw since 03/11/25. | 1.SR096145, SR096237 2. SR095177 | SR096237 | SR095177
Kohls - Canton | CT | 15599 | 15474 | 125 | 0.8078% | 13622.22 | 1976.78 | 14.51%
Kohls - East Amherst | NY | 33923 | 33484 | 439 | 1.311% | 38691.72 | -4768.72 | -12.32% | 1. Inverter 1 tripped offline at 10:50 AM on 04/29/25 due to an "Sleep state" fault and remained offline throught the month. | 1. SR100632
Kohls - East Brunswick | NJ | 51292 | 45152 | 6140 | 13.6% | 52486.96 | -1194.96 | -2.277%
Kohls - Edgewood | MD | 253311 | 251326 | 1985 | 0.7898% | 281330.29 | -28019.29 | -9.96%
Kohls - Granite Run | PA | 33656 | 33351 | 305 | 0.9145% | 33638.5 | 17.5 | 0.05202%
Kohls - Greece | NY | 30322 | 30024 | 298 | 0.9925% | 41394.59 | -11072.59 | -26.75% | 1. Low production/generation due to rain on 04/05,04/08,04/10,04/11 & 04/21
Kohls - Hanover | PA | 38762 | 38506 | 256 | 0.6648% | 39108.42 | -346.42 | -0.8858%
Kohls - Horsehead | NY | 28572 | 28360 | 212 | 0.7475% | 28509.69 | 62.31 | 0.2186%
Kohls - Hudson | NY | 32078 | 31920 | 158 | 0.495% | 32526.96 | -448.96 | -1.38%
Kohls - Ithaca | NY | 28862 | 28664 | 198 | 0.6908% | 34202.37 | -5340.37 | -15.61% | 1. Low production/generation due to rain on 04/01,04/05,04/08 & 04/10
Kohls - Kingston | NY | 42416 | 42109 | 307 | 0.7291% | 53122.43 | -10706.43 | -20.15% | 1. Low production/generation due to rain on 04/11,04/12 & 04/27
Kohls - Mechanicsburg | PA | 45237 | 44885 | 352 | 0.7842% | 45680.27 | -443.27 | -0.9704%
Kohls - Middletown | NJ | 67983 | 64693 | 3290 | 5.086% | 60239.89 | 7743.11 | 12.85%
Kohls - North Amherst | NY | 13184 | 13117 | 67 | 0.5108% | 37025.57 | -23841.57 | -64.39% | 1. Site was brought back online at 12:00 PM on 04/17/25 after Power Factor crew completed testing and energization. On 04/18/25, technician accessed the rooftop with Power Factor crew, confirmed the string with broken panels was left disconnected with the fuse holder open in the combiner box, and verified the site is online | 1. SR093861, SR100060 | SR100060
Kohls - Staten Island | NY | 29453 | N/A |  |  | 36582.56 | -7129.56 | -19.49% | 1. Inverter 8 was offline due to Internal hardware “Error E018” fault till date. Inverter 20 was offline from 07/22/24 due to Internal Error -E018 fault. Inverter 21 was tripped offline at 09:05Am on 08/17/24 due to Internal Error - E018 fault and was being RMA'd. 2. Site back online on 04/01/25 after the technician replaced the mini auxiliary power transformer. Due to layout incompatibility, the tech reconfigured the strut, used flex conduit, and pulled new conductors to the transformer and DAS. 3. Site communication at 12:05 PM on 04/05/25 and was restored at 7:25 AM on 04/08/25. On 04/09, the technician found the Radlepoint modem had no signal lights. Tech reseated all connections, antennas, and moved the SIM card from slot 1 to slot 2. Signal was restored. | 1. SR095623 2. SR098185 3. SR099451 | SR098185 | SR099451
Kohls - Warminster | PA | 43159 | 42719 | 440 | 1.03% | 41056.14 | 2102.86 | 5.122%
Kohls - Waterbury | CT | 39101 | 38771 | 330 | 0.8512% | 36953.81 | 2147.19 | 5.81%
Mojave Water Agency - Headquarters | CA | 46801 | 45206 | 1595 | 3.528% | 38772.3 | 8028.7 | 20.71% | 1. Meter regained communication on 03/29/25. | 1. SR098973
CSU - Bakersfield | CA | 147778 | 154191 | -6413 | -4.159% | 146508.14 | 1269.86 | 0.8668% | 1. Inverter 2 went offline on 04/03/25 due to a hardware fault and DPCB ISO +5V fault. On 04/04/25, the technician cleared the faults and re-energized the inverter at 2:55 PM. | 1. SR099380
Greenfield USD - Fairfield ES | CA | 13686 | 13065 | 621 | 4.753% | 14550.3 | -864.3 | -5.94%
Greenfield USD - Granite Point ES | CA | 24339 | 22902 | 1437 | 6.275% | 38398.82 | -14059.82 | -36.62% | 1. Pad 1 - inverters 1, 2 tripped offline at 6:20PM on 04/17/25 and remained offline throught the month pending for schedule queue. | 1. SR100011
Greenfield USD - Greenfield MS | CA | 24096 | 22207 | 1889 | 8.506% | 26177.669 | -2081.669 | -7.952% | 1. Inverter Pad 1 was brought back online at 15:10 on 04/30/25 after a restart limit fault was found. Technician pulled log files to send to Bold Renewables the next day and power cycled the inverter. | 1. SR100743, SR092112 & SR089763 | SR092112 | SR089763
Greenfield USD - Horizon ES | CA | 37129 | 35670 | 1459 | 4.09% | 39744.47 | -2615.47 | -6.581% | 1. Inverter 4 (Pad 2 Inv 2) was underproducing by ~20kW, showing 26kW vs. 43kW from peer inverter (Pad A Inv 1) since 01/02/25 at 12:50. On 04/15/25, technician found two strings disconnected due to broken MC4 connectors and open fuses in Combiner 1. Replaced MC4s, reconnected strings, closed fuses, and restored production to over 40kW by 11:40 AM 2. Inverter 1 ( Pad 1) has been offline since 04/27/25 due to an "Pre-Charge fault" and remained offline throught the month. | 1. SR099725 2. SR100459 | SR100459
Greenfield USD - McKee MS | CA | 18174 | 17477 | 697 | 3.988% | 24293.39 | -6119.39 | -25.19% | 1. Low production/generation due to rain on 04/26 & 04/27
Greenfield USD - Plantation ES | CA | 16955 | 16271 | 684 | 4.204% | 17353.74 | -398.74 | -2.298%
Greenfield USD - Planz ES | CA | 6726 | 6438 | 288 | 4.473% | 20901.69 | -14175.69 | -67.82% | 1. Inverter 1 meter has been down for some time. On 04/30/25, technician worked with GPM support to connect to the modem and data logger but was unsuccessful. GPM is escalating the comms issue; return visit needed. Inverter is on and producing. | 1. SR092298, SR099912 | SR099912
Greenfield USD - Raffaello Palla ES | CA | 25512 | 23739 | 1773 | 7.469% | 43062.63 | -17550.63 | -40.76% | 1. Meter reporting zero from 03/30, later from 04/06 at 13:30 meter reading its production but issue has been occurring intermittently, production can be confirmed at inverter level. | 1. SR099206
Greenfield USD - Valle Verde ES | CA | 42399 | 40587 | 1812 | 4.464% | 40204.05 | 2194.95 | 5.46%
Greenfield USD - W.A. Kendrick ES | CA | 0 | N/A |  |  | 15487.84 | -15487.84 | -100% | 1.Meter reporting half of inverter production since 6/11/22 waiting for client approval for investigation | 1. SR094440
Muroc Joint USD - Boron HS | CA | 0 | N/A |  |  | 37116.29 | -37116.29 | -100% | 1. Site back communication at 9:15AM on 12/30/2024 and Inverter remains offline because of Inverter down hard - Power supply critical failure. 2. Weather station began reporting erroneous values on 12/30/2024, and the POA sensor needed to be replaced along with additional repairs. | 1. SR095163, SR092023 & SR089707 2. SR093065 | SR092023 | SR089707 | SR093065
Muroc Joint USD - W. Boron ES | CA | 14149 | 13663 | 486 | 3.557% | 13684.78 | 464.22 | 3.392%
Colusa - WTP | CA | 0 | N/A |  |  | 54361.94 | -54361.94 | -100% | 1. Site came back online at 09:40 AM on 02/11/25 after the technician replaced four air filters in the central inverter. Meter replacement is required. 2. Site has been offline since 02/13/25 and the site was under water may not self-resolve. On 02/28/25, the technician found the inverter displaying a 0020 fault code (Delta High Temp Warning). The manual advises contacting the manufacturer for this code. Emailed Bold Renewables for guidance and will update once they respond with a solution and remained offline throught the month. 3. Meter communications have dropped onsite 04/27/25 | 1.SR089464, SR093180, SR093174 & SR095356 2. SR096916 3. SR100537 | SR093180 | SR093174 | SR095356 | SR096916 | SR100537
CDCR-North Kern State Prision | CA | 114921 | 114921 | 0 | 0% | 209926.89 | -95005.89 | -45.26% | 1. 43 Damaged (Thermal) SF 290-36-P Modules onsite are needed for replacement | 1. SR092753
Muroc Joint USD - District Office | CA | 7125 | 6887 | 238 | 3.456% | 9656.11 | -2531.11 | -26.21% | 1. Low production/generation due to rain on 04/26
Whole Foods - Manhattan Beach | CA | 17007 | 16746 | 261 | 1.559% | 21784.09 | -4777.09 | -21.93% | 1. Inverters 3 & 8 have been offline throughout the month due to parts delays. On 02/26/25, FIMER tested replacement logic boards, but they failed bench tests. As of 04/10/25, remanufactured boards are still failing functional tests. FIMER is working with the repair center and engineering team in Italy, but no ETA is available. 2. Inverter 9 has been offline since 02/25/25, remaind offline through out the month and parts are needed to bring these inverter back online. | 1. SR090375, SR089461 2. SR098018 | SR089461 | SR098018
Pioneer USD - Frontier ES | CA | 30397 | N/A |  |  | 35194.19 | -4797.19 | -13.63% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. Waiting for approval to dispatch. | 1. SR092276
Pioneer USD - Pioneer ES | CA | 19143 | N/A |  |  | 35767.49 | -16624.49 | -46.48% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. 2. Pad 1 Inverter 1 was offline throughout the month, and on Pad 2, Inverter 1 is not communicating, although production data is being captured at the meter. On 03/13/25, it was approved to investigate the auxiliary equipment installed and the fault logs, with BOLD. | 1. SR085968 2. SR092256, SR090090 & SR095592 | SR092256 | SR090090 | SR095592
Pioneer USD - Pioneer MS | CA | 42437 | N/A |  |  | 47914.68 | -5477.68 | -11.43% | 1. Weather station is not communicating through out the month, It was found that the pyranometer is not installed on-site. The installation of a new pyranometer will be required. | 1. SR089470, SR092603 | SR092603
Kingsburg Joint UHSD - Kingsburg HS | CA | 82857 | 79179 | 3678 | 4.645% | 90441.64 | -7584.64 | -8.386% | 1. Inverter A and Meter A resumed communication on 04/07/25 at 7:00 AM. On 04/08/25, technician swapped red and blue Ethernet cables and confirmed with ROC that data was reporting 2. Meter B is regularly capturing data from 7:20 AM to 10:00 AM, in sync with Inverter B. However, Inverter B is capturing data from 10:05 AM to 4:45 PM due to the MOXA not functioning. On 04/01/25, the technician installed the MOXA (datalogger), but the communication failed. On 04/09,04/10 Inverter and meter are interfered due sharing ports and both lost communication at 17:40 on 04/10/25 due to faulty dataloggers, and additional troubleshooting is required. 3. Inverter 2 pad C intermittently tripping during high irradiance; possibly due to overheating. | 1.SR089612, SR095339 & SR095385, SR097012 2. SR089612, SR095385 3. SR099766 | SR095339 | SR095385 | SR097012 | SR089612 | SR095385 | SR099766
CADRB | CA | 0 | N/A |  |  | 791823 | -791823 | -100% | 1. Site back online on 01/09/25 after the technician re-energized it, we cannot confirm as silicon ranch only has access to site. 2.Inverter 3 was back online on 11/15/2024 but we cannot confirm through SCADA since site is not communicating 3.Pyranometer has been giving bad readings. Prior to 9/25, the pyranometer read at most 450 W/m2. Since then, readings are between 950 and 400 W/m2. | 1. SR092166, SR097558, SR098717 2. SR086220, SR098717 3. SR091312 | SR097558 | SR098717 | SR086220 | SR098717 | SR091312
CDCR-CA State Prison LA County | CA | 312836 | 302364 | 10472 | 3.463% | 501677.37 | -188841.37 | -37.64% | 1. Inverter 1 is not communicating, and according to the meter data, it is offline due to a breaker issue. A case was raised on 03/24/25 to request support for the breaker replacement. | 1. SR098397
Central USD Akers ES | CA | 37590 | 38998 | -1408 | -3.61% | 38046.05 | -456.05 | -1.199% | 1. Meter experiences intermittent communication loss, but inverter continues reporting production. Meter communication has been consistent since 04/01/25, as confirmed by inverter data 2. Weather station is reporting 0w/m2. Waiting for appoval | 1. SR098178 2. SR090370 | SR090370
CUSD - District Office | CA | 21592 | 20775 | 817 | 3.933% | 31419.67 | -9827.67 | -31.28% | 1. Inverter 1 was brought online at 11:35 on 04/10/25 after the technician re-energized it and completed PM inspection. It tripped offline again at 18:25 on 04/12/25 due to a watchdog timer fault and remained offline for the rest of the month. | 1. SR099747, PM10476, SR099540 2. SR098177 | SR099540 | SR098177
Parlier - WTP | CA | 56290 | 52027 | 4263 | 8.194% | 91735.31 | -35445.31 | -38.64% | 1. Inverter 2 went offline on 04/21/25 due to system, latching, RTC, and restart limit faults. On 04/22/25 at 12:10 PM, technician found a Restart Limit fault, verified AC/DC voltages and fuses (all good), and cleaned out heavy dust. A power supply error was noted, indicating potential failure. Event logs were pulled and a ticket was submitted to Bold Renewables. Inverter was restarted and is online pending further support | 1. SR100064, SR100858 | SR100858
Snowline SD - Quail Valley MS | CA | 39517 | 33704 | 5813 | 17.25% | 43263.19 | -3746.19 | -8.659% | 1. Inverter has been tripping frequently. On 04/28/25, technician power cycled DAS equipment and inverter, tested Cat5 (checked good), but comms were not restored. Contacted Bold, sent photos of the comms card, and opened a case. Bold recommended replacing the comms and comm max boards. Awaiting parts quote; further troubleshooting is needed to restore communication and resolve tripping | 1. SR094545, SR100842 | SR100842
Snowline SD - Serrano HS - Middle Lot | CA | 34848 | 34831 | 17 | 0.04881% | 55029.14 | -20181.14 | -36.67% | 1. Site production was low on 04/26 and 04/27 due to bad weather.
Snowline SD - Pinon Hills ES | CA | 12845 | 12825 | 20 | 0.1559% | 25215.87 | -12370.87 | -49.06% | 1. 23 modules need replacement; quote declined by client on 11/07/24 | 1. SR090734
Ramona - Santa Maria WTP | CA | 67314 | 66838 | 476 | 0.7122% | 83468.89 | -16154.89 | -19.35% | 1. Site production was low on 04/26 and 04/27 due to bad weather.
Kohls - Redding | CA | 507 | N/A |  |  | 31544.14 | -31037.14 | -98.39% | 1. Weather station is started reporting from 03/31/25. 1. Inverter 1 tripped offline at 13:15 on 03/31 due to a Xantrex fault (state 592: ""contactor open"") and remained offline for the rest of the month. | 1. SR090293, SR095854 2. SR099225 | SR095854 | SR099225
Kohls - Salinas | CA | 34837 | 33148 | 1689 | 5.095% | 49956.33 | -15119.33 | -30.27% | 1. Inverters 3, 7, 10, 14, and 21 are offline through out the month and parts are needed to bring these inverters back online. 2. Inverter 11 was brought online at 10:45 AM on 04/14/25 after replacing the AC GFCI and re-terminating wires. It tripped offline again at 10:00 AM on 04/24/25 and remained down; additional parts are needed. For Inverter 2, technician verified LOTO, removed two broken/burned fuse holders, installed new parts with two Ameresco 15A fuses, and removed LOTO the same day. | 1. SR098183, SR095449, SR093474, SR090380 & SR089474. 2. SR098183 | SR095449 | SR093474 | SR090380 | SR089474 | SR098183
Kohls - San Bernardino - Central | CA | 1201 | 1199 | 2 | 0.1668% | 137860.17 | -136659.17 | -99.13% | 1. Inverter 1 has been underperforming by 90kW since 11:40 on 08/21/24. During the Annual Preventative Maintenance on 04/02/25, the technician found poor filters and a potential hazard with the AC switch. New filters are needed to restore performance. 2. Inverter 1 went offline at 11:30 AM on 04/01/25, followed by Inverter 2 at 12:45 PM. The meter still shows voltage. Inverter 1 has a status code of 1,314 (FAULT, WARNING, MPP, AUTO START), while Inverter 2 shows 1,792 (MPP, SLEEP, AUTO START). On 04/04/25, the technician confirmed that the site would remain offline due to ongoing contractor activity. Additional information from the Kohls team indicated that large-scale electrical work was being carried out inside the facility. As a safety measure, the utility feed was disconnected at 09:10 AM on the same day. The site has remained offline throughout the month due to continued electrical work. | 1. SR098826, PM11103 2. SR099327, PM11103 | SR099327
Kohls - Sonora | CA | 29241 | 27901 | 1340 | 4.803% | 33281.85 | -4040.85 | -12.14% | 1.Inverter 3 has been offline since 01/28/25, remained offline through out the month due to additional parts needed. 2. Inverter 7 was offline through out the month and parts needed to bring these inverter back online. 3. Inverter 12 has been offline since 01/30/25, remaind offline through out the month and parts are needed to bring these inverter back online. | 1. SR089477, SR096348 2. SR089477, SR096348 3. SR089477, SR096348 | SR096348 | SR089477 | SR096348 | SR089477 | SR096348
CUSD - Stratford ES | CA | 25704 | 24673 | 1031 | 4.179% | 23724.43 | 1979.57 | 8.344%
Taft - City Hall | CA | 876 | 48 | 828 | 1725% | 9524.29 | -8648.29 | -90.8% | 1. Metering Energy values are much lower than expected vs meter Power. | 1. SR097948
Taft - Federal Prison | CA | 16199 | 16129 | 70 | 0.434% | 15175.89 | 1023.11 | 6.742%
Taft - Police Department | CA | 11295 | 11249 | 46 | 0.4089% | 10899.77 | 395.23 | 3.626%
Taft - WTP | CA | 876 | 52750 | -51874 | -98.34% | 9524.29 | -8648.29 | -90.8% | 1. Meter was not communicating production at the inverters. so we considered inverter productionas site production. 2. Inverter A stopped communicating since at 11:15 AM on 04/08/25 due to a loss of communication with the meter. Production cannot be confirmed and the inverter may be offline. | 1.SR095559, SR099641 2. SR099641 | SR099641 | SR099641
CDCR - CA Correctional Institution | CA | 193202 | 201735 | -8533 | -4.23% | 221609.78 | -28407.78 | -12.82% | 1. Inverter 1 production is being affected in the morning hours due to stuck trackers. but expected production restored from 04/11/25. 2. Site has been not communicating from 12:50PM on 04/08/25 to 10:05AM on 04/09/25, energy has not backfilled. | 1. SR092170, SR092456 2. SR101007 | SR092456 | SR101007
CDCR - CA Correctional Institution II | CA | 317401.68 | 140503 | 176898.68 | 125.9% | 317401.68 | 0 | 0% | 1. Inverter 2's production being affected in the afternoon hours possibly due to stuck trackers. 2. Inverter 2 tripped offline at 09:35 AM on 04/09/25 due to a FAN 5 fault. The onsite technician confirmed the issue and requested a quote from BOLD. It was restored at 06:45 AM on 04/10/25. The inverter tripped again at 09:25 AM on 04/16/25 and came back online at 06:50 AM on 04/17/25. It went offline at 12:10 PM on 04/24/25 due to an Asymmetrical Array Fault and was restored at 06:40 AM on 04/25/25. Further trips occurred on 04/26/25 and 04/27/25 due to the FAN 5 fault, with recovery on 04/28/25 and again tripped offline at 07:50AM on 04/30 . FAN 5 needs replacement to restore expected production. 3. Inverter 3 is underperforming by approximately 200 kW and It has been offline since at 11:30AM on 04/29/25, remaind offline through out the month and parts are needed to bring these inverter back online. 4. Site tripped offline at 12:30 PM on 04/07/25 and was brought back online at 09:25 AM on 04/09/25 after the technician closed the breaker at the switchgear and repaired the malfunctioning trackers | 1. SR092171, SR092455 2. SR099609 3. SR098778 4. SR099493 | SR092455 | SR099609 | SR098778 | SR099493
Snowline SD - Vista Verde ES | CA | 15985 | 17072 | -1087 | -6.367% | 31954.52 | -15969.52 | -49.98% | 1. Inverter 1 back online at 11:00AM on 04/16/25 after technician performed all tests and reenergised it but it requires new Air filter. | 1. SR098343, PM10928
North Stonington | CT | 1425880 | N/A |  |  | N/A |  |  | 1. Site Curtailed to 5.2MW from 17:11PM to 17:18 PM. No production was impacted during the curtailment event as the on-site production production was around 1.5MW which is much lower than the curtailed command power (5.2MW). | 1. SR097960

## May
Silicon Ranch |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 4480761 | 2823886 | 1656875 | 58.67% | 5417492.11 | -936731.11 | -17.29%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT | 29586 | 29449 | 137 | 0.4652% | 34313.45 | -4727.45 | -13.78% | 1. Low production/generation due to rain on 05/05, 05/09 & 05/22.
Kohls - Auburn | NY | 31098 | 30780 | 318 | 1.033% | 45680.29 | -14582.29 | -31.92% | 1. Low production/generation due to rain on 05/03, 05/04, 05/07 & 05/09.
Kohls - Bensalem | PA | 0 | N/A |  |  | 37858.58 | -37858.58 | -100% | 1. Site has communicated intermittently throughout the month due to a faulty modem, with data expected to backfill later. On 04/17/2024, the technician found the inverter online and producing, but the cell modem's indicator lights were not flashing, indicating no data transmission. DAS was power cycled with no change. Multiple attempts to contact Green Power Monitor for support went unanswered. The modem had been previously replaced and updated with a new IP address, suggesting a possible SIM card or data issue. The site last update was on 04/24/25. On 05/08/25 need to dispatch to power cycle as well as provide the modems nameplate to GPM. | 1. SR098590
Kohls - Brick | NJ | 31086 | 31002 | 84 | 0.271% | 46381.08 | -15295.08 | -32.98% | 1. Inverter tripped offline at 09:45 On 05/06/25 due to "GFI device fault" and back online at 07:50 on 05/11/25 self resoved and again tripped offline at 09:55 the same day and back online at 08:45 on 05/13/25, Technician found the fault, and rebooted it. Troubleshooting with Bold Renewables revealed the "tickle" wire needed a second loop through the GFI device. Adding a wire splice and looping it again increased current flow, extending the device’s life and resolving the issue. | 1.SR101056
Kohls - Buffalo | NY | 38164 | N/A |  |  | 50993.46 | -12829.46 | -25.16% | 1. Inverter 4 is offline throught the month due to an INV 4 was thermally damaged in the DC box. 2. Inverter 5 derating to about 19kW, most operating around 22kW since 03/11/25. | 1.SR096145, SR096237 2. SR095177 | SR096237 | SR095177
Kohls - Canton | CT | 14284 | 14088 | 196 | 1.391% | 15305.66 | -1021.66 | -6.675%
Kohls - East Amherst | NY | 26632 | 26383 | 249 | 0.9438% | 45726.58 | -19094.58 | -41.76% | 1. Inverter 1 tripped offline at 10:50 AM on 04/29/25 due to a "Sleep state" fault. On 05/01/25, a technician found all equipment manually shut down by non-Ameresco personnel; main disconnect was locked (not tagged), and meter, DAS, and inverter disconnects were off. On 05/09/25, a technician cut the lock on the AC disconnect, restored power, and brought the inverter back online at 09:25 AM. Inverter is now operating but shows an active DC surge warning; surge protectors need replacement. Advance Energy (Bold Renewables) was contacted, and a callback is pending. | 1. SR100632
Kohls - East Brunswick | NJ | 49282 | 48916 | 366 | 0.7482% | 59211.63 | -9929.63 | -16.77% | 1. Inverter 1 tripped offline at 14:50 on 05/26/25 due to "Fan 7 fault" and back online at 08:25 on 05/27/25. | 1. SR101939
Kohls - Edgewood | MD | 263413 | 261246 | 2167 | 0.8295% | 310676.77 | -47263.77 | -15.21% | 1. Low production/generation due to rain on 05/13, 05/21 & 05/28
Kohls - Granite Run | PA | 33132 | 32778 | 354 | 1.08% | 37858.03 | -4726.03 | -12.48% | 1. Low production/generation due to rain on 05/13, 05/14 & 05/21
Kohls - Greece | NY | 32389 | 32066 | 323 | 1.007% | 49808.65 | -17419.65 | -34.97% | 1. Low production/generation due to rain on 05/03, 05/22, 05/23 & 05/24
Kohls - Hanover | PA | 40175 | 39884 | 291 | 0.7296% | 41915.35 | -1740.35 | -4.152%
Kohls - Horsehead | NY | 27105 | 26765 | 340 | 1.27% | 35914.8 | -8809.8 | -24.53% | 1. Low production/generation due to rain on 05/04, 05/09 & 05/22.
Kohls - Hudson | NY | 31815 | 31591 | 224 | 0.7091% | 35803.72 | -3988.72 | -11.14% | 1. Low production/generation due to rain on 05/04, 05/05 & 05/09.
Kohls - Ithaca | NY | 28310 | 28039 | 271 | 0.9665% | 41098.38 | -12788.38 | -31.12% | 1. Low production/generation due to rain on 05/04, 05/09 & 05/31.
Kohls - Kingston | NY | 41330 | 40900 | 430 | 1.051% | 59092.81 | -17762.81 | -30.06% | 1. Low production/generation due to rain on 05/04, 05/05, 05/09 & 05/22
Kohls - Mechanicsburg | PA | 43971 | 43589 | 382 | 0.8764% | 48943.99 | -4972.99 | -10.16% | 1. Low production/generation due to rain on 05/13 & 05/28.
Kohls - Middletown | NJ | 42063 | 41447 | 616 | 1.486% | 72424.36 | -30361.36 | -41.92% | 1. Inverter 01 tripped on 05/02/25 due to an "Ambient temperature fault" and self-resolved on 05/03/25. Multiple trips occurred starting 05/10/25. On 05/13/25, a technician found an "Aux Supply" fault after pulling logs and restarting the inverter. Bold Renewables identified aging IDC connectors as the issue and further multiple tripes occured on 05/20, 05/22 & 05/23 and tripped at 12:35 on 05/24/25 and remained offline through the month, in order to bring inverter online ICD connectors are need to be replaced. | 1. SR100937, SR101331 | SR101331
Kohls - North Amherst | NY | 27872 | 27733 | 139 | 0.5012% | 43967.86 | -16095.86 | -36.61% | 1. 5 faulty Modules and one faulty fuse are need to be replaced. | 1. SR100060, SR093440, PM4000 | SR093440
Kohls - Staten Island | NY | 29967 | N/A |  |  | 41334.61 | -11367.61 | -27.5% | 1. Inverter 8 was offline due to Internal hardware “Error E018” fault till date. Inverter 20 was offline from 07/22/24 due to Internal Error -E018 fault. Inverter 21 was tripped offline at 09:05 on 08/17/24 due to Internal Error - E018 fault and was being RMA'd. Inverter 10 was offline from 03/05/25 due stuck in "Stand by mode". | 1. SR102013, SR095623 | SR095623
Kohls - Warminster | PA | 44971 | 44618 | 353 | 0.7912% | 46156.09 | -1185.09 | -2.568%
Kohls - Waterbury | CT | 32687 | 32243 | 444 | 1.377% | 41949.53 | -9262.53 | -22.08% | 1. Site tripped offline at 16:00 on 05/05/25 and was brought back online at 11:00 on 05/08/25 after the technician after resetting site. | 1. SR101039
Mojave Water Agency - Headquarters | CA | 50274 | 50207 | 67 | 0.1334% | 39526.57 | 10747.43 | 27.19%
CSU - Bakersfield | CA | 192332 | 197878 | -5546 | -2.803% | 171459.72 | 20872.28 | 12.17%
Greenfield USD - Fairfield ES | CA | 16135 | 16022 | 113 | 0.7053% | 16930.92 | -795.92 | -4.701%
Greenfield USD - Granite Point ES | CA | 31577 | 31397 | 180 | 0.5733% | 44787.9 | -13210.9 | -29.5% | 1. Pad 1 - inverters 1, 2 were brought back online at 11:25 on 05/12/25 after the technician closed both inverters' AC/DC disconnects. 2. Weather station has intermittent comms losses since 05/12/25. It frequently loses comms for 15 minutes to 1 hour several times a day. 3. Pad 2 - inverter 1 tripped offline at 12:00 on 05/22/25 due to an overcurrent fault and remained offline throught the month pending for schedule queue. | 1. SR100011 2. SR101440 3. SR101862 | SR101440 | SR101862
Greenfield USD - Greenfield MS | CA | 18679 | 18643 | 36 | 0.1931% | 30442.57 | -11763.57 | -38.64% | 1. Inverter 1 Pad 1 tripped offline at 08:50 on 05/02/25 and remained offline through the month. Pending approval for a Comm Card replacement. | 1. SR100743
Greenfield USD - Horizon ES | CA | 36639 | 36562 | 77 | 0.2106% | 46583.01 | -9944.01 | -21.35% | 1. Inverter 1 ( Pad 1) has been offline since 04/27/25 due to an "Pre-Charge fault". On 05/12/25, the technician inverter had DC contactor fault and swapped contactor with AC contactor. Inverter began producing at 10:25 the same day and was left to run. Fault has now followed to AC contactor so will need to replace contactor. Quote is pending. 2. Pad A Inverter 2 has been intermittently tripping online/offline. Status 128, Fault 0: 96, Fault 1: 5. It tripped offline at 5:55 PM on 05/07/25. On 05/12/25, the technician removed the AC contactor and found worn contacts replacement needed. A P10 power supply fault was also found; BOLD recommends replacing the power distribution card. Inverter was power cycled and brought back online at 10:20. and again tripped offline at 18:25 on 05/19/25. 3. Inverter 1 (Pad B) tripping on and offline multiple times on 05/28/25, 05/29/25 and resolved on 05/30/25. | 1. SR100459 2. SR101131 3. SR102150 | SR101131 | SR102150
Greenfield USD - McKee MS | CA | 21628 | 21598 | 30 | 0.1389% | 28438.8 | -6810.8 | -23.95% | 1. Site production was low on 05/04 and 05/13 due to cloudy weather.
Greenfield USD - Plantation ES | CA | 19780 | 20342 | -562 | -2.763% | 20341 | -561 | -2.758%
Greenfield USD - Planz ES | CA | 7844 | 8046 | -202 | -2.511% | 22372.35 | -14528.35 | -64.94% | 1. Inverter 1 meter has been down for some time. On 04/30/25, technician worked with GPM support to connect to the modem and data logger but was unsuccessful. GPM is escalating the comms issue; return visit needed. | 1. SR099912
Greenfield USD - Raffaello Palla ES | CA | 28616 | 29654 | -1038 | -3.5% | 50057.44 | -21441.44 | -42.83% | 1. Meter reporting zero from 03/30, later from 04/06 at 13:30 meter reading its production but issue has been occurring intermittently, production can be confirmed at inverter level. | 1. SR099206
Greenfield USD - Valle Verde ES | CA | 48072 | 49360 | -1288 | -2.609% | 46702.51 | 1369.49 | 2.932%
Greenfield USD - W.A. Kendrick ES | CA | 0 | N/A |  |  | 18015.53 | -18015.53 | -100% | 1.Meter reporting half of inverter production since 6/11/22 waiting for client approval for investigation | 1. SR094440
Muroc Joint USD - Boron HS | CA | 0 | N/A |  |  | 40633.79 | -40633.79 | -100% | 1. Site back communication at 9:15 on 12/30/2024 and Inverter remains offline because of Inverter down hard - Power supply critical failure. 2. Weather station began reporting erroneous values on 12/30/2024, and the POA sensor needed to be replaced along with additional repairs. | 1. SR095163 2. SR093065 | SR093065
Muroc Joint USD - W. Boron ES | CA | 13740 | 14135 | -395 | -2.794% | 14985.37 | -1245.37 | -8.311%
Colusa - WTP | CA | 0 | N/A |  |  | 62987.19 | -62987.19 | -100% | 1. Site came back online at 09:40 on 02/11/25 after the technician replaced four air filters in the central inverter. Meter replacement is required. 2. Site has been offline since 02/13/25 and the site was under water may not self-resolve. On 02/28/25, the technician found the inverter displaying a 0020 fault code (Delta High Temp Warning). The manual advises contacting the manufacturer for this code. Emailed Bold Renewables for guidance and will update once they respond with a solution and remained offline throught the month. 3. Meter communications have dropped onsite 04/27/25 | 1.SR089464, SR093180, SR093174 & SR095356 2. SR096916 3. SR100537 | SR093180 | SR093174 | SR095356 | SR096916 | SR100537
CDCR-North Kern State Prision | CA | 140327 | 139595 | 732 | 0.5244% | 253737.72 | -113410.72 | -44.7% | 1. 43 Damaged (Thermal) SF 290-36-P Modules onsite are needed for replacement | 1. SR092753
Muroc Joint USD - District Office | CA | 6928 | 7138 | -210 | -2.942% | 10570.6 | -3642.6 | -34.46% | 1. Site tripped offline from 15:00 to 19:55 on 05/10/25
Whole Foods - Manhattan Beach | CA | 16498 | 17021 | -523 | -3.073% | 22703.25 | -6205.25 | -27.33% | 1. Inverters 3 & 8 have been offline throughout the month due to parts delays. On 02/26/25, FIMER tested replacement logic boards, but they failed bench tests. As of 04/10/25, remanufactured boards are still failing functional tests. FIMER is working with the repair center and engineering team in Italy, but no ETA is available. 2. Inverter 9 back online at 14:45 on 05/06/25, after technician swapped Breaker from Inverter 8 which is offline for RMA to Inverter 9. 3. Inverters 2 and 5 are underperforming, likely due to soiling. Inverter 2 is down 1 kW, and inverter 5 is down 3 kW and also inverter 9 down a string from 05/15/25. | 1. SR090375, SR089461 2. SR098018 3. SR101562, SR101561 | SR089461 | SR098018 | SR101562 | SR101561
Pioneer USD - Frontier ES | CA | 33974 | N/A |  |  | 39041.66 | -5067.66 | -12.98% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. Waiting for approval to dispatch. | 1. SR092276
Pioneer USD - Pioneer ES | CA | 9968 | N/A |  |  | 39764.35 | -29796.35 | -74.93% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. 2. Pad 1 Inverter 1 was offline throughout the month, and on Pad 2, Inverter 1 is not communicating, although production data is being captured at the meter. On 03/13/25, it was approved to investigate the auxiliary equipment installed and the fault logs, with BOLD. 3. Pad 1 Inverter 2 went offline at 12:05 on 05/05. The technician power-cycled Inverters 1 and 2; both came back online briefly but tripped offline again. The technician contacted Bold Renewables for further troubleshooting. Currently, Inverters 1 and 2 remain offline, while Inverter 3 is online and producing. | 1. SR085968 2. SR092256, SR090090 & SR095592 3. SR095592, PM9954 | SR092256 | SR090090 | SR095592 | SR095592
Pioneer USD - Pioneer MS | CA | 47623 | N/A |  |  | 53427.14 | -5804.14 | -10.86% | 1. Site was taken offline from 08:40 to 10:35 on 05/27/25 to work on Preventative Maintenance. 2. Weather station is not communicating through out the month, It was found that the pyranometer is not installed on-site. The installation of a new pyranometer will be required. | 1. PM11514 2. SR089470, SR092603 | SR092603
Kingsburg Joint UHSD - Kingsburg HS | CA | 74894 | 60742 | 14152 | 23.3% | 87255.83 | -12361.83 | -14.17% | 1. Meter B is regularly capturing data from 7:20 to 10:00 , in sync with Inverter B. However, Inverter B is capturing data from 10:05 to 4:45 due to the MOXA not functioning. On 04/01/25, the technician installed the MOXA (datalogger), but the communication failed. On 05/03/25, 05/09/25 and 05/20/25 meter communiting intermitently and on 05/22/25 stopped communication both at 11:15 due to faulty dataloggers, and additional troubleshooting is required. 2. Inverter 2 (Pad C) is intermittently tripping during high irradiance, possibly due to overheating. On 05/20/25, tech contacted SMA no immediate response. SMA later advised checking AC and DC voltages. AC wire was found improperly stripped and was corrected. SMA suspects unstable incoming AC power. Awaiting their follow-up on voltage readings 3. Weather station reporting zero from 16:20 on 05/20/25. Will nvestigate after the bulk production work is completed onsite. | 1. SR089612, SR095385 & SR102060 2. SR099766 | SR095385 | SR102060 | SR099766
CADRB | CA | 0 | N/A |  |  | 906720 | -906720 | -100% | 1. Site back online on 01/09/25 after the technician re-energized it, we cannot confirm as silicon ranch only has access to site. 2.Inverter 3 was back online on 11/15/2024 but we cannot confirm through SCADA since site is not communicating 3.Pyranometer has been giving bad readings. Prior to 9/25, the pyranometer read at most 450 W/m2. Since then, readings are between 950 and 400 W/m2. | 1. SR092166, SR097558, SR098717 2. SR086220, SR098717 3. SR091312 | SR097558 | SR098717 | SR086220 | SR098717 | SR091312
CDCR-CA State Prison LA County | CA | 337153 | 336647 | 506 | 0.1503% | 572636 | -235483 | -41.12% | 1. Inverter 1 is not communicating, and according to the meter data, it is offline due to a breaker issue. A case was raised on 03/24/25 to request support for the breaker replacement. 2. Site was taken offline from 10:20 to 12:20 on 05/14/25, to work on inverter 1 and tracker troubleshooting. Additionally, working on wire management. | 1. SR098397 2. SR098397 | SR098397
Central USD Akers ES | CA | 48197 | N/A |  |  | 43541.58 | 4655.42 | 10.69%
CUSD - District Office | CA | 24878 | 25251 | -373 | -1.477% | 37350.56 | -12472.56 | -33.39% | 1. Inverter 1 was brought online at 10:05 on 05/21/25 after technician reopened doors to check voltages for an AC Contactor Restart Limit Current Imbalance fault. No loose wires found. Logs pulled; Bold advised replacing Power Distribution Cards. and it again tripped offline at 13:50 on 05/29/25 and remained offline throught the month. 2. Inverter 2 has been frequently tripping offline this month due to fault code 21: Peak Power Tracking. On 05/21/25, the technician shut down the inverter from 08:30 to 09:25 to pull logs, then brought it back online. Logs were sent to Bold Renewables, the Power Distribution Card are need to be replaced and it again tripped offline at 19:45 on 05/24/25 due to an "watch dog timer fault". and remained offline throught the month. | 1. SR101829, PM10476 2. SR101132 | SR101132
Parlier - WTP | CA | 43664 | 43639 | 25 | 0.05729% | 103327.84 | -59663.84 | -57.74% | 1. Inverter 2 went offline on 05/16/25 due to system, latching faults, remaind offline through out the month and parts are needed to bring these inverter back online. | 1. SR100858
Snowline SD - Quail Valley MS | CA | 42433 | 43953 | -1520 | -3.458% | 49077.26 | -6644.26 | -13.54% | 1. Inverter has been tripping frequently. On 04/28/25, technician power cycled DAS equipment and inverter, tested Cat5 (checked good), but comms were not restored. Contacted Bold, sent photos of the comms card, and opened a case. Bold recommended replacing the comms and comm max boards. Awaiting parts quote; further troubleshooting is needed to restore communication and resolve tripping | 1. SR094545, SR100842 | SR100842
Snowline SD - Serrano HS - Middle Lot | CA | 38334 | 38295 | 39 | 0.1018% | 62475.15 | -24141.15 | -38.64% | 1. Site production was low on 0/04 & 05/05 due to cloudy weather.
Snowline SD - Pinon Hills ES | CA | 13006 | 13385 | -379 | -2.832% | 26919.02 | -13913.02 | -51.68% | 1. 23 modules need replacement; quote declined by client on 11/07/24 2. Site was offline from 08:20 to 18:20 05/03/25. | 1. SR080516 2. SR100976 | SR100976
Ramona - Santa Maria WTP | CA | 67824 | 68980 | -1156 | -1.676% | 81023.93 | -13199.93 | -16.29% | 1. Site production was low on 05/04 to 05/06 due to bad weather.
Kohls - Redding | CA | 36806 |  |  |  | 36330.5 | 475.5 | 1.309%
Kohls - Salinas | CA | 40888 | 42185 | -1297 | -3.075% | 53596.2 | -12708.2 | -23.71% | 1. Inverters 3, 7, 10, 14, and 21 are offline through out the month and parts are needed to bring these inverters back online. 2. Inverter 11 was brought online at 10:45 on 04/14/25 after replacing the AC GFCI and re-terminating wires. It tripped offline again at 10:00 on 04/24/25 and remained down; additional parts are needed. For Inverter 2, technician verified LOTO, removed two broken/burned fuse holders, installed new parts with two Ameresco 15A fuses, and removed LOTO the same day. 3. Inverter 16 offline since 05/20/25 due to "Standby" fault and remained offline throught out the month. | 1. SR098183, SR095449, SR093474, SR090380 & SR089474. 2. SR098183 3. SR101740 | SR095449 | SR093474 | SR090380 | SR089474 | SR098183 | SR101740
Kohls - San Bernardino - Central | CA | 0 | N/A |  |  | 174622.88 | -174622.88 | -100% | 1. Inverter 1 has been underperforming by 90kW since 11:40 on 08/21/24. During the Annual Preventative Maintenance on 04/02/25, the technician found poor filters and a potential hazard with the AC switch. New filters are needed to restore performance. 2. Inverter 1 went offline at 11:30 on 04/01/25, followed by Inverter 2 at 12:45. The meter still shows voltage. Inverter 1 has a status code of 1,314 (FAULT, WARNING, MPP, AUTO START), while Inverter 2 shows 1,792 (MPP, SLEEP, AUTO START). On 04/04/25, the technician confirmed that the site would remain offline due to ongoing contractor activity. Additional information from the Kohls team indicated that large-scale electrical work was being carried out inside the facility. As a safety measure, the utility feed was disconnected at 09:10 on the same day. The site has remained offline throughout the month due to continued electrical work. | 1. SR098826, SR099338, PM11103 2. SR099327, PM11103, & SR102082 | SR099338 | SR099327 | SR102082
Kohls - Sonora | CA | 32625 | 33495 | -870 | -2.597% | 38514.63 | -5889.63 | -15.29% | 1. Inverter 3 has been offline since 01/28/25. on 05/27/25, the technician replaced the old circuit breaker and a broken AC disconnect switch and brought back online at 10:45. 2. Inverter 7 was offline through out the month and parts needed to bring these inverter back online. 3. Inverter 12 has been offline since 01/30/25, remaind offline through out the month and parts are needed to bring these inverter back online. 4. Inverter 2 was offline from 05/11/25 to 05/27/25 due to tripped local circuit breakers. It was shut down and inspected. String isolation and system tests found no issues and brought back online at 10:45 by closing breaker and again offline from 05/29/25, remained offline throught the month. 5. Inverter 4 tripped offline at 14:00 on 05/27/25 and remained offline throught the month. | 1. SR089477, SR096348 & SR101285 2. SR089477, SR096348 3. SR089477, SR096348 4. SR102153, SR101285 5. SR102153 | SR096348 | SR101285 | SR089477 | SR096348 | SR089477 | SR096348 | SR102153 | SR101285 | SR102153
CUSD - Stratford ES | CA | 28234 | 29015 | -781 | -2.692% | 26263.15 | 1970.85 | 7.504%
Taft - City Hall | CA | 796 | 64 | 732 | 1144% | 11244.78 | -10448.78 | -92.92% | 1. Metering Energy values are much lower than expected vs meter Power. | 1. SR097948
Taft - Federal Prison | CA | 18988 | 19527 | -539 | -2.76% | 17368.26 | 1619.74 | 9.326%
Taft - Police Department | CA | 13959 | 14376 | -417 | -2.901% | 12861.22 | 1097.78 | 8.536%
Taft - WTP | CA | 65151 | 64939 | 212 | 0.3265% | 77110.15 | -11959.15 | -15.51% | 1. Meter was not communicating production at the inverters. So we considered inverter productionas site production. 2. Inverter A stopped communicating since at 11:15 on 04/08/25 due to a loss of communication with the meter. Production cannot be confirmed and the inverter may be offline. | 1.SR095559, SR099641 2. SR099641 | SR099641 | SR099641
CDCR - CA Correctional Institution | CA | 250530 | 249898 | 632 | 0.2529% | 260218.07 | -9688.07 | -3.723% | 1. Site tripped offline at 12:00AM on 05/16/25 and was brought back online at 11:40 AM on 05/17/25 after the technician closed the breaker at the switchgear. | 1.SR101606
CDCR - CA Correctional Institution II | CA | 203177 | 202781 | 396 | 0.1953% | 386824.62 | -183647.62 | -47.48% | 1. Inverter 2's production being affected in the afternoon hours possibly due to stuck trackers. 2. Inverter 2 back online at 06:20 on 05/01/25, then tripped again at 07:30 on 05/02/25 and recovered at 06:50 on 05/03/25. It went offline from 11:00 to 11:55 on 05/06/25 due to an Asymmetrical Array Fault. It tripped again at 11:55 on 05/15/25 due to a FAN 5 fault and came back online on 05/16/25. FAN 5 replacement is required to restore expected production. 3. Inverter 3 has been underperforming by 200 kW and went offline at 11:30 on 04/29/25. On 05/06/25, the technician replaced the filters with new ones from Bold Renewables, but the inverter remained offline through the month. Combiner fuses are needed to bring it back online. | 1. SR092171, SR092455 2. SR101475 3. SR098778 | SR092455 | SR101475 | SR098778
Snowline SD - Vista Verde ES | CA | 15618 | 15599 | 19 | 0.1218% | 36285.41 | -20667.41 | -56.96% | 1. Inverter 1 tripped offline at 7:40 on 05/15/25 due to faulty air filters and remained offline through the month. | 1. SR101624
North Stonington | CT | 1403640 | N/A |  |  | 0 |  |  | 1. Site taken offline from 08:20 to 9:20 and 11:45 to 12:30 on 05/02/25 due to technician worked on Re-Pressurizing Sealed Transformer with Nitrogen (XMFR B03). 2. Inverter A.02.15 tripped offline at 08:35 on 05/23/25 due to islanding and remained offline through the month. On 05/27, a technician identified a thermal relay failure as the cause. Sungrow was contacted, and a replacement was RMA’d. | 1. SR100820, PM8852 2. SR101886 | SR101886

## Jun
Silicon Ranch |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 4618132 | 2685129 | 1933003 | 71.99% | 5564523.006 | -946391.006 | -17.01%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT | 34203 | 34070 | 133 | 0.3904% | 36386.88 | -2183.88 | -6.002%
Kohls - Auburn | NY | 38234 | 38019 | 215 | 0.5655% | 43542.07 | -5308.07 | -12.19% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Kohls - Bensalem | PA | 0 | N/A |  |  | 38810.24 | -38810.24 | -100% | 1. Site has communicated intermittently throughout the month due to a faulty modem, with data expected to backfill later. On 04/17/2024, the technician found the inverter online and producing, but the cell modem's indicator lights were not flashing, indicating no data transmission. DAS was power cycled with no change. Multiple attempts to contact Green Power Monitor for support went unanswered. The modem had been previously replaced and updated with a new IP address, suggesting a possible SIM card or data issue. The site last update was on 04/24/25. On 05/08/25 need to dispatch to power cycle as well as provide the modems nameplate to GPM. | 1.SR098590
Kohls - Brick | NJ | 44342 | 44268 | 74 | 0.1672% | 46826.96 | -2484.96 | -5.307%
Kohls - Buffalo | NY | 33455 | N/A |  |  | 51113.8 | -17658.8 | -34.55% | 1. Meter is reporting zero from 19:25, 06/22 but production can be verified at inverters. Will investigate after getting response from GPM. | 1.SR103346
Kohls - Canton | CT | 16944 | 16776 | 168 | 1.001% | 16488.62 | 455.38 | 2.762%
Kohls - East Amherst | NY | 1158 | 1143 | 15 | 1.312% | 45911.7 | -44753.7 | -97.48% | 1. Site tripped offline at 8:45 on 06/02 and the inverter is reporting a DNS Server Fault and Sleep State. Site will remain offline through out the month until that work is finished | 1.SR102277
Kohls - East Brunswick | NJ | 49427 | 49189 | 238 | 0.4838% | 61550.24 | -12123.24 | -19.7% | 1.The inverter has been experiencing repeated trip events from 06/06 | 1.SR102623
Kohls - Edgewood | MD | 254970 | 246644 | 8326 | 3.376% | 325236.26 | -70266.26 | -21.6% | 1.Meter 3 stopped communicating at 16:23 from 06/23 but production can be verified at inverter level. | 1.SR102796
Kohls - Granite Run | PA | 36002 | 35701 | 301 | 0.8431% | 38472.17 | -2470.17 | -6.421% | 1.1 string and CB offline from 06/18 | 1.SR103142
Kohls - Greece | NY | 39812 | 39530 | 282 | 0.7134% | 50012.29 | -10200.29 | -20.4% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Kohls - Hanover | PA | 42098 | 41881 | 217 | 0.5181% | 43878.47 | -1780.47 | -4.058% | 1. Inverter tripped offline at 10:00 on 06/27 and back online at 06/28 at 07:00 | 1.SR103669
Kohls - Horsehead | NY | 32992 | 32788 | 204 | 0.6222% | 36470.18 | -3478.18 | -9.537%
Kohls - Hudson | NY | 30623 | 19297 | 11326 | 58.69% | 38886.1 | -8263.1 | -21.25% | 1.Meter power dropped to zero at 13:50 from 06/05 through out the month. The weather station data indicates normal irradiance levels, and no major issues were observed on site. Based on the available information, the system performance appears consistent with typical operating conditions. It is possibly a data glitch affecting the expected value. | 1.SR102624
Kohls - Ithaca | NY | 33290 | 33121 | 169 | 0.5103% | 41422.35 | -8132.35 | -19.63% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Kohls - Kingston | NY | 35999 | 35715 | 284 | 0.7952% | 62369.57 | -26370.57 | -42.28% | 1.Site tripped offline at 11:50 on 06/24 through out the month | 1.SR103424
Kohls - Mechanicsburg | PA | 38425 | 38125 | 300 | 0.7869% | 51230.67 | -12805.67 | -25% | 1.Meter is reporting zero value from 19:50, 06/24. Production can be confirmed at inverter level. | 1.SR103623
Kohls - Middletown | NJ | 0 | N/A |  |  | 71205.01 | -71205.01 | -100% | 1.Inverter 1 tripped offline on 05/02 and was offline through out the month | 1.SR101331
Kohls - North Amherst | NY | 35591 | 35470 | 121 | 0.3411% | 43967.86 | -8376.86 | -19.05% | 1. 5 faulty Modules and one faulty fuse are need to be replaced. | 1.SR100060
Kohls - Staten Island | NY | 31014 | N/A |  |  | 44009.37 | -12995.37 | -29.53% | 1. Inverter 8 was offline due to Internal hardware “Error E018” fault till date. Inverter 20 was offline from 07/22/24 due to Internal Error -E018 fault. Inverter 21 was tripped offline at 09:05 on 08/17/24 due to Internal Error - E018 fault and was being RMA'd. Inverter 10 was offline from 03/05/25 due stuck in "Stand by mode". | 1. SR102013, SR095623 | SR095623
Kohls - Warminster | PA | 46979 | 39236 | 7743 | 19.73% | 47419.53 | -440.53 | -0.929% | 1.Meter is reporting erroneous value from 15:50 on 06/12 but production is confirmed at inverter level and later technician powercycled the meter on 06/20 at 07:00. The weather station data indicates normal irradiance levels, and no major issues were observed on site. Based on the available information, the system performance appears consistent with typical operating conditions. It is possibly a data glitch affecting the expected value. | 1.SR102907
Kohls - Waterbury | CT | 41302 | 40904 | 398 | 0.973% | 41585.54 | -283.54 | -0.6818%
Mojave Water Agency - Headquarters | CA | 48001 | 45858 | 2143 | 4.673% | 42273.72 | 5727.28 | 13.55% | 1. The weather station has been reporting low irradiance (approximately 40 W/m²) since 06/25. The pyranometer recorded normal irradiance starting at 16:00 on 06/25, but the levels dropped back to around 40 W/m² by 09:00 on 06/26 | 1.SR103534
CSU - Bakersfield | CA | 197214 | 196762 | 452 | 0.2297% | 193210.61 | 4003.39 | 2.072%
Greenfield USD - Fairfield ES | CA | 3965 | 3920 | 45 | 1.148% | 16940.11 | -12975.11 | -76.59% | 1.Inverter 1 was offline from 06/03. After being re-energized, it came back online at 09:20 on 06/26. | 1.SR102456
Greenfield USD - Granite Point ES | CA | 46308 | 46078 | 230 | 0.4992% | 44892.68 | 1415.32 | 3.153% | 1. Pad 2 - inverter 1 tripped offline at 12:00 on 05/22 due to an overcurrent fault. Inverter came back online at 09:45 on 06/02 | 1.SR101862
Greenfield USD - Greenfield MS | CA | 21143 | 21124 | 19 | 0.08995% | 30479.336 | -9336.336 | -30.63% | 1.Inverter 1 Pad 1 tripped offline at 08:50 on 05/02. After replacing the communication card on inverter 1 came back online at 09:15 on 06/17 | 1. SR100743
Greenfield USD - Horizon ES | CA | 29096 | 29067 | 29 | 0.09977% | 46803.61 | -17707.61 | -37.83% | 1. Pad A Inverter 2 has been intermittently tripping online and offline. Status: 128, Fault 0: 96, Fault 1: 5. It tripped offline at 17:55. After replacing the AC contactor and the power distribution board, Inverter 2 came back online on 06/27. 2.Inverter 1 (Pad B) tripped offline and reported "watch dog, over current fault". from 06/22 | 1.SR101131 2.SR102150 | SR102150
Greenfield USD - McKee MS | CA | 20399 | 20390 | 9 | 0.04414% | 28558.29 | -8159.29 | -28.57% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Greenfield USD - Plantation ES | CA | 19830 | 19791 | 39 | 0.1971% | 20460.5 | -630.5 | -3.082%
Greenfield USD - Planz ES | CA | 7842 | 7809 | 33 | 0.4226% | 22583.75 | -14741.75 | -65.28% | 1. Inverter 1 meter has been down for some time. On 04/30/25, technician worked with GPM support to connect to the modem and data logger but was unsuccessful. GPM is escalating the comms issue; return visit needed. | 1.SR099912
Greenfield USD - Raffaello Palla ES | CA | 42185 | 41864 | 321 | 0.7668% | 50085.01 | -7900.01 | -15.77% | 1. Meter reporting zero from 03/30, later from 04/06 at 13:30 meter reading its production but issue has been occurring intermittently, production can be confirmed at inverter level. | 1. SR099206
Greenfield USD - Valle Verde ES | CA | 46743 | 46683 | 60 | 0.1285% | 46739.27 | 3.73 | 0.00798%
Greenfield USD - W.A. Kendrick ES | CA | 0 | N/A |  |  | 18024.72 | -18024.72 | -100% | 1.Meter reporting half of inverter production since 6/11/22 waiting for client approval for investigation. | 1.SR094440
Muroc Joint USD - Boron HS | CA | 0 | N/A |  |  | 39659.47 | -39659.47 | -100% | 1. Site back communication at 9:15AM on 12/30/2024 and Inverter remains offline because of Inverter down hard - Power supply critical failure. 2. Weather station began reporting erroneous values on 12/30/2024, and the POA sensor needed to be replaced along with additional repairs. | 1. SR095163 2.SR093065 | SR093065
Muroc Joint USD - W. Boron ES | CA | 13826 | 13782 | 44 | 0.3193% | 14625.55 | -799.55 | -5.467%
Colusa - WTP | CA | 0 | N/A |  |  | 65825.77 | -65825.77 | -100% | 1. Site came back online at 09:40 on 02/11/25 after the technician replaced four air filters in the central inverter. Meter replacement is required. 2. Site has been offline since 02/13/25 and the site was under water may not self-resolve. On 02/28/25, the technician found the inverter displaying a 0020 fault code (Delta High Temp Warning). The manual advises contacting the manufacturer for this code. Emailed Bold Renewables for guidance and will update once they respond with a solution and remained offline throught the month. 3. Meter communications have dropped onsite 04/27/25. Will be investigated once parts were received. | 1.SR089464, SR093180, SR093174 & SR095356 2. SR096916 3. SR100537 | SR093180 | SR093174 | SR095356 | SR096916 | SR100537
CDCR-North Kern State Prision | CA | 141129 | 140568 | 561 | 0.3991% | 263777 | -122648 | -46.5% | 1.43 Damaged (Thermal) SF 290-36-P Modules onsite are needed for replacement. On Hold Currently during fire remediation, will be investigated once completion of priority tasks. | 1. SR092753
Muroc Joint USD - District Office | CA | 9927 | 9916 | 11 | 0.1109% | 10315.02 | -388.02 | -3.762%
Whole Foods - Manhattan Beach | CA | 15504 | 15456 | 48 | 0.3106% | 21449.05 | -5945.05 | -27.72% | 1. Inverters 3 & 8 have been offline throughout the month due to parts delays. On 02/26/25, FIMER tested replacement logic boards, but they failed bench tests. As of 04/10/25, remanufactured boards are still failing functional tests. FIMER is working with the repair center and engineering team in Italy, but no ETA is available and 0n 06/25/25 FIMER confirms that inverter 8 is under RMA. 2. Inverters 2 and 5 are underperforming, likely due to soiling. Inverter 2 is down 1 kW, and inverter 5 is down 3 kW and also inverter 9 down a string from 05/15/25. and on 06/12/25, technician confirmed that inverter 9 remains underperforming by 4 kW has an internal issue manufacturer was contacted. inverter 5 string repaired. 3. Inverter 1 tripped offline at 08:40 on 06/02/25 and reporting "Ground Fault" and was offline throughout the month. | 1. SR090375, SR089461,SR101136 2. SR101562, SR101561, SR103159 3. SR102346 | SR089461 | SR101136 | SR101562 | SR101561 | SR103159 | SR102346
Pioneer USD - Frontier ES | CA | 31765 | N/A |  |  | 39224.36 | -7459.36 | -19.02% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. Waiting for approval to dispatch. | 1. SR092276
Pioneer USD - Pioneer ES | CA | 7837 | N/A |  |  | 39859.75 | -32022.75 | -80.34% | 1. Weather station was not communicating through out the month because the entire station needs to be replaced. 2. Pad 1 Inverter 1 was offline throughout the month, and on Pad 2, Inverter 1 is not communicating, although production data is being captured at the meter. On 03/13/25, it was approved to investigate the auxiliary equipment installed and the fault logs, with BOLD. 3. Pad 1 Inverter 2 went offline sine 05/05 . The technician contacted Bold Renewables for further troubleshooting. Currently, Inverters 1 and 2 remain offline and pending filter to be replace. | 1. SR085968 2. SR092256, SR090090, SR095592 & SR101190 3. SR095592, SR101190 PM9954 | SR092256 | SR090090 | SR095592 | SR101190 | SR095592 | SR101190
Pioneer USD - Pioneer MS | CA | 66270 | N/A |  |  | 53161.64 | 13108.36 | 24.66%
Kingsburg Joint UHSD - Kingsburg HS | CA | 11153 | N/A |  |  | 88262.31 | -77109.31 | -87.36% | 1. Meter B is regularly capturing data from 7:20 to 10:00 , in sync with Inverter B. However, Inverter B is capturing data from 10:05 to 16:45 due to the MOXA not functioning. On 04/01/25, the technician installed the MOXA (datalogger), but the communication failed. on 05/22/25 stopped communication both at 11:15 due to faulty dataloggers, and additional troubleshooting is required. 2. Inverter 2 (Pad C) is intermittently tripping during high irradiance, possibly due to overheating. On 05/20/25, tech contacted SMA no immediate response. SMA later advised checking AC and DC voltages. AC wire was found improperly stripped and was corrected. SMA suspects unstable incoming AC power. Awaiting their follow-up on voltage readings 3. Weather station reporting zero from 16:20 on 05/20/25. Will nvestigate after the bulk production work is completed onsite. | 1. SR089612, SR095385 & SR102060 2. SR099766 | SR095385 | SR102060 | SR099766
CADRB | CA | 0 | N/A |  |  | 945631 | -945631 | -100% | 1. Site back online on 01/09/25 after the technician re-energized it, we cannot confirm as silicon ranch only has access to site. 2.Inverter 3 was back online on 11/15/2024 but we cannot confirm through SCADA since site is not communicating. 3.Pyranometer has been giving bad readings. Prior to 9/25, the pyranometer read at most 450 W/m2. Since then, readings are between 950 and 400 W/m2. | 1. SR092166, SR097558, SR098717 2. SR086220, SR098717 3. SR091312 | SR097558 | SR098717 | SR086220 | SR098717 | SR091312
CDCR-CA State Prison LA County | CA | 313581 | 312903 | 678 | 0.2167% | 569051.78 | -255470.78 | -44.89% | 1. Inverter 1 is not communicating, and according to the meter data, it is offline due to a breaker issue. A case was raised on 03/24/25 to request support for the breaker replacement. | 1. SR098397
Central USD Akers ES | CA | 42269 | N/A |  |  | 43241.29 | -972.29 | -2.249%
CUSD - District Office | CA | 13941 | 13912 | 29 | 0.2085% | 37509.37 | -23568.37 | -62.83% | 1. Inverter 1 tripped offline at 13:50 on 05/29/25 and remained offline throught the month pending parts to be replace. 2. Inverter 2 again tripped offline at 19:45 on 05/24/25 due to an "watch dog timer fault". and remained offline throught the month and needed install power distribution cards. | 1. SR101829, PM10476 2. SR101132 | SR101132
Parlier - WTP | CA | 49857 | 49841 | 16 | 0.0321% | 112049.85 | -62192.85 | -55.5% | 1. Inverter 2 went offline on 05/16/25 due to system, latching faults and back online at 12:40 on 06/03/25. | 1. SR100858
Snowline SD - Quail Valley MS | CA | 49138 | 49087 | 51 | 0.1039% | 50428.09 | -1290.09 | -2.558% | 1. Inverter has been tripping frequently. On 04/28/25, technician power cycled DAS equipment and inverter, tested Cat5 (checked good), but comms were not restored. Contacted Bold, sent photos of the comms card, and opened a case. Bold recommended replacing the comms and comm max boards. Awaiting parts quote; further troubleshooting is needed to restore communication and resolve tripping issue. | 1. SR094545, SR100842 | SR100842
Snowline SD - Serrano HS - Middle Lot | CA | 21719 | 20532 | 1187 | 5.781% | 60759.23 | -39040.23 | -64.25% | 1. Site tripped offline at 15:15 on 06/10 and back online at 11:30 on 06/13. 2. Inverter 2 tripped offline at 14:55 on 06/10 and remained offline throughout the month. | 1. SR102808 2. SR102808 | SR102808
Snowline SD - Pinon Hills ES | CA | 13280 | 13267 | 13 | 0.09799% | 26187.01 | -12907.01 | -49.29% | 1. The inverter is underperforming by approximately 70kW since 06/12. Will need to be investigate. | 1. SR102897, SR80516, SR90734 | SR80516, | SR90734
Ramona - Santa Maria WTP | CA | 74655 | 74477 | 178 | 0.239% | 81869.56 | -7214.56 | -8.812%
Kohls - Redding | CA | 44733 | 56 | 44677 | 79780% | 37815.99 | 6917.01 | 18.29% | 1. Weather station was reporting irradiance during the day. Likely a faulty pyranometer. Due to that expected energy values are low.Waiting for approval | 1. SR090293
Kohls - Salinas | CA | 37254 | 37059 | 195 | 0.5262% | 50893.87 | -13639.87 | -26.8% | 1. Inverters 3, 7, 10, 14, and 21 are offline through out the month and parts are needed to bring these inverters back online. 2. Inverter 11 tripped offline again at 10:00 on 04/24/25 and remained down; additional parts are needed and is back online at 09:20 on 06/27/25. 3. Inverter 16 offline since 05/20/25 due to "Standby" fault and remained offline throught out the month and inverter is under replacement. | 1. SR098183, SR095449, SR093474, SR090380 & SR089474. 2. SR098183 3. SR101740 | SR095449 | SR093474 | SR090380 | SR089474 | SR098183 | SR101740
Kohls - San Bernardino - Central | CA | 20237 | 20187 | 50 | 0.2477% | 173166.93 | -152929.93 | -88.31% | 1. Inverter 1 has been underperforming by 90kW since 11:40 on 08/21/24. During the Annual Preventative Maintenance on 04/02/25, the technician found poor filters and a potential hazard with the AC switch. New filters are needed to restore performance and Later, a technician re-energized the inverter, and it was brought back online at 14:00 on 06/27/2025 and producing as expected. 2. Inverter 1 went offline at 11:30 on 04/01/25, followed by Inverter 2 at 12:45, though the meter still showed voltage. Status codes indicated faults and auto-start attempts. On 04/04/25, the technician confirmed the site would stay offline due to contractor electrical work, and the utility feed was disconnected at 09:10 for safety. The site was re-energized and brought back online at 14:00 on 06/27/25. | 1. SR098826, SR099338, PM11103 2. SR099327, PM11103, & SR102082 | SR099338 | SR099327 | SR102082
Kohls - Sonora | CA | 32433 | 32270 | 163 | 0.5051% | 38490.73 | -6057.73 | -15.74% | 1. Inverter 7 was offline through out the month and parts needed to bring these inverter back online and it's under RMA. 2. Inverter 12 has been offline since 01/30, remained offline through out the month and parts are needed to bring these inverter back online and it's under RMA.. 3. Inverter 2 tripped offline from 05/29 and back online at 09:50 on 06/25. 4. Inverter 4 tripped offline at 14:00 on 05/27 and back online at 09:50 on 06/25. | 1. SR089477, SR096348 2. SR089477, SR096348 3. SR102153, SR101285 4. SR102153 | SR096348 | SR089477 | SR096348 | SR102153 | SR101285 | SR102153
CUSD - Stratford ES | CA | 22815 | 22765 | 50 | 0.2196% | 25679.48 | -2864.48 | -11.15% | 1. Inverter 1 was tripping on & off intermittently since 05/29, seems to be heating issue. Dispatch scheduled on 07/03. | 1. SR102151
Taft - City Hall | CA | 246 | 42 | 204 | 485.7% | 11320.54 | -11074.54 | -97.83% | 1. Meter is reporting erroneous energy readings since 06/27. 2. The weather station data indicates normal irradiance levels, and no major issues were observed on site. Based on the available information, the system performance appears consistent with typical operating conditions. It is possibly a data glitch affecting the expected value. | 1. SR103666
Taft - Federal Prison | CA | 19072 | 19051 | 21 | 0.1102% | 17196.66 | 1875.34 | 10.91%
Taft - Police Department | CA | 14121 | 14107 | 14 | 0.09924% | 12944.27 | 1176.73 | 9.091%
Taft - WTP | CA | 63372 | 63142 | 230 | 0.3643% | 76485.12 | -13113.12 | -17.14% | 1. Inverter A stopped communicating since at 11:15 on 04/08/25 due to a loss of communication with the meter. Production cannot be confirmed and the inverter may be offline. The work is scheduled during the next PM on 07/09/2025. | 1. SR099641
CDCR - CA Correctional Institution | CA | 244241 | 243776 | 465 | 0.1907% | 272813.68 | -28572.68 | -10.47% | 1. Site was offline from 9:50 to 10:05 on 06/24 due to technicians were onsite repair a broken PVC conduits. 2. At system 1 tracker is not working and on 06/24 PVC conduits has been replaced. Required further troubleshooting. | 1. SR096410 2. SR092456 | SR092456
CDCR - CA Correctional Institution II | CA | 218011 | 217710 | 301 | 0.1383% | 409853.3 | -191842.3 | -46.81% | 1. Inverter 3 has been underperforming by 200 kW and went offline at 11:30 on 04/29. Replaced the filters with new ones from Bold Renewables, but the inverter remained offline through the month. Combiner fuses are needed to bring it back online. 2. Inverter 2 tripped offline at 19:40 on 06/28 and reporting "AC Current imbalance fault". | 1. SR098778 2. SR103724 | SR103724
Snowline SD - Vista Verde ES | CA | 0 | N/A |  |  | 37127.85 | -37127.85 | -100% | 1. Inverter 1 tripped offline at 07:40 on 05/15/2025 due to faulty air filters and remained offline throughout the month. Parts need to be replaced, and additional troubleshooting is required. | 1. SR101624, SR102522 | SR102522
North Stonington | CT | 1626160 | N/A |  |  | 0 | 1626160 |  | 1. Inverter A.02.15 tripped offline at 08:35 on 05/23 and reporting islanding. After replacing the inverter, it was back online at 13:50 on 06/03. | 1. SR101886

## Jul
Silicon Ranch |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 4487553 | 2532830 | 1954723 | 77.18% | 5398892.686 | -911339.686 | -16.88% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT | 37799 | 37699 | 100 | 0.2653% | 35701.9 | 2097.1 | 5.874%
Kohls - Auburn | NY | 44556 | 44420 | 136 | 0.3062% | 44245.55 | 310.45 | 0.7017%
Kohls - Bensalem | PA | 0 | N/A |  |  | 39533.49 | -39533.49 | -100% | 1. Site has communicated intermittently throughout the month due to a faulty modem, with data expected to backfill later. On 04/17/2024, the technician found the inverter online and producing, but the cell modem's indicator lights were not flashing, indicating no data transmission. DAS was power cycled with no change. Multiple attempts to contact Green Power Monitor for support went unanswered. The modem had been previously replaced and updated with a new IP address, suggesting a possible SIM card or data issue. The site last update was on 04/24/25. On 05/08/25 need to dispatch to power cycle as well as provide the modems nameplate to GPM. | 1. SR098590
Kohls - Brick | NJ | 48789 | 48707 | 82 | 0.1684% | 49138.28 | -349.28 | -0.7108%
Kohls - Buffalo | NY | 58595 | NA |  |  | 52511.51 | 6083.49 | 11.59% | 1. Meter is reporting zero from 19:25, 06/22 but production can be verified at inverters. Meter regained its communication on 07/17 2.Inverter 6 offline from 07/22 and it came back online at 13:35 on 07/29 and again tripped offline from 07/30 3.Meter reporting zero at 17:50 on 07/23 but production can be confirmed at Inverter level.On 07/29 Meter communication restored. Issue resolved. | 1. SR103346 2. SR104755 3. SR104916 | SR104755 | SR104916
Kohls - Canton | CT | 18679 | 18476 | 203 | 1.099% | 16279.33 | 2399.67 | 14.74%
Kohls - East Amherst | NY | 0 | 0 | 0 |  | 48225.8 | -48225.8 | -100% | 1. Site tripped offline at 8:45 on 06/02 and the inverter is reporting a DNS Server Fault and Sleep State. Site will remain offline through out the month until that work is finished.Technician found site offline for R&R work | 1. SR102467 ,SR102277 | SR102277
Kohls - East Brunswick | NJ | 21605 | 21561 | 44 | 0.2041% | 60986.06 | -39381.06 | -64.57% | 1.Inverter was offline from 07/04 and reporting "Tension AC fault and Thermal connection error". Inverter came back online at 03:30 on 07/22 | 1. SR104016
Kohls - Edgewood | MD | 182967 | 182193 | 774 | 0.4248% | 322055.92 | -139088.92 | -43.19% | 1.Meter 3 stopped communicating at 16:23 from 06/23 but production can be verified at inverter level.Meter has failed and needs to be replaced. 2.Inverter 2 tripped offline frequently throughout the month starting on 07/05. On 07/21, a technician, in coordination with Bold Renewables, identified a fault in the array. Resolving the issue will require an additional troubleshoot and repair the fault. | 1. SR102796 2.SR104045 | SR104045
Kohls - Granite Run | PA | 39643 | 39349 | 294 | 0.7472% | 39195.43 | 447.57 | 1.142%
Kohls - Greece | NY | 42002 | 41818 | 184 | 0.44% | 50058.57 | -8056.57 | -16.09% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Kohls - Hanover | PA | 38149 | 37978 | 171 | 0.4503% | 44023.48 | -5874.48 | -13.34% | 1.Inverter offline from 07/02 and it came back online on 07/06 | 1. SR103669
Kohls - Horsehead | NY | 37333 |  |  |  | 36747.88 | 585.12 | 1.592%
Kohls - Hudson | NY | 49090 | 688 | 48402 | 7035% | 41607.48 | 7482.52 | 17.98% | 1.Meter power reporting Zero at 13:30 from 06/25 through out the month. The weather station data indicates normal irradiance levels, and no major issues were observed on site. Based on the available information, the system performance appears consistent with typical operating conditions. It is possibly a data glitch affecting the expected value. | 1. SR103499
Kohls - Ithaca | NY | 38495 | 38361 | 134 | 0.3493% | 42051.79 | -3556.79 | -8.458%
Kohls - Kingston | NY | 63760 | 51065 | 12695 | 24.86% | 61555.01 | 2204.99 | 3.582% | 1.Meter power restored at 09:35 from 07/02 | 1.SR103424
Kohls - Mechanicsburg | PA | 3184 | 3163 | 21 | 0.6639% | 51398.34 | -48214.34 | -93.81% | 1.Meter is reporting zero value from 19:50, 06/24. Production can be confirmed at inverter level. On 07/30 Meter regained its communication. | 1.SR103623
Kohls - Middletown | NJ | 0 | 0 | 0 |  | 70367.84 | -70367.84 | -100% | 1.Inverter 1 tripped offline on 05/02 and was offline through out the month | 1.SR101331
Kohls - North Amherst | NY | 23666 | 23596 | 70 | 0.2967% | 44708.37 | -21042.37 | -47.07% | 1.Site stopped communicating at 16:55 from 07/18. On 07/25 Technician has reached out to GPM support for assistance, GPM has mentioned the Cradlepoint/modem is the older version and will no longer support for any updates GPM stated that the Cradlepoint/modem needs to be replaced in order to restore the communication and they will be sending a quote for the replacement | 1. SR104634
Kohls - Staten Island | NY | 35516 | NA |  |  | 40682.01 | -5166.01 | -12.7% | 1.Inverter 8 was offline due to Internal hardware “Error E018” fault till date. Inverter 20 was offline from 07/22/24 due to Internal Error -E018 fault. Inverter 21 was tripped offline at 09:05 on 08/17/24 due to Internal Error - E018 fault and was being RMA'd. Inverter 10 was offline from 03/05/25 due stuck in "Stand by mode". Service requests was closed due to no warranty, and no replacement options 2. Inverters 7,11 an 23 are tripped offline from 07/29 and came back online at 13:00 on 07/30 | 1. SR102013, SR095623 2. SR105300 | SR095623 | SR105300
Kohls - Warminster | PA | 51308 | 51124 | 184 | 0.3599% | 48325.86 | 2982.14 | 6.171%
Kohls - Waterbury | CT | 43943 | 43673 | 270 | 0.6182% | 41803.94 | 2139.06 | 5.117%
Mojave Water Agency - Headquarters | CA | 4075 | 2601 | 1474 | 56.67% | 39251.32 | -35176.32 | -89.62% | 1. Inverter offline since 07/03 Waiting on Parts quote from BOLD | 1.SR104085 , SR104907 | SR104907
CSU - Bakersfield | CA | 190709 | 190291 | 418 | 0.2197% | 193659.71 | -2950.71 | -1.524%
Greenfield USD - Fairfield ES | CA | 6869 | 6810 | 59 | 0.8664% | 17096.37 | -10227.37 | -59.82% | 1. Inverter is offline from 7/12 reporting watchdog timer fault. On 07/30 inverter has been reenergized at 08:30. Bold recommends replacing the air filters as well. | 1.SR104402
Greenfield USD - Granite Point ES | CA | 46822 | 46511 | 311 | 0.6687% | 45287.92 | 1534.08 | 3.387%
Greenfield USD - Greenfield MS | CA | 25214 | 25198 | 16 | 0.0635% | 30764.276 | -5550.276 | -18.04% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Greenfield USD - Horizon ES | CA | 32399 | 32335 | 64 | 0.1979% | 47171.28 | -14772.28 | -31.32% | 1.Inverter 1 (Pad B) tripped offline and reported "watch dog, over current fault". from 06/22. It came back online at 10:25 on 07/09 2.Inverter 2 pad A offline from 07/12 and reporting "WATCHDOG TIMER FAULT". | 1. SR102150 2.SR104343 | SR104343
Greenfield USD - McKee MS | CA | 19824 | 19814 | 10 | 0.05047% | 28788.08 | -8964.08 | -31.14% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Greenfield USD - Plantation ES | CA | 19773 | 19751 | 22 | 0.1114% | 20625.94 | -852.94 | -4.135%
Greenfield USD - Planz ES | CA | 7662 | 7627 | 35 | 0.4589% | 23208.78 | -15546.78 | -66.99% | 1.On 07/30Technician restored the communication for SMA inverter, currently all 7 SMA inverters are communicating. Additional troubleshooting required to restore the communication for PVP meter. | 1. SR104165 , SR103032 | SR103032
Greenfield USD - Raffaello Palla ES | CA | 39368 | 39039 | 329 | 0.8427% | 50572.17 | -11204.17 | -22.15% | 1. Meter reporting zero from 03/30, later from 04/06 at 13:30 meter reading its production but issue has been occurring intermittently, production can be confirmed at inverter level. | 1. SR104919, SR099206 | SR099206
Greenfield USD - Valle Verde ES | CA | 45490 | 45416 | 74 | 0.1629% | 47171.28 | -1681.28 | -3.564%
Greenfield USD - W.A. Kendrick ES | CA | 0 | 0 | 0 |  | 18190.17 | -18190.17 | -100% | 1.Meter reporting half of inverter production since 6/11/22 waiting for client approval for investigation. | 1. SR094440
Muroc Joint USD - Boron HS | CA | 0 | 0 | 0 |  | 38442.26 | -38442.26 | -100% | 1. Site back communication at 9:15AM on 12/30/2024 and Inverter remains offline because of Inverter down hard - Power supply critical failure. | 1. SR095163
Muroc Joint USD - W. Boron ES | CA | 14154 | 14113 | 41 | 0.2905% | 14183.26 | -29.26 | -0.2063%
Colusa - WTP | CA | 0 | NA |  |  | 67861.15 | -67861.15 | -100% | 1. The meter has been reporting 60 kW of production onsite since 07/25. 2. 14 replacement modules and connector repairs are needed onsite, along with 16 strings that require repair. | 1. SR105065 2. SR105063 | SR105063
CDCR-North Kern State Prision | CA | 104432 | 104067 | 365 | 0.3507% | 265603.15 | -161171.15 | -60.68% | 1. Inverter 1 has been offline since 07/19 due to "ASYMMETRICAL ARRAY". 2. 43 Damaged (Thermal) SF 290-36-P Modules onsite are needed for replacement. On Hold Currently during fire remediation, will be investigated once completion of priority tasks. | 1. SR104640 2. SR092753 | SR092753
Muroc Joint USD - District Office | CA | 8475 | 8467 | 8 | 0.09448% | 9995.08 | -1520.08 | -15.21% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Whole Foods - Manhattan Beach | CA | 16724 | 16692 | 32 | 0.1917% | 23457.05 | -6733.05 | -28.7% | 1. Inverter 9 has been offline since 12:30 on 07/05. 2. Inverter 1 tripped offline at 08:40 on 06/02/25, reporting "Ground Fault", and has remained offline since then. 3. Inverters 2 and 5 are underperforming, likely due to soiling. Inverter 2 is down by 1 kW, and inverter 5 is down by 3 kW. Inverter 9 has been down a string since 05/15/25. On 06/12/25, it was confirmed that inverter 9 remains underperforming by 4 kW due to an internal issue; the manufacturer has been contacted. The string on inverter 5 has been repaired. | 1. SR104027 2. SR102346 3. SR103159, SR105161, SR105162 | SR102346 | SR103159 | SR105161 | SR105162
Pioneer USD - Frontier ES | CA | 10267 | 0 | 10267 |  | 39491.66 | -29224.66 | -74% | 1. The weather station was not communicating throughout the month as the entire station needs to be replaced. | 1. SR092276
Pioneer USD - Pioneer ES | CA | 7212 | 0 | 7212 |  | 40411.45 | -33199.45 | -82.15% | 1. Site has no communications since 07/11.Inverter 2 Needs a Communication Card and 5A fuses - Inverter 1 Needs additional troubleshooting | 1. SR101137, SR104917 | SR104917
Pioneer USD - Pioneer MS | CA | 43768 | 0 | 43768 |  | 54189.43 | -10421.43 | -19.23% | As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Kingsburg Joint UHSD - Kingsburg HS | CA | 23415 | 0 | 23415 |  | 93257.03 | -69842.03 | -74.89% | 1. Weather station reporting zero from 16:20 on 05/20/25. Pending PO for weather station sensor 2. Meter B is regularly capturing data from 7:20 to 10:00 , in sync with Inverter B. However, Inverter B is capturing data from 10:05 to 16:45 due to the MOXA not functioning. On 04/01/25, the technician installed the MOXA (datalogger), but the communication failed. on 05/22/25 stopped communication both at 11:15 due to faulty dataloggers, and additional troubleshooting is required. | 1.SR105133 2.SR089612, SR095385 & SR102060 | SR089612 | SR095385 | SR102060
CADRB | CA | 0 | 0 | 0 |  | 932886 | -932886 | -100% | 1. Site back online on 01/09/25 after the technician re-energized it, we cannot confirm as silicon ranch only has access to site. 2.Inverter 3 was back online on 11/15/2024 but we cannot confirm through SCADA since site is not communicating. 3.Pyranometer has been giving bad readings. Prior to 9/25, the pyranometer read at most 450 W/m2. Since then, readings are between 950 and 400 W/m2. | 1. SR092166, SR097558, SR098717 2. SR086220, SR098717 3. SR091312 | SR097558 | SR098717 | SR086220 | SR098717 | SR091312
CDCR-CA State Prison LA County | CA | 224654 | 224234 | 420 | 0.1873% | 550300.92 | -325646.92 | -59.18% | 1.Inverter 2 offline at 06:50 on 07/04 2. Inverter 1 is not communicating, and according to the meter data, it is offline due to a breaker issue. A case was raised on 03/24/25 to request support for the breaker replacement. | 1. SR104021 2. SR098397 | SR098397
Central USD Akers ES | CA | 3124 | N/A |  |  | 42446.3 | -39322.3 | -92.64% | 1. Site had no communications since 07/03 and need to replace Modem and Datalogger. | 1. SR094234, SR104249 | SR104249
CUSD - District Office | CA | 30845 | 30784 | 61 | 0.1982% | 36534.58 | -5689.58 | -15.57% | 1.Inverter 2 came back online at 13:45 on 007/03 2.Inverter 1 came back online at 13:45 on 07/03 | 1.SR101132 2. SR101829 | SR101829
Parlier - WTP | CA |  | 47921
Snowline SD - Quail Valley MS | CA | 51648 | 51603 | 45 | 0.0872% | 48529.62 | 3118.38 | 6.426%
Snowline SD - Serrano HS - Middle Lot | CA |  | 51356 | [5 empty] | 1. Inverter 2 tripped offline at 14:55 on 06/10 and came back online at 15:10 on 07/09 | 1.SR102808
Snowline SD - Pinon Hills ES | CA | 13315 | 13307 | 8 | 0.06012% | 25453.18 | -12138.18 | -47.69% | 1. The inverter is underperforming by approximately 70kW since 06/12. Will need to be investigate. | 1.SR102897
Ramona - Santa Maria WTP | CA | 79894 | 79770 | 124 | 0.1554% | 84213.41 | -4319.41 | -5.129%
Kohls - Redding | CA | 43166 | 133 | 43033 | 32356% | 38835.61 | 4330.39 | 11.15% | 1. Weather station was reporting irradiance during the day. Likely a faulty pyranometer. Due to that expected energy values are low.Waiting for approval | 1. SR090293
Kohls - Salinas | CA | 35475 | 35241 | 234 | 0.664% | 51757.88 | -16282.88 | -31.46% | 1. Inverters 3, 7, 10, 14, and 21 are offline through out the month and parts are needed to bring these inverters back online. 2. Inverter 11 tripped offline again at 10:00 on 04/24/25 and remained down; additional parts are needed and is back online at 09:20 on 06/27/25. 3. Inverter 16 offline since 05/20/25 due to "Standby" fault and remained offline throught out the month and inverter is under replacement. | 1. SR098183, SR095449, SR093474, SR090380 & SR089474. 2. SR098183 3. SR101740 | SR095449 | SR093474 | SR090380 | SR089474 | SR098183 | SR101740
Kohls - San Bernardino - Central | CA | 169840 | 168308 | 1532 | 0.9102% | 182266.61 | -12426.61 | -6.818%
Kohls - Sonora | CA | 34686 | 34522 | 164 | 0.4751% | 39593.72 | -4907.72 | -12.4% | 1. Inverter 7 was offline through out the month and parts needed to bring these inverter back online and it's under RMA. 2. Inverter 12 has been offline since 01/30, remained offline through out the month and parts are needed to bring these inverter back online and it's under RMA. 3. Inverter 2 went offline at 07:00 on 06/27. Later, on 07/25, the technician replaced the OCPD, and the inverter came back online at 10:10 on 07/25. and again tripped offline at 07:00 on 07/28 and remained offline. | 1. SR089477, SR096348 2. SR089477, SR096348 3. SR103802, SR105126 | SR096348 | SR089477 | SR096348 | SR103802 | SR105126
CUSD - Stratford ES | CA | 26243 | 26203 | 40 | 0.1527% | 25376.16 | 866.84 | 3.416% | 1. Inverter 1 was tripping on & off intermittently since 05/29, seems to be heating issue. Dispatch scheduled on 08/11. | 1. SR102151
Taft - City Hall | CA | 176 | 88 | 88 | 100% | 11379.86 | -11203.86 | -98.45% | 1. Meter is reporting erroneous energy readings since 06/27. 2. The weather station data indicates normal irradiance levels, and no major issues were observed on site. Based on the available information, the system performance appears consistent with typical operating conditions. It is possibly a data glitch affecting the expected value. | 1. SR103666, SR104943 | SR104943
Taft - Federal Prison | CA | 6848 | 6840 | 8 | 0.117% | 17410.24 | -10562.24 | -60.67% | 1. Inverter 1 tripped offline at 14:30 on 07/11 and reporting "overcurrent fault" and back online at 13:25 on 07/31. | 1. SR104404
Taft - Police Department | CA | 14052 | 14039 | 13 | 0.0926% | 13013.64 | 1038.36 | 7.979%
Taft - WTP | CA | 63472 | 63265 | 207 | 0.3272% | 77461.27 | -13989.27 | -18.06% | 1. Inverter A stopped communicating since at 11:15 on 04/08/25 due to a loss of communication with the meter. Production cannot be confirmed and the inverter may be offline. The work is scheduled during the next PM. | 1. SR099641
CDCR - CA Correctional Institution | CA | 215482 | 215107 | 375 | 0.1743% | 280389.3 | -64907.3 | -23.15% | 1. Site was offline at 21:25 on 07/04 due to main bracker trip late back online at 13:35 on 07/07. 2. Site was tripped offline at 12:30 on 07/31. 3. At system 1 tracker is not working and on 06/24 PVC conduits has been replaced. later on tracker are back online on 07/10. | 1. SR104035 2. SR105453 3. SR092456 | SR105453 | SR092456
CDCR - CA Correctional Institution II | CA | 198551 | 198232 | 319 | 0.1609% | 415368.28 | -216817.28 | -52.2% | 1. Inverter 3 has been underperforming by 200 kW and went offline at 11:30 on 04/29. Replaced the filters with new ones from Bold Renewables, but the inverter remained offline through the month. Combiner fuses are needed to bring it back online. 2. Inverter 2 tripped offline at 19:40 on 06/28 and reporting "AC Current imbalance fault" and back online at 07:00 on 07/01. 3. Site was offline at 21:25 on 07/04 due to main bracker trip late back online at 12:35 on 07/07. 4. Site was tripped offline at 12:30 on 07/31. | 1. SR098778, SR103948 2. SR103724 3. SR104036 4. SR105452 | SR103948 | SR103724 | SR104036 | SR105452
Snowline SD - Vista Verde ES | CA | 9281 | 9274 | 7 | 0.07548% | 35793.45 | -26512.45 | -74.07% | 1. Inverter 1 tripped offline at 07:40 on 05/15/2025 due to faulty air filters. After installing new fuses, the inverter came back online at 13:10 on 07/24. | 1. SR102522
North Stonington | CT | 1721070 | N/A |  |  | N/A

## Aug
Silicon Ranch |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Silicon Ranch | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT
Kohls - Auburn | NY
Kohls - Bensalem | PA
Kohls - Brick | NJ
Kohls - Buffalo | NY
Kohls - Canton | CT
Kohls - East Amherst | NY
Kohls - East Brunswick | NJ
Kohls - Edgewood | MD
Kohls - Granite Run | PA
Kohls - Greece | NY
Kohls - Hanover | PA
Kohls - Horsehead | NY
Kohls - Hudson | NY
Kohls - Ithaca | NY
Kohls - Kingston | NY
Kohls - Mechanicsburg | PA
Kohls - Middletown | NJ
Kohls - North Amherst | NY
Kohls - Staten Island | NY
Kohls - Warminster | PA
Kohls - Waterbury | CT
Mojave Water Agency - Headquarters | CA
CSU - Bakersfield | CA
Greenfield USD - Fairfield ES | CA
Greenfield USD - Granite Point ES | CA
Greenfield USD - Greenfield MS | CA
Greenfield USD - Horizon ES | CA
Greenfield USD - McKee MS | CA
Greenfield USD - Plantation ES | CA
Greenfield USD - Planz ES | CA
Greenfield USD - Raffaello Palla ES | CA
Greenfield USD - Valle Verde ES | CA
Greenfield USD - W.A. Kendrick ES | CA
Muroc Joint USD - Boron HS | CA
Muroc Joint USD - W. Boron ES | CA
Colusa - WTP | CA
CDCR-North Kern State Prision | CA
Muroc Joint USD - District Office | CA
Whole Foods - Manhattan Beach | CA
Pioneer USD - Frontier ES | CA
Pioneer USD - Pioneer ES | CA
Pioneer USD - Pioneer MS | CA
Kingsburg Joint UHSD - Kingsburg HS | CA
CADRB | CA
CDCR-CA State Prison LA County | CA
Central USD Akers ES | CA
CUSD - District Office | CA
Parlier - WTP | CA
Snowline SD - Quail Valley MS | CA
Snowline SD - Serrano HS - Middle Lot | CA
Snowline SD - Pinon Hills ES | CA
Ramona - Santa Maria WTP | CA
Kohls - Redding | CA
Kohls - Salinas | CA
Kohls - San Bernardino - Central | CA
Kohls - Sonora | CA
CUSD - Stratford ES | CA
Taft - City Hall | CA
Taft - Federal Prison | CA
Taft - Police Department | CA
Taft - WTP | CA
CDCR - CA Correctional Institution | CA
CDCR - CA Correctional Institution II | CA
Snowline SD - Vista Verde ES | CA
North Stonington | CT

## Sep
Silicon Ranch |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT
Kohls - Auburn | NY
Kohls - Bensalem | PA
Kohls - Brick | NJ
Kohls - Buffalo | NY
Kohls - Canton | CT
Kohls - East Amherst | NY
Kohls - East Brunswick | NJ
Kohls - Edgewood | MD
Kohls - Granite Run | PA
Kohls - Greece | NY
Kohls - Hanover | PA
Kohls - Horsehead | NY
Kohls - Hudson | NY
Kohls - Ithaca | NY
Kohls - Kingston | NY
Kohls - Mechanicsburg | PA
Kohls - Middletown | NJ
Kohls - North Amherst | NY
Kohls - Staten Island | NY
Kohls - Warminster | PA
Kohls - Waterbury | CT
Mojave Water Agency - Headquarters | CA
CSU - Bakersfield | CA
Greenfield USD - Fairfield ES | CA
Greenfield USD - Granite Point ES | CA
Greenfield USD - Greenfield MS | CA
Greenfield USD - Horizon ES | CA
Greenfield USD - McKee MS | CA
Greenfield USD - Plantation ES | CA
Greenfield USD - Planz ES | CA
Greenfield USD - Raffaello Palla ES | CA
Greenfield USD - Valle Verde ES | CA
Greenfield USD - W.A. Kendrick ES | CA
Muroc Joint USD - Boron HS | CA
Muroc Joint USD - W. Boron ES | CA
Colusa - WTP | CA
CDCR-North Kern State Prision | CA
Muroc Joint USD - District Office | CA
Whole Foods - Manhattan Beach | CA
Pioneer USD - Frontier ES | CA
Pioneer USD - Pioneer ES | CA
Pioneer USD - Pioneer MS | CA
Kingsburg Joint UHSD - Kingsburg HS | CA
CADRB | CA
CDCR-CA State Prison LA County | CA
Central USD Akers ES | CA
CUSD - District Office | CA
Parlier - WTP | CA
Snowline SD - Quail Valley MS | CA
Snowline SD - Serrano HS - Middle Lot | CA
Snowline SD - Pinon Hills ES | CA
Ramona - Santa Maria WTP | CA
Kohls - Redding | CA
Kohls - Salinas | CA
Kohls - San Bernardino - Central | CA
Kohls - Sonora | CA
CUSD - Stratford ES | CA
Taft - City Hall | CA
Taft - Federal Prison | CA
Taft - Police Department | CA
Taft - WTP | CA
CDCR - CA Correctional Institution | CA
CDCR - CA Correctional Institution II | CA
Snowline SD - Vista Verde ES | CA
North Stonington | CT

## Oct
Silicon Ranch |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT
Kohls - Auburn | NY
Kohls - Bensalem | PA
Kohls - Brick | NJ
Kohls - Buffalo | NY
Kohls - Canton | CT
Kohls - East Amherst | NY
Kohls - East Brunswick | NJ
Kohls - Edgewood | MD
Kohls - Granite Run | PA
Kohls - Greece | NY
Kohls - Hanover | PA
Kohls - Horsehead | NY
Kohls - Hudson | NY
Kohls - Ithaca | NY
Kohls - Kingston | NY
Kohls - Mechanicsburg | PA
Kohls - Middletown | NJ
Kohls - North Amherst | NY
Kohls - Staten Island | NY
Kohls - Warminster | PA
Kohls - Waterbury | CT
Mojave Water Agency - Headquarters | CA
CSU - Bakersfield | CA
Greenfield USD - Fairfield ES | CA
Greenfield USD - Granite Point ES | CA
Greenfield USD - Greenfield MS | CA
Greenfield USD - Horizon ES | CA
Greenfield USD - McKee MS | CA
Greenfield USD - Plantation ES | CA
Greenfield USD - Planz ES | CA
Greenfield USD - Raffaello Palla ES | CA
Greenfield USD - Valle Verde ES | CA
Greenfield USD - W.A. Kendrick ES | CA
Muroc Joint USD - Boron HS | CA
Muroc Joint USD - W. Boron ES | CA
Colusa - WTP | CA
CDCR-North Kern State Prision | CA
Muroc Joint USD - District Office | CA
Whole Foods - Manhattan Beach | CA
Pioneer USD - Frontier ES | CA
Pioneer USD - Pioneer ES | CA
Pioneer USD - Pioneer MS | CA
Kingsburg Joint UHSD - Kingsburg HS | CA
CADRB | CA
CDCR-CA State Prison LA County | CA
Central USD Akers ES | CA
CUSD - District Office | CA
Parlier - WTP | CA
Snowline SD - Quail Valley MS | CA
Snowline SD - Serrano HS - Middle Lot | CA
Snowline SD - Pinon Hills ES | CA
Ramona - Santa Maria WTP | CA
Kohls - Redding | CA
Kohls - Salinas | CA
Kohls - San Bernardino - Central | CA
Kohls - Sonora | CA
CUSD - Stratford ES | CA
Taft - City Hall | CA
Taft - Federal Prison | CA
Taft - Police Department | CA
Taft - WTP | CA
CDCR - CA Correctional Institution | CA
CDCR - CA Correctional Institution II | CA
Snowline SD - Vista Verde ES | CA
North Stonington | CT

## Nov
Silicon Ranch |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT
Kohls - Auburn | NY
Kohls - Bensalem | PA
Kohls - Brick | NJ
Kohls - Buffalo | NY
Kohls - Canton | CT
Kohls - East Amherst | NY
Kohls - East Brunswick | NJ
Kohls - Edgewood | MD
Kohls - Granite Run | PA
Kohls - Greece | NY
Kohls - Hanover | PA
Kohls - Horsehead | NY
Kohls - Hudson | NY
Kohls - Ithaca | NY
Kohls - Kingston | NY
Kohls - Mechanicsburg | PA
Kohls - Middletown | NJ
Kohls - North Amherst | NY
Kohls - Staten Island | NY
Kohls - Warminster | PA
Kohls - Waterbury | CT
Mojave Water Agency - Headquarters | CA
CSU - Bakersfield | CA
Greenfield USD - Fairfield ES | CA
Greenfield USD - Granite Point ES | CA
Greenfield USD - Greenfield MS | CA
Greenfield USD - Horizon ES | CA
Greenfield USD - McKee MS | CA
Greenfield USD - Plantation ES | CA
Greenfield USD - Planz ES | CA
Greenfield USD - Raffaello Palla ES | CA
Greenfield USD - Valle Verde ES | CA
Greenfield USD - W.A. Kendrick ES | CA
Muroc Joint USD - Boron HS | CA
Muroc Joint USD - W. Boron ES | CA
Colusa - WTP | CA
CDCR-North Kern State Prision | CA
Muroc Joint USD - District Office | CA
Whole Foods - Manhattan Beach | CA
Pioneer USD - Frontier ES | CA
Pioneer USD - Pioneer ES | CA
Pioneer USD - Pioneer MS | CA
Kingsburg Joint UHSD - Kingsburg HS | CA
CADRB | CA
CDCR-CA State Prison LA County | CA
Central USD Akers ES | CA
CUSD - District Office | CA
Parlier - WTP | CA
Snowline SD - Quail Valley MS | CA
Snowline SD - Serrano HS - Middle Lot | CA
Snowline SD - Pinon Hills ES | CA
Ramona - Santa Maria WTP | CA
Kohls - Redding | CA
Kohls - Salinas | CA
Kohls - San Bernardino - Central | CA
Kohls - Sonora | CA
CUSD - Stratford ES | CA
Taft - City Hall | CA
Taft - Federal Prison | CA
Taft - Police Department | CA
Taft - WTP | CA
CDCR - CA Correctional Institution | CA
CDCR - CA Correctional Institution II | CA
Snowline SD - Vista Verde ES | CA
North Stonington | CT

## Dec
Silicon Ranch |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Iron Mountain - Windsor | CT
Kohls - Auburn | NY
Kohls - Bensalem | PA
Kohls - Brick | NJ
Kohls - Buffalo | NY
Kohls - Canton | CT
Kohls - East Amherst | NY
Kohls - East Brunswick | NJ
Kohls - Edgewood | MD
Kohls - Granite Run | PA
Kohls - Greece | NY
Kohls - Hanover | PA
Kohls - Horsehead | NY
Kohls - Hudson | NY
Kohls - Ithaca | NY
Kohls - Kingston | NY
Kohls - Mechanicsburg | PA
Kohls - Middletown | NJ
Kohls - North Amherst | NY
Kohls - Staten Island | NY
Kohls - Warminster | PA
Kohls - Waterbury | CT
Mojave Water Agency - Headquarters | CA
CSU - Bakersfield | CA
Greenfield USD - Fairfield ES | CA
Greenfield USD - Granite Point ES | CA
Greenfield USD - Greenfield MS | CA
Greenfield USD - Horizon ES | CA
Greenfield USD - McKee MS | CA
Greenfield USD - Plantation ES | CA
Greenfield USD - Planz ES | CA
Greenfield USD - Raffaello Palla ES | CA
Greenfield USD - Valle Verde ES | CA
Greenfield USD - W.A. Kendrick ES | CA
Muroc Joint USD - Boron HS | CA
Muroc Joint USD - W. Boron ES | CA
Colusa - WTP | CA
CDCR-North Kern State Prision | CA
Muroc Joint USD - District Office | CA
Whole Foods - Manhattan Beach | CA
Pioneer USD - Frontier ES | CA
Pioneer USD - Pioneer ES | CA
Pioneer USD - Pioneer MS | CA
Kingsburg Joint UHSD - Kingsburg HS | CA
CADRB | CA
CDCR-CA State Prison LA County | CA
Central USD Akers ES | CA
CUSD - District Office | CA
Parlier - WTP | CA
Snowline SD - Quail Valley MS | CA
Snowline SD - Serrano HS - Middle Lot | CA
Snowline SD - Pinon Hills ES | CA
Ramona - Santa Maria WTP | CA
Kohls - Redding | CA
Kohls - Salinas | CA
Kohls - San Bernardino - Central | CA
Kohls - Sonora | CA
CUSD - Stratford ES | CA
Taft - City Hall | CA
Taft - Federal Prison | CA
Taft - Police Department | CA
Taft - WTP | CA
CDCR - CA Correctional Institution | CA
CDCR - CA Correctional Institution II | CA
Snowline SD - Vista Verde ES | CA
North Stonington | CT

## Sites
Portfolio: | Silicon Ranch
Site DAS Name | Site | State | Column1 | DAS
zz.Iron Mountain - Windsor | Iron Mountain - Windsor | CT | FA | Green Power Monitor
zz.Kohls - Auburn | Kohls - Auburn | NY | FA | Green Power Monitor
zz.Kohls - Bensalem | Kohls - Bensalem | PA | FA | Green Power Monitor
zz.Kohls - Brick | Kohls - Brick | NJ | FA | Green Power Monitor
zz.Kohls - Buffalo | Kohls - Buffalo | NY | FA | Green Power Monitor
zz.Kohls - Canton | Kohls - Canton | CT | FA | Green Power Monitor
zz.Kohls - East Amherst | Kohls - East Amherst | NY | FA | Green Power Monitor
zz.Kohls - East Brunswick | Kohls - East Brunswick | NJ | FA | Green Power Monitor
zz.Kohls - Edgewood | Kohls - Edgewood | MD | FA | Green Power Monitor
zz.Kohls - Granite Run | Kohls - Granite Run | PA | FA | Green Power Monitor
zz.Kohls - Greece | Kohls - Greece | NY | FA | Green Power Monitor
zz.Kohls - Hanover | Kohls - Hanover | PA | FA | Green Power Monitor
zz.Kohls - Horsehead | Kohls - Horsehead | NY | FA | Green Power Monitor
zz.Kohls - Hudson | Kohls - Hudson | NY | FA | Green Power Monitor
zz.Kohls - Ithaca | Kohls - Ithaca | NY | FA | Green Power Monitor
zz.Kohls - Kingston | Kohls - Kingston | NY | FA | Green Power Monitor
zz.Kohls - Mechanicsburg | Kohls - Mechanicsburg | PA | FA | Green Power Monitor
zz.Kohls - Middletown | Kohls - Middletown | NJ | FA | Green Power Monitor
zz.Kohls - North Amherst | Kohls - North Amherst | NY | FA | Green Power Monitor
zz.Kohls - Staten Island | Kohls - Staten Island | NY | FA | Green Power Monitor
zz.Kohls - Warminster | Kohls - Warminster | PA | FA | Green Power Monitor
zz.Kohls - Waterbury | Kohls - Waterbury | CT | FA | Green Power Monitor
zz.Mojave Water Agency - Headquarters | Mojave Water Agency - Headquarters | CA | FA | Green Power Monitor
zz.CSU - Bakersfield | CSU - Bakersfield | CA | FA | Green Power Monitor
zz.Greenfield USD - Fairfield ES | Greenfield USD - Fairfield ES | CA | FA | Green Power Monitor
zz.Greenfield USD - Granite Point ES | Greenfield USD - Granite Point ES | CA | FA | Green Power Monitor
zz.Greenfield USD - Greenfield MS | Greenfield USD - Greenfield MS | CA | FA | Green Power Monitor
zz.Greenfield USD - Horizon ES | Greenfield USD - Horizon ES | CA | FA | Green Power Monitor
zz.Greenfield USD - McKee MS | Greenfield USD - McKee MS | CA | FA | Green Power Monitor
zz.Greenfield USD - Plantation ES | Greenfield USD - Plantation ES | CA | FA | Green Power Monitor
zz.Greenfield USD - Planz ES | Greenfield USD - Planz ES | CA | FA | Green Power Monitor
zz.Greenfield USD - Raffaello Palla ES | Greenfield USD - Raffaello Palla ES | CA | FA | Green Power Monitor
zz.Greenfield USD - Valle Verde ES | Greenfield USD - Valle Verde ES | CA | FA | Green Power Monitor
zz.Greenfield USD - W.A. Kendrick ES | Greenfield USD - W.A. Kendrick ES | CA | FA | Green Power Monitor
zz.Muroc Joint USD - Boron HS | Muroc Joint USD - Boron HS | CA | FA | Green Power Monitor
zz.Muroc Joint USD - W. Boron ES | Muroc Joint USD - W. Boron ES | CA | FA | Green Power Monitor
zz.Colusa - WTP | Colusa - WTP | CA | FA | Green Power Monitor
zz.CDCR-North Kern State Prision | CDCR-North Kern State Prision | CA |  | Green Power Monitor
zz.Muroc Joint USD - District Office | Muroc Joint USD - District Office | CA | FA | Green Power Monitor
zz.Whole Foods - Manhattan Beach | Whole Foods - Manhattan Beach | CA | FA | Green Power Monitor
zz.Pioneer USD - Frontier ES | Pioneer USD - Frontier ES | CA | FA | Green Power Monitor
zz.Pioneer USD - Pioneer ES | Pioneer USD - Pioneer ES | CA | FA | Green Power Monitor
zz.Pioneer USD - Pioneer MS | Pioneer USD - Pioneer MS | CA | FA | Green Power Monitor
zz.Kingsburg Joint UHSD - Kingsburg HS | Kingsburg Joint UHSD - Kingsburg HS | CA | FA | Green Power Monitor
CADRB | CADRB | CA | FA | Green Power Monitor
zz.CDCR-CA State Prison LA County | CDCR-CA State Prison LA County | CA |  | Green Power Monitor
zz.Central USD Akers ES | Central USD Akers ES | CA |  | Green Power Monitor
zz.CUSD - District Office | CUSD - District Office | CA | FA | Green Power Monitor
zz.Parlier - WTP | Parlier - WTP | CA |  | Green Power Monitor
zz.Snowline SD - Quail Valley MS | Snowline SD - Quail Valley MS | CA | FA | Green Power Monitor
zz.Snowline SD - Serrano HS - Middle Lot | Snowline SD - Serrano HS - Middle Lot | CA |  | Green Power Monitor
zz.Snowline SD - Pinon Hills ES | Snowline SD - Pinon Hills ES | CA | FA | Green Power Monitor
zz.Ramona - Santa Maria WTP | Ramona - Santa Maria WTP | CA | FA | Green Power Monitor
zz.Kohls - Redding | Kohls - Redding | CA | FA | Green Power Monitor
zz.Kohls - Salinas | Kohls - Salinas | CA | FA | Green Power Monitor
zz.Kohls - San Bernardino - Central | Kohls - San Bernardino - Central | CA |  | Green Power Monitor
zz.Kohls - Sonora | Kohls - Sonora | CA | FA | Green Power Monitor
zz.CUSD - Stratford ES | CUSD - Stratford ES | CA | FA | Green Power Monitor
zz.Taft - City Hall | Taft - City Hall | CA | FA | Green Power Monitor
zz.Taft - Federal Prison | Taft - Federal Prison | CA | FA | Green Power Monitor
zz.Taft - Police Department | Taft - Police Department | CA | FA | Green Power Monitor
zz.Colusa - WTP | Taft - WTP | CA |  | Green Power Monitor
zz.CDCR - CA Correctional Institution | CDCR - CA Correctional Institution | CA |  | Green Power Monitor
zz.CDCR - CA Correctional Institution II | CDCR - CA Correctional Institution II | CA |  | Green Power Monitor
zz.Snowline SD - Vista Verde ES | Snowline SD - Vista Verde ES | CA | FA | Green Power Monitor
North Stonington - 450 Providence-New London Tpk | North Stonington | CT |  | Green Power Monitor