## Year to Date
BRANDFON |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 137022.76 | 0 | 137022.76 | 0% | 90595 | 46427.76 | 51.25%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Brandfon Honda | CT | 63472.69 | 0 | 63472.69 |  | 90595 | -27122.31 | -29.94%
New Haven - Brandfon Hyundai | CT | 73550.07 | 0 | 73550.07 |  | 0 | 0

## 1st Qtr
BRANDFON |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 50544.54 | 0 | 50544.54 | 0% | 32021 | 18523.54 | 57.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Brandfon Honda | CT | 23518.69 | 0 | 23518.69 |  | 32021 | -8502.31 | -26.55%
New Haven - Brandfon Hyundai | CT | 27025.85 | 0 | 27025.85 |  | 0 | 0

## 2nd Qtr
BRANDFON |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 86478.22 | 0 | 86478.22 | 0% | 58574 | 27904.22 | 47.64%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Brandfon Honda | CT | 39954 | 0 | 39954 |  | 58574 | -18620 | -31.79%
New Haven - Brandfon Hyundai | CT | 46524.22 | 0 | 46524.22 |  | 0 | 0

## 3rd Qtr
BRANDFON |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Brandfon Honda | CT | 0 | 0 | 0 |  | 0 | 0
New Haven - Brandfon Hyundai | CT | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
BRANDFON |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Branford - Brandfon Honda | CT | 0 | 0 | 0 |  | 0 | 0
New Haven - Brandfon Hyundai | CT | 0 | 0 | 0 |  | 0 | 0

## Jan
BRANDFON |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 11534.15 | 0 | 11534.15 | 0% | 6972 | 4562.15 | 65.44%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT | 5527.7 | N/A |  |  | 6972 | -1444.3 | -20.72% | 1.Inverter 5 experienced a late start at 12:00 on 01/01. Additionally, it went offline on 01/18 due to an insulation fault and came back online on 01/20. 2.Inverter 2 was offline on 01/19 due to Insulation resist/Ground Fuse fault and self-resolved on 01/20. 3. Low generation due to snow/rain. | 1.SR095178 2.SR095703 | SR095703
New Haven - Brandfon Hyundai | CT | 6006.45 | N/A |  |  | N/A

## Feb
BRANDFON |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 14122.42 | 0 | 14122.42 | 0% | 9497 | 4625.42 | 48.7%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT | 6524.59 | N/A |  |  | 9497 | -2972.41 | -31.3% | 1. Inverter 5 experienced late starts on 02/01, 02/03, 02/04, and 02/07 due to an insulation resistance/ground fuse fault. 2. Inverter 2 was offline since mornig and back online at 14:15 on 02/01 due to Insulation fault. 3. Low generation due to snow/rain. | 1.SR095178 2.SR095703 | SR095703
New Haven - Brandfon Hyundai | CT | 7597.83 | N/A |  |  | N/A

## Mar
BRANDFON |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 24887.97 | 0 | 24887.97 | 0% | 15552 | 9335.97 | 60.03%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT | 11466.4 | N/A |  |  | 15552 | -4085.6 | -26.27% | 1.Inverter 3 tripped offline at 13:45 on 05/25/24, reporting "Power output outside specified range." Inverter 3 is currently locked out and will require a PUK code for access. Further troubleshooting will need to be performed by SMA. | 1. SR085236
New Haven - Brandfon Hyundai | CT | 13421.57 | N/A |  |  | N/A |  |  | 1. Inverter 3 producing ~4kW down compared to peer inverters, possibly string down since 08/30/24. 2. Inverter 2 is derating by 2 kW on high irradiance days. First occurrence on 4/29/24. Possible fan issue. | 1. SR089771 2. SR085289 | SR085289

## Apr
BRANDFON |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 29010.07 | 0 | 29010.07 | 0% | 17255 | 11755.07 | 68.13%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT | 13321.6 | N/A |  |  | 17255 | -3933.4 | -22.8% | 1. Inverter 3 was offline for whole month. | 1. SR085236
New Haven - Brandfon Hyundai | CT | 15688.47 | N/A |  |  | N/A |  |  | 1. Inverter 3 producing ~4kW down compared to peer inverters, possibly string down since 08/30/24. | 1.SR089771 2.SR103756 | SR103756

## May
BRANDFON |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 27751.23 | 0 | 27751.23 | 0% | 20385 | 7366.23 | 36.14%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT | 12823.1 | N/A |  |  | 20385 | -7561.9 | -37.1% | 1. Inverter 3 was offline for whole month. | 1. SR085236
New Haven - Brandfon Hyundai | CT | 14928.13 | N/A |  |  | N/A |  |  | 1. Inverter 3 producing ~4kW down compared to peer inverters, possibly string down since 08/30/24. | 1. SR089771 2.SR103756 | SR103756

## Jun
BRANDFON |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 29716.92 | 0 | 29716.92 | 0% | 20934 | 8782.92 | 41.96%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT | 13809.3 | N/A |  |  | 20934 | -7124.7 | -34.03% | 1. Inverter 3 was offline for whole month. | 1. SR085236
New Haven - Brandfon Hyundai | CT | 15907.62 | N/A |  |  | N/A |  |  | 1. Inverter 3 producing ~4kW down compared to peer inverters, possibly string down since 08/30/24. 2. Inverter 2 dropped production to 50% at 9:45am on 06/11due to DC A input tripped offline and reporting "Fault / Input A defective / | 1. SR089771 2. SR102859 | SR102859

## Jul
BRANDFON |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT |  | 0
New Haven - Brandfon Hyundai | CT |  | 0

## Aug
BRANDFON |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT |  | 0
New Haven - Brandfon Hyundai | CT |  | 0

## Sep
BRANDFON |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT |  | 0
New Haven - Brandfon Hyundai | CT |  | 0

## Oct
BRANDFON |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT |  | 0
New Haven - Brandfon Hyundai | CT |  | 0

## Nov
BRANDFON |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT |  | 0
New Haven - Brandfon Hyundai | CT |  | 0

## Dec
BRANDFON |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Branford - Brandfon Honda | CT |  | 0
New Haven - Brandfon Hyundai | CT |  | 0

## Sites
Portfolio: | BRANDFON
Site DAS Name | Site | State | Update | DAS
Brandfon Honda | Branford - Brandfon Honda | CT | AF | PoweTrack
Brandfon Hyundai | New Haven - Brandfon Hyundai | CT | A | PoweTrack