## Year to Date
ALIGNED |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 5249489.1144 | 5408311.778 | -158822.6636 | -2.937% | 6785322.3 | -1535833.1856 | -22.63%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 753681 | 776319.165 | -22638.165 | -2.916% | 1062900 | -309219 | -29.09%
Loudon - 7046 Pleasant Street | NH | 814239.4999 | 887813.03 | -73573.5301 | -8.287% | 1028835.7 | -214596.2001 | -20.86%
Nashua - Pennichuck Water East | NH | 815650.5 | 826021.305 | -10370.805 | -1.256% | 707336 | 108314.5 | 15.31%
Nashua - Pennichuck Water West | NH | 620773.8312 | 528726.627 | 92047.2042 | 17.41% | 841600 | -220826.1688 | -26.24%
Boothbay - Wiscasset Road | ME | 532951.813 | 564398.352 | -31446.539 | -5.572% | 610900 | -77948.187 | -12.76%
Thorndike - Leonard Road | ME | 495412.1875 | 557091.494 | -61679.3065 | -11.07% | 1251326.5 | -755914.3125 | -60.41%
Topsham - Solarize LLC | ME | 420394.2503 | 419567.005 | 827.2453 | 0.1972% | 447590 | -27195.7497 | -6.076%
Cherryfield - 727 North Main St (IRA) | ME | 796386.0325 | 848374.8 | -51988.7675 | -6.128% | 834834.1 | -38448.0675 | -4.605%

## 1st Qtr
ALIGNED |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1148376.8312 | 1241693.46 | -93316.6288 | -7.515% | 1469478.1 | -321101.2688 | -21.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 265531 | 297220.15 | -31689.15 | -10.66% | 437000 | -171469 | -39.24%
Loudon - 7046 Pleasant Street | NH | 304616.5 | 396427 | -91810.5 | -23.16% | 419806.1 | -115189.6 | -27.44%
Nashua - Pennichuck Water East | NH | 331162.5 | 294876.74 | 36285.76 | 12.31% | 290072 | 41090.5 | 14.17%
Nashua - Pennichuck Water West | NH | 247066.8312 | 253169.57 | -6102.7388 | -2.411% | 322600 | -75533.1688 | -23.41%
Boothbay - Wiscasset Road | ME | 0 | 0 | 0 |  | 0 | 0
Thorndike - Leonard Road | ME | 0 | 0 | 0 |  | 0 | 0
Topsham - Solarize LLC | ME | 0 | 0 | 0 |  | 0 | 0
Cherryfield - 727 North Main St (IRA) | ME | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
ALIGNED |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 4101112.2831 | 4166618.318 | -65506.0349 | -1.572% | 5315844.2 | -1214731.9169 | -22.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 488150 | 479099.015 | 9050.985 | 1.889% | 625900 | -137750 | -22.01%
Loudon - 7046 Pleasant Street | NH | 509622.9999 | 491386.03 | 18236.9699 | 3.711% | 609029.6 | -99406.6001 | -16.32%
Nashua - Pennichuck Water East | NH | 484488 | 531144.565 | -46656.565 | -8.784% | 417264 | 67224 | 16.11%
Nashua - Pennichuck Water West | NH | 373707 | 275557.057 | 98149.943 | 35.62% | 519000 | -145293 | -27.99%
Boothbay - Wiscasset Road | ME | 532951.813 | 564398.352 | -31446.539 | -5.572% | 610900 | -77948.187 | -12.76%
Thorndike - Leonard Road | ME | 495412.1875 | 557091.494 | -61679.3065 | -11.07% | 1251326.5 | -755914.3125 | -60.41%
Topsham - Solarize LLC | ME | 420394.2503 | 419567.005 | 827.2453 | 0.1972% | 447590 | -27195.7497 | -6.076%
Cherryfield - 727 North Main St (IRA) | ME | 796386.0325 | 848374.8 | -51988.7675 | -6.128% | 834834.1 | -38448.0675 | -4.605%

## 3rd Qtr
ALIGNED |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 0 | 0 | 0 |  | 0 | 0
Loudon - 7046 Pleasant Street | NH | 0 | 0 | 0 |  | 0 | 0
Nashua - Pennichuck Water East | NH | 0 | 0 | 0 |  | 0 | 0
Nashua - Pennichuck Water West | NH | 0 | 0 | 0 |  | 0 | 0
Boothbay - Wiscasset Road | ME | 0 | 0 | 0 |  | 0 | 0
Thorndike - Leonard Road | ME | 0 | 0 | 0 |  | 0 | 0
Topsham - Solarize LLC | ME | 0 | 0 | 0 |  | 0 | 0
Cherryfield - 727 North Main St (IRA) | ME |  | 0 |  |  | 0 | 0

## 4th Qtr
ALIGNED |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Conway -US 302 and Stirch Road | NH | 0 | 0 | 0 |  | 0 | 0
Loudon - 7046 Pleasant Street | NH | 0 | 0 | 0 |  | 0 | 0
Nashua - Pennichuck Water East | NH | 0 | 0 | 0 |  | 0 | 0
Nashua - Pennichuck Water West | NH | 0 | 0 | 0 |  | 0 | 0
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Jan
ALIGNED |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 346871.4782 | 348784.49 | -1913.0118 | -0.5485% | 387367.4 | -40495.9218 | -10.45% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 80975 | 75060.55 | 5914.45 | 7.88% | 118300 | -37325 | -31.55% | 1. The Site tripped offline at 10:00AM to 12:15 on 01/10 due to tech on site to work on the air break switch at the pole. 2. The site tripped offline at 01:15 AM on 01/20 due to the main breaker tripping. The site back online at 10:15 on 01/21 after resetting the SEL and main breaker. 3. Inverter 4 offline from 11/30/2024 due to Permanent fault of power module - Fault and it has been RMA'd & remain offline from 12/02/2024. | 1. SR094963 2. SR095713 3. SR093738
Loudon - 7046 Pleasant Street | NH | 94149.5 | 123337.6 | -29188.1 | -23.67% | 110003.4 | -15853.9 | -14.41% | 1. The site tripped offline from 10:15 to 13:15 on 01/08 due to Grid Phase Voltage out of range. After being re-energized, the site is back online. | 1. SR095389
Nashua - Pennichuck Water East | NH | 97358.6357 | 67312.38 | 30046.2557 | 44.64% | 72464 | 24894.6357 | 34.35% | 1. Weather station experiencing seasonal shading from January to March resulting in expected energy value reporting low. Actual production is not being impacted | 1. SR099647
Nashua - Pennichuck Water West | NH | 74388.3425 | 83073.96 | -8685.6175 | -10.46% | 86600 | -12211.6575 | -14.1% | 1. Site generation was low due to rain/snow
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Feb
ALIGNED |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 260811.3697 | 383101.45 | -122290.0803 | -31.92% | 474636.9 | -213825.5303 | -45.05% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 50574.1816 | 92518.7 | -41944.5184 | -45.34% | 140800 | -90225.8184 | -64.08% | 1. Inverter 4 offline from 11/30/2024 due to Permanent fault of power module - Fault and it has been RMA'd & remain offline from 12/02/24. | 1.SR093738
Loudon - 7046 Pleasant Street | NH | 68847.5 | 123029.3 | -54181.8 | -44.04% | 138036.9 | -69189.4 | -50.12% | 1. Site generation was low due to rain/snow
Nashua - Pennichuck Water East | NH | 84190.3643 | 90026.76 | -5836.3957 | -6.483% | 91800 | -7609.6357 | -8.289% | 1. Weather station experiencing seasonal shading from January to March resulting in expected energy value reporting low. Actual production is not being impacted | 1. SR099647
Nashua - Pennichuck Water West | NH | 57199.3238 | 77526.69 | -20327.3662 | -26.22% | 104000 | -46800.6762 | -45% | 1. Site generation was low due to rain/snow
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Mar
ALIGNED |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 540693.9834 | 509807.52 | 30886.4634 | 6.058% | 607473.8 | -66779.8166 | -10.99% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 133981.8184 | 129640.9 | 4340.9184 | 3.348% | 177900 | -43918.1816 | -24.69% | 1. Site tripped offline at 11:00 AM due to main breaker trip and back online at 15:45 on 03/07 after technician has reset the relay. 2.Site tripped offline at 5:15 AM on 03/17 due to main breaker trip and back online at 8:15AM on 03/18 after technician reset relay. 3.Inverter 4 was offline from 11/30/2024 due to Permanent fault of power module - Fault0010 and it has been RMA'd from 12/02/24. Technician has replaced the RMA'd inverter with a new Chint inverter, bringing it back online and producing from 03/12 at 13:00. | 1.SR098258 2.SR098648 3.SR093738 | SR098648 | SR093738
Loudon - 7046 Pleasant Street | NH | 141619.5 | 150060.1 | -8440.6 | -5.625% | 171765.8 | -30146.3 | -17.55% | 1.Site tripped offline at 5:33AM on 03/07 due to utility outage and was back online at 14:45 on 03/08 after technician has reset SEL and re-energize the site. | 1.SR098240
Nashua - Pennichuck Water East | NH | 149613.5 | 137537.6 | 12075.9 | 8.78% | 125808 | 23805.5 | 18.92% | 1. Weather station experiencing seasonal shading from January to March resulting in expected energy value reporting low. Actual production is not being impacted | 1. SR099647
Nashua - Pennichuck Water West | NH | 115479.165 | 92568.92 | 22910.245 | 24.75% | 132000 | -16520.835 | -12.52%
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Apr
ALIGNED |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 1104316.488 | 1080231.758 | 24084.73 | 2.23% | 1355401.3 | -251084.812 | -18.52% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 169580.5 | 161751.515 | 7828.985 | 4.84% | 192500 | -22919.5 | -11.91% | 1.Site tripped offline between 8:45AM to 11:45Am on 04/07 due to loss of utility power later technician reset main breaker and re-energised the site. | 1.SR099472
Loudon - 7046 Pleasant Street | NH | 169913.505 | 165500.23 | 4413.275 | 2.667% | 187247.5 | -17333.995 | -9.257% | 1. Inverter 1.2 has tripped offline 13:30 on 04/29 due to Grid Phase Voltage Out of Range - GridV.OutLim fault. Inverter self resolved at 15:45 on the same day. | 1.SR100664
Nashua - Pennichuck Water East | NH | 164578.201 | 175490.065 | -10911.864 | -6.218% | 131368 | 33210.201 | 25.28% | 1.Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. | 1.SR099647
Nashua - Pennichuck Water West | NH | 126556 | 96930.197 | 29625.803 | 30.56% | 143000 | -16444 | -11.5% | 1. Inverter 5 experienced derating of approximately 44 kW to 50 kW during peak hours on 04/19, 04/24, 04/28, and 04/29 due to an External Fan Error. The issue self-resolved on the following days. | 1.SR100020
Boothbay - Wiscasset Road | ME | 174667.813 | 176099.452 | -1431.639 | -0.813% | 186049 | -11381.187 | -6.117%
Thorndike - Leonard Road | ME | 165038.875 | 172328.694 | -7289.819 | -4.23% | 380356.8 | -215317.925 | -56.61% | 1.Site tripped offline from 12:15AM to 14:00 on 04/07. | 1.SR099480
Topsham - Solarize LLC | ME | 133981.594 | 132131.605 | 1849.989 | 1.4% | 134880 | -898.406 | -0.6661% | 1.Inverter 1 tripped offline at 12:30 AM on 04/24 due to a "Grid Voltage > Installation" fault related to a grid connection issue. It was brought back online at 4:45 PM the same day after a technician reset the breaker. 2.The weather station has been starting late on multiple days throughout the month. | 1.SR100347
Cherryfield - 727 North Main St (IRA) | ME

## May
ALIGNED |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 1370681.6601 | 1378772.24 | -8090.5799 | -0.5868% | 1994351.5 | -623669.8399 | -31.27%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 133175 | 133034.1 | 140.9 | 0.1059% | 216200 | -83025 | -38.4% | 1. The site tripped offline at 08:00 on 05/12 due to a main breaker trip. A technician was on-site on 05/13 and reset the breaker. The site came back online at 16:00 on 05/13. 2. The site was taken offline from 12:53 to 13:27 on 05/16 while a technician was on-site for a preventive maintenance work. | 1. SR101376 2. PM8049
Loudon - 7046 Pleasant Street | NH | 157983.6224 | 148646.9 | 9336.7224 | 6.281% | 211772.2 | -53788.5776 | -25.4%
Nashua - Pennichuck Water East | NH | 142766.1615 | 162107 | -19340.8385 | -11.93% | 144688 | -1921.8385 | -1.328% | 1. The site tripped offline at 08:30 on 05/28. The technician later re-energized the site, and it came back online at 15:00 on 05/28. 2. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. | 1. SR102029 2. SR099647 | SR099647
Nashua - Pennichuck Water West | NH | 109093 | 83703.94 | 25389.06 | 30.33% | 216200 | -107107 | -49.54% | 1. The site tripped offline at 08:30 on 05/28. The technician later re-energized the site, and it came back online at 15:00 on 05/28. 2. The site tripped offline at 11:45 on 05/31. The technician later re-energized the site, and it came back online at 13:45 on 05/31. 3. Inverter 5 has been experiencing derating of approximately 44 to 50 kW during peak hours due to an "External Fan Err" since 04/19. A technician was on-site on 05/19, removed the faulty fan, and installed a new RMA’d fan. The inverter has been producing in line with its peers since 15:00 on 05/19. | 1. SR102030 2. SR102218 3. SR100020 | SR102218 | SR100020
Boothbay - Wiscasset Road | ME | 173991 | 176162 | -2171 | -1.232% | 213942 | -39951 | -18.67% | 1. Site production was low on 05/08 and 05/09 because a technician was on-site performing preventive maintenance work. | 1. PM13669
Thorndike - Leonard Road | ME | 172047.625 | 178637.2 | -6589.575 | -3.689% | 432588.1 | -260540.475 | -60.23% | 1. Inverters 2 and 3 tripped offline at 14:15 on 05/28 due to "Waiting for grid voltage > Installation failure grid connection > Check grid and fuses". A technician was on-site on 05/29 and closed the inverter breakers. Both inverters came back online at 15:00 on 05/29. However, Inverter 2 tripped offline again at 10:15 on 05/30, followed by Inverter 3 at 13:30 on 05/30, both due to "Waiting for grid voltage". | 1. SR102061
Topsham - Solarize LLC | ME | 129390.5312 | 128884.4 | 506.1313 | 0.3927% | 155893 | -26502.4688 | -17% | 1. Inverter 1 tripped offline at 11:30 on 05/01due to "Waiting for grid voltage > Installation failure grid connection > Check grid and fuses". A technician was on-site on 05/01 and replaced the faulty inverter breaker with a spare one. The inverter came back online at 15:30 on 05/21. | 1. SR100825
Cherryfield - 727 North Main St (IRA) | ME | 352234.72 | 367596.7 | -15361.98 | -4.179% | 403068.2 | -50833.48 | -12.61% | 1. Site outage (06/24-06/25). | 1.SR103383

## Jun
ALIGNED |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 1626114.135 | 1707614.32 | -81500.185 | -4.773% | 1966091.4 | -339977.265 | -17.29%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH | 185394.5 | 184313.4 | 1081.1 | 0.5866% | 217200 | -31805.5 | -14.64% | 1. The site tripped offline at 11:15 on 06/11 and came back online at 16:04 on the same day. 2. Inverter 2 tripped offline at 15:00 on 06/23 due to 'Grid Line Voltage Out of Range' and came back online at 10:00 on 06/24. 3. Inverter 3 tripped offline at 07:00 on 06/12 and came back online at 07:15 on 06/13. | 1. SR102825 2. SR103332 3. SR102780 | SR103332 | SR102780
Loudon - 7046 Pleasant Street | NH | 181725.8725 | 177238.9 | 4486.9725 | 2.532% | 210009.9 | -28284.0275 | -13.47% | 1. The site tripped offline at 13:30 on 06/20 and came back online at 12:45 on 06/21. | 1. SR103230
Nashua - Pennichuck Water East | NH | 177143.6375 | 193547.5 | -16403.8625 | -8.475% | 141208 | 35935.6375 | 25.45% | 1. Weather station is experiencing seasonal shading from 2023. Production is not being impacted but the expected energy value reporting low due to shading. | 1. SR099647
Nashua - Pennichuck Water West | NH | 138058 | 94922.92 | 43135.08 | 45.44% | 159800 | -21742 | -13.61%
Boothbay - Wiscasset Road | ME | 184293 | 212136.9 | -27843.9 | -13.13% | 210909 | -26616 | -12.62% | 1. Inverter 4 tripped offline at 14:45 on 06/05 due to 'Waiting for Grid Voltages' and came back online at 14:45 on 06/06. It tripped offline again at 11:45 on 06/08 due to 'Installation Failure - Grid Connection' and later came back online at 13:00 on 06/10. 2. Inverter 5 tripped offline at 10:00 on 06/11 and has been offline since then. | 1. SR102549 2. SR102549, SR102969 | SR102549 | SR102969
Thorndike - Leonard Road | ME | 158325.6875 | 206125.6 | -47799.9125 | -23.19% | 438381.6 | -280055.9125 | -63.88% | 1. Inverter 2 was offline from 10:15 on 05/30, and Inverter 3 was offline from 13:30 on 05/30 due to 'Waiting for Grid Voltage.' Inverter 2 came back online at 13:00 on 06/20, but Inverter 3 has remained offline since then. | 1. SR102971, SR102367, SR102061 | SR102367 | SR102061
Topsham - Solarize LLC | ME | 157022.125 | 158551 | -1528.875 | -0.9643% | 156817 | 205.125 | 0.1308% | 1. The site tripped offline at 06:00 on 06/17 and came back online at 10:30 on the same day. 2. Inverter 5 tripped offline at 12:15 on 06/24 due to 'Installation Failure - Grid Connection' and came back online at 07:30 on 06/25. | 1. SR103058 2. SR103397 | SR103397
Cherryfield - 727 North Main St (IRA) | ME | 444151.3125 | 480778.1 | -36626.7875 | -7.618% | 431765.9 | 12385.4125 | 2.869% | 1. The site tripped offline at 09:15 on 06/24 and came back online at 09:15 on 06/25. | 1. SR103383

## Jul
ALIGNED |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH
Loudon - 7046 Pleasant Street | NH
Nashua - Pennichuck Water East | NH
Nashua - Pennichuck Water West | NH
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Aug
ALIGNED |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH
Loudon - 7046 Pleasant Street | NH
Nashua - Pennichuck Water East | NH
Nashua - Pennichuck Water West | NH
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Sep
ALIGNED |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH
Loudon - 7046 Pleasant Street | NH
Nashua - Pennichuck Water East | NH
Nashua - Pennichuck Water West | NH
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Oct
ALIGNED |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH
Loudon - 7046 Pleasant Street | NH
Nashua - Pennichuck Water East | NH
Nashua - Pennichuck Water West | NH
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Nov
ALIGNED |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH
Loudon - 7046 Pleasant Street | NH
Nashua - Pennichuck Water East | NH
Nashua - Pennichuck Water West | NH
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Dec
ALIGNED |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Conway -US 302 and Stirch Road | NH
Loudon - 7046 Pleasant Street | NH
Nashua - Pennichuck Water East | NH
Nashua - Pennichuck Water West | NH
Boothbay - Wiscasset Road | ME
Thorndike - Leonard Road | ME
Topsham - Solarize LLC | ME
Cherryfield - 727 North Main St (IRA) | ME

## Sites
Portfolio: | ALIGNED
Site DAS Name | Site | State | Update | DAS
Conway - Lake | Conway -US 302 and Stirch Road | NH | AEF | PowerTrack
Loudon Pleasant Street Solar GSSG | Loudon - 7046 Pleasant Street | NH | AEF | PowerTrack
Pennichuck Water East GSSG | Nashua - Pennichuck Water East | NH | AEF | PowerTrack
Pennichuck Water West GSSG | Nashua - Pennichuck Water West | NH | AEF | PowerTrack
Boothbay Solar | Boothbay - Wiscasset Road | ME |  | PowerTrack
Thorndike Solar | Thorndike - Leonard Road | ME |  | PowerTrack
Topsham Solar | Topsham - Solarize LLC | ME |  | PowerTrack
Cherryfield | Cherryfield - 727 North Main St (IRA) | ME |  | PowerTrack