## Year to Date
Greenbacker Capital |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 29287073.5272 | 28134184.5373 | 1152888.9899 | 4.098% | 22300857.36 | 6986216.1672 | 31.33%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 81514.4375 | 78039.672 | 3474.7655 | 4.453% | 89427.97 | -7913.5325 | -8.849%
15 Walpole Park South | MA | 289560 | 304822.56 | -15262.56 | -5.007% | 312391.38 | -22831.38 | -7.309%
19 Walpole Park South | MA | 179084.375 | 184329.01 | -5244.635 | -2.845% | 199361.61 | -20277.235 | -10.17%
23 Walpole Park South | MA | 225242.75 | 239852.84 | -14610.09 | -6.091% | 261606.85 | -36364.1 | -13.9%
24 Walpole Park South | MA | 365599.75 | 319399.22 | 46200.53 | 14.46% | 402342.99 | -36743.24 | -9.132%
25 Walpole Park South | MA | 340198.5 | 361272.69 | -21074.19 | -5.833% | 408191.36 | -67992.86 | -16.66%
3 Walpole Park South | MA | 434557.6875 | 466556.65 | -31998.9625 | -6.859% | 486667.67 | -52109.9825 | -10.71%
4 Walpole Park South | MA | 252434.5 | 263024.96 | -10590.46 | -4.026% | 269962.82 | -17528.32 | -6.493%
Brockton | MA | 426164.5 | 394896.82 | 31267.68 | 7.918% | 452635.33 | -26470.83 | -5.848%
Canton | MA | 396546.75 | 407536.46 | -10989.71 | -2.697% | 432580.18 | -36033.43 | -8.33%
Chelsea | MA | 708407 | 718292.4 | -9885.4 | -1.376% | 724220.72 | -15813.72 | -2.184%
Hamilton Landfill | MA | 537959.13 | 655973.28 | -118014.15 | -17.99% | 0 | 176669.6
Holliston | MA | 981242 | 1133135.57 | -151893.57 | -13.4% | 1176462.28 | -195220.28 | -16.59%
Natick HS - Carports | MA | 336701.181 | 426779.582 | -90078.401 | -21.11% | 0 | 105302.9
Norton | MA | 36513.4999 | 291741.2 | -255227.7001 | -87.48% | 599800.2 | -563286.7001 | -93.91%
Palmer - Boston Rd. | MA | 363262.5 | 355123.65 | 8138.85 | 2.292% | 419500 | -56237.5 | -13.41%
Shirley Bartkus | MA | 509436.0578 | 618560.06 | -109124.0022 | -17.64% | 646175 | -136738.9422 | -21.16%
Stoughton | MA | 480946 | 327549.85 | 153396.15 | 46.83% | 486485.41 | -5539.41 | -1.139%
Wellfleet Landfill | MA | 602294.533 | 618950.486 | -16655.953 | -2.691% | 0 | 210714
Wilmington Garage & Building 7 | MA | 611157.75 | 729294.38 | -118136.63 | -16.2% | 742306.41 | -131148.66 | -17.67%
Woburn | MA | 942462.8644 | 1098790.3 | -156327.4356 | -14.23% | 1049324.21 | -106861.3456 | -10.18%
Friendship Solar 1 | MD | 2222573 | 2312994.7 | -90421.7 | -3.909% | 2661091.4 | -438518.4 | -16.48%
Friendship Solar 2 | MD | 2162728 | 2354600.5 | -191872.5 | -8.149% | 2635348.4 | -472620.4 | -17.93%
101 Carnegie Center | NJ | 351305.724 | 425581.318 | -74275.594 | -17.45% | 0 | 342707.354
302 Carnegie Center | NJ | 388360.87 | 408824.544 | -20463.674 | -5.005% | 0 | 152769.524
510 Carnegie Center | NJ | 969963.046 | 1109729.729 | -139766.683 | -12.59% | 0 | 366376.853
701 Carnegie Center | NJ | 761408.47 | 882427.167 | -121018.697 | -13.71% | 0 | 295715.548
Hudson County Correction | NJ | 990115.7451 | 948220.38 | 41895.3651 | 4.418% | 1077905.21 | -87789.4649 | -8.144%
ER Bison Solar | PA | 1031512 | 200043.6 | 831468.4 | 415.6% | 1140137 | -108625 | -9.527%
Danville | IL | 1846604.446 | 0 | 1846604.446 |  | 0 | 788803.73
Camden - Campbell Soup HQ | NJ | 1579811 | 2580362.7319 | -1000551.7319 | -38.78% | 2731211.54 | -1151400.54 | -42.16%
Westport - Pine Hill | MA | 2458437.3211 | 711236.4 | 1747200.9211 | 245.7% | 2895721.42 | -437284.0989 | -15.1%
Oaks Landfill - ANEM | MD | 1789208.592 | 2055491.8124 | -266283.2204 | -12.95% | 0 | 573344.3
Oaks Landfill - CS2 | MD | 1800200.201 | 2069751.718 | -269551.517 | -13.02% | 0 | 560672.3
Oaks Landfill - CS1 | MD | 1833559.346 | 2080998.297 | -247438.951 | -11.89% | 0 | 584094.9
Plympton - Upland Solar - PV & BESS (IRA) | MA

## 1st Qtr
Greenbacker Capital |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 11287095.4432 | 12049918.6999 | -762823.2567 | -6.331% | 7707275.33 | 3579820.1132 | 46.45%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 28480.5 | 30150.152 | -1669.652 | -5.538% | 30894.78 | -2414.28 | -7.815%
15 Walpole Park South | MA | 99535.5 | 124192.25 | -24656.75 | -19.85% | 105340.49 | -5804.99 | -5.511%
19 Walpole Park South | MA | 59076.125 | 73197.7 | -14121.575 | -19.29% | 67768.36 | -8692.235 | -12.83%
23 Walpole Park South | MA | 76139 | 94797.78 | -18658.78 | -19.68% | 88133.96 | -11994.96 | -13.61%
24 Walpole Park South | MA | 120525.5 | 112494.58 | 8030.92 | 7.139% | 135652.04 | -15126.54 | -11.15%
25 Walpole Park South | MA | 115304.0628 | 140624.52 | -25320.4572 | -18.01% | 138033.84 | -22729.7772 | -16.47%
3 Walpole Park South | MA | 142878.6875 | 187677.3 | -44798.6125 | -23.87% | 161958.48 | -19079.7925 | -11.78%
4 Walpole Park South | MA | 86259.5 | 108634.01 | -22374.51 | -20.6% | 92343.57 | -6084.07 | -6.589%
Brockton | MA | 149376.5 | 153472.93 | -4096.43 | -2.669% | 153606.27 | -4229.77 | -2.754%
Canton | MA | 135542 | 167175.7 | -31633.7 | -18.92% | 147523.69 | -11981.69 | -8.122%
Chelsea | MA | 251627 | 284169.8 | -32542.8 | -11.45% | 247313.42 | 4313.58 | 1.744%
Hamilton Landfill | MA | 176669.6 | 278430 | -101760.4 | -36.55% | 0 | 176669.6
Holliston | MA | 329638 | 377648.67 | -48010.67 | -12.71% | 392025.68 | -62387.68 | -15.91%
Natick HS - Carports | MA | 105302.9 | 164122.85 | -58819.95 | -35.84% | 0 | 105302.9
Norton | MA | 0 | 0 | 0 |  | 0 | 0
Palmer - Boston Rd. | MA | 143516 | 164176.06 | -20660.06 | -12.58% | 177011 | -33495 | -18.92%
Shirley Bartkus | MA | 217882.5578 | 308199.7 | -90317.1422 | -29.3% | 240628 | -22745.4422 | -9.453%
Stoughton | MA | 171818 | 141376.62 | 30441.38 | 21.53% | 162931.05 | 8886.95 | 5.454%
Wellfleet Landfill | MA | 210714 | 196967.8 | 13746.2 | 6.979% | 0 | 210714
Wilmington Garage & Building 7 | MA | 182135.125 | 283219.88 | -101084.755 | -35.69% | 244076.21 | -61941.085 | -25.38%
Woburn | MA | 296544.5 | 483276.2 | -186731.7 | -38.64% | 345279.41 | -48734.91 | -14.11%
Friendship Solar 1 | MD | 905797 | 959345.1 | -53548.1 | -5.582% | 997729.3 | -91932.3 | -9.214%
Friendship Solar 2 | MD | 900552 | 985864.9 | -85312.9 | -8.654% | 1000565.5 | -100013.5 | -9.996%
101 Carnegie Center | NJ | 342707.354 | 416221.708 | -73514.354 | -17.66% | 0 | 342707.354
302 Carnegie Center | NJ | 152769.524 | 175506.75 | -22737.226 | -12.96% | 0 | 152769.524
510 Carnegie Center | NJ | 366376.853 | 450788.4 | -84411.547 | -18.73% | 0 | 366376.853
701 Carnegie Center | NJ | 295715.548 | 353851.2 | -58135.652 | -16.43% | 0 | 295715.548
Hudson County Correction | NJ | 382514.555 | 336163.78 | 46350.775 | 13.79% | 364717.01 | 17797.545 | 4.88%
ER Bison Solar | PA | 426729 | 0 | 426729 |  | 434940 | -8211 | -1.888%
Danville | IL | 788803.73 | 0 | 788803.73 |  | 0 | 788803.73
Camden - Campbell Soup HQ | NJ | 616249 | 971787.4149 | -355538.4149 | -36.59% | 1018009.01 | -401760.01 | -39.47%
Westport - Pine Hill | MA | 700840.3211 | 711236.4 | -10396.0789 | -1.462% | 960794.26 | -259953.9389 | -27.06%
Oaks Landfill - ANEM | MD | 764378.8 | 931117.2 | -166738.4 | -17.91% | 0 | 573344.3
Oaks Landfill - CS2 | MD | 765667.7 | 936388.9 | -170721.2 | -18.23% | 0 | 560672.3
Oaks Landfill - CS1 | MD | 779029 | 947642.445 | -168613.445 | -17.79% | 0 | 584094.9
Plympton - Upland Solar - PV & BESS (IRA) | MA

## 2nd Qtr
Greenbacker Capital |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 19349311.084 | 17447209.0564 | 1902102.0276 | 10.9% | 16059581.53 | 3289729.554 | 20.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 53033.9375 | 47889.52 | 5144.4175 | 10.74% | 58533.19 | -5499.2525 | -9.395%
15 Walpole Park South | MA | 190024.5 | 180630.31 | 9394.19 | 5.201% | 207050.89 | -17026.39 | -8.223%
19 Walpole Park South | MA | 120008.25 | 111131.31 | 8876.94 | 7.988% | 131593.25 | -11585 | -8.804%
23 Walpole Park South | MA | 149103.75 | 145055.06 | 4048.69 | 2.791% | 173472.89 | -24369.14 | -14.05%
24 Walpole Park South | MA | 245074.25 | 206904.64 | 38169.61 | 18.45% | 266690.95 | -21616.7 | -8.106%
25 Walpole Park South | MA | 224894.4372 | 220648.17 | 4246.2672 | 1.924% | 270157.52 | -45263.0828 | -16.75%
3 Walpole Park South | MA | 291679 | 278879.35 | 12799.65 | 4.59% | 324709.19 | -33030.19 | -10.17%
4 Walpole Park South | MA | 166175 | 154390.95 | 11784.05 | 7.633% | 177619.25 | -11444.25 | -6.443%
Brockton | MA | 276788 | 241423.89 | 35364.11 | 14.65% | 299029.06 | -22241.06 | -7.438%
Canton | MA | 261004.75 | 240360.76 | 20643.99 | 8.589% | 285056.49 | -24051.74 | -8.438%
Chelsea | MA | 456780 | 434122.6 | 22657.4 | 5.219% | 476907.3 | -20127.3 | -4.22%
Hamilton Landfill | MA | 361289.53 | 377543.28 | -16253.75 | -4.305% | 0 | 0
Holliston | MA | 651604 | 755486.9 | -103882.9 | -13.75% | 784436.6 | -132832.6 | -16.93%
Natick HS - Carports | MA | 231398.281 | 262656.732 | -31258.451 | -11.9% | 0 | 0
Norton | MA | 36513.4999 | 291741.2 | -255227.7001 | -87.48% | 599800.2 | -563286.7001 | -93.91%
Palmer - Boston Rd. | MA | 219746.5 | 190947.59 | 28798.91 | 15.08% | 242489 | -22742.5 | -9.379%
Shirley Bartkus | MA | 291553.5 | 310360.36 | -18806.86 | -6.06% | 405547 | -113993.5 | -28.11%
Stoughton | MA | 309128 | 186173.23 | 122954.77 | 66.04% | 323554.36 | -14426.36 | -4.459%
Wellfleet Landfill | MA | 391580.533 | 421982.686 | -30402.153 | -7.205% | 0 | 0
Wilmington Garage & Building 7 | MA | 429022.625 | 446074.5 | -17051.875 | -3.823% | 498230.2 | -69207.575 | -13.89%
Woburn | MA | 645918.3644 | 615514.1 | 30404.2644 | 4.94% | 704044.8 | -58126.4356 | -8.256%
Friendship Solar 1 | MD | 1316776 | 1353649.6 | -36873.6 | -2.724% | 1663362.1 | -346586.1 | -20.84%
Friendship Solar 2 | MD | 1262176 | 1368735.6 | -106559.6 | -7.785% | 1634782.9 | -372606.9 | -22.79%
101 Carnegie Center | NJ | 8598.37 | 9359.61 | -761.24 | -8.133% | 0 | 0
302 Carnegie Center | NJ | 235591.346 | 233317.794 | 2273.552 | 0.9744% | 0 | 0
510 Carnegie Center | NJ | 603586.193 | 658941.329 | -55355.136 | -8.401% | 0 | 0
701 Carnegie Center | NJ | 465692.922 | 528575.967 | -62883.045 | -11.9% | 0 | 0
Hudson County Correction | NJ | 607601.1901 | 612056.6 | -4455.4099 | -0.7279% | 713188.2 | -105587.0099 | -14.8%
ER Bison Solar | PA | 604783 | 200043.6 | 404739.4 | 202.3% | 705197 | -100414 | -14.24%
Danville | IL | 1057800.716 | 0 | 1057800.716 |  | 0 | 0
Camden - Campbell Soup HQ | NJ | 963562 | 1608575.317 | -645013.317 | -40.1% | 1713202.53 | -749640.53 | -43.76%
Westport - Pine Hill | MA | 1757597 | 0 | 1757597 |  | 1934927.16 | -177330.16 | -9.165%
Oaks Landfill - ANEM | MD | 1024829.792 | 1124374.6124 | -99544.8204 | -8.853% | 0 | 0
Oaks Landfill - CS2 | MD | 1034532.501 | 1133362.818 | -98830.317 | -8.72% | 0 | 0
Oaks Landfill - CS1 | MD | 1054530.346 | 1133355.852 | -78825.506 | -6.955% | 0 | 0
Plympton - Upland Solar - PV & BESS (IRA) | MA | 1349333 | 1362943.219 | -13610.219 | -0.9986% | 1465999.5 | -116666.5 | -7.958%

## 3rd Qtr
Greenbacker Capital |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
15 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
19 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
23 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
24 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
25 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
3 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
4 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
Brockton | MA | 0 | 0 | 0 |  | 0 | 0
Canton | MA | 0 | 0 | 0 |  | 0 | 0
Chelsea | MA | 0 | 0 | 0 |  | 0 | 0
Hamilton Landfill | MA | 0 | 0 | 0 |  | 0 | 0
Holliston | MA | 0 | 0 | 0 |  | 0 | 0
Natick HS - Carports | MA | 0 | 0 | 0 |  | 0 | 0
Norton | MA | 0 | 0 | 0 |  | 0 | 0
Palmer - Boston Rd. | MA | 0 | 0 | 0 |  | 0 | 0
Shirley Bartkus | MA | 0 | 0 | 0 |  | 0 | 0
Stoughton | MA | 0 | 0 | 0 |  | 0 | 0
Wellfleet Landfill | MA | 0 | 0 | 0 |  | 0 | 0
Wilmington Garage & Building 7 | MA | 0 | 0 | 0 |  | 0 | 0
Woburn | MA | 0 | 0 | 0 |  | 0 | 0
Friendship Solar 1 | MD | 0 | 0 | 0 |  | 0 | 0
Friendship Solar 2 | MD | 0 | 0 | 0 |  | 0 | 0
101 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
302 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
510 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
701 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
Hudson County Correction | NJ | 0 | 0 | 0 |  | 0 | 0
ER Bison Solar | PA | 0 | 0 | 0 |  | 0 | 0
Danville | IL | 0 | 0 | 0 |  | 0 | 0
Camden - Campbell Soup HQ | NJ | 0 | 0 | 0 |  | 0 | 0
Westport - Pine Hill | MA | 0 | 0 | 0 |  | 0 | 0
Oaks Landfill - ANEM | MD | 0 | 0 | 0 |  | 0 | 0
Oaks Landfill - CS2 | MD | 0 | 0 | 0 |  | 0 | 0
Oaks Landfill - CS1 | MD | 0 | 0 | 0 |  | 0 | 0
Plympton - Upland Solar - PV & BESS (IRA) | MA

## 4th Qtr
Greenbacker Capital |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
10 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
15 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
19 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
23 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
24 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
25 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
3 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
4 Walpole Park South | MA | 0 | 0 | 0 |  | 0 | 0
Brockton | MA | 0 | 0 | 0 |  | 0 | 0
Canton | MA | 0 | 0 | 0 |  | 0 | 0
Chelsea | MA | 0 | 0 | 0 |  | 0 | 0
Hamilton Landfill | MA | 0 | 0 | 0 |  | 0 | 0
Holliston | MA | 0 | 0 | 0 |  | 0 | 0
Natick HS - Carports | MA | 0 | 0 | 0 |  | 0 | 0
Norton | MA | 0 | 0 | 0 |  | 0 | 0
Palmer - Boston Rd. | MA | 0 | 0 | 0 |  | 0 | 0
Shirley Bartkus | MA | 0 | 0 | 0 |  | 0 | 0
Stoughton | MA | 0 | 0 | 0 |  | 0 | 0
Wellfleet Landfill | MA | 0 | 0 | 0 |  | 0 | 0
Wilmington Garage & Building 7 | MA | 0 | 0 | 0 |  | 0 | 0
Woburn | MA | 0 | 0 | 0 |  | 0 | 0
Friendship Solar 1 | MD | 0 | 0 | 0 |  | 0 | 0
Friendship Solar 2 | MD | 0 | 0 | 0 |  | 0 | 0
101 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
302 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
510 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
701 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0
Hudson County Correction | NJ | 0 | 0 | 0 |  | 0 | 0
ER Bison Solar | PA | 0 | 0 | 0 |  | 0 | 0
Danville | IL | 0 | 0 | 0 |  | 0 | 0
Camden - Campbell Soup HQ | NJ | 0 | 0 | 0 |  | 0 | 0
Westport - Pine Hill | MA | 0 | 0 | 0 |  | 0 | 0
Oaks Landfill - ANEM | MD | 0 | 0 | 0 |  | 0 | 0
Oaks Landfill - CS2 | MD | 0 | 0 | 0 |  | 0 | 0
Oaks Landfill - CS1 | MD | 0 | 0 | 0 |  | 0 | 0
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Jan
Greenbacker Capital |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 2570856.9448 | 3159610.8919 | -588753.9471 | -18.63% | 1580526.447 | 990330.4978 | 62.66% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 6082.5625 | 6594.437 | -511.8745 | -7.762% | 6789.067 | -706.5045 | -10.41% | 1. Site production was low due to rain/ snow.
15 Walpole Park South | MA | 22096 | 34986.43 | -12890.43 | -36.84% | 21495.47 | 600.53 | 2.794% | 1. Site production was low due to rain/ snow.
19 Walpole Park South | MA | 12286.625 | 18535.3 | -6248.675 | -33.71% | 14377.87 | -2091.245 | -14.54% | 1. Site production was low due to rain/ snow.
23 Walpole Park South | MA | 17017.5 | 24815.12 | -7797.62 | -31.42% | 18470.54 | -1453.04 | -7.867% | 1.Inverter 1&3 tripped offline at 12:45PM on 01/04 due to Grid Line Voltage Out of Range fault and back online at 11:45AM on 01/06 after technician re-energised, Inverter 2 stopped communicating at 12:30PM from 01/04, upon technician arrival he found inverter 2 was also offline and is being RMA'd. | 1.SR095312
24 Walpole Park South | MA | 23711.25 | 19088.14 | 4623.11 | 24.22% | 28498.52 | -4787.27 | -16.8% | 1.Inverter 10 tripped offline from 06/18/24 due to Relay fault - Fault0100 and is being RMA'd. 2.Inverter 8 was offline on 01/18 and back online on 01/19. 3.Site was taken offline from 09:15AM to 10:15AM on 01/13 due to technicians checked-in to replace the SEL751a relay battery. | 1.SR089997 2.SR095693 3.SR094233 | SR095693 | SR094233
25 Walpole Park South | MA | 24218 | 32717.42 | -8499.42 | -25.98% | 28984.84 | -4766.84 | -16.45% | 1.Inverter 13 was RMA'd since 08/20/24 due to thermal event in powerhead of the inverter. | 1.SR089170, SR095220 | SR095220
3 Walpole Park South | MA | 32137.6875 | 51986.12 | -19848.4325 | -38.18% | 34626.19 | -2488.5025 | -7.187% | 1.Inverter 9 was offline from 11/02/24 due to Protect 0010 fault and is being RMA'd . 2.The site was taken offline at 10:30 AM on 01/22 as the technician checked in to replace the SEL 751 UPS battery cluster and site was brought back online at 14:30 on 01/23. | 1.SR089564, SR093404 2.SR093406 | SR093404 | SR093406
4 Walpole Park South | MA | 18926.5 | 30719.42 | -11792.92 | -38.39% | 19589.08 | -662.58 | -3.382% | 1. Site production was low due to rain/ snow.
Brockton | MA | 35242.5 | 41958.95 | -6716.45 | -16.01% | 35711.3 | -468.8 | -1.313% | 1. Site production was low due to rain/ snow.
Canton | MA | 30237.25 | 44905.17 | -14667.92 | -32.66% | 30749.97 | -512.72 | -1.667% | 1. Site production was low due to rain/ snow.
Chelsea | MA | 66681 | 78143.31 | -11462.31 | -14.67% | 54727.88 | 11953.12 | 21.84% | 1.Inverter B3 is being RMA'd from 12/19/24. 2.Site was taken offfline from 08:30AM to 11:00AM on 01/13 due to technicians checked-in to examine Transformer-1. 3.Inverter C1 tripped offline at 9AM on 01/03 due to Bus hardware overvoltage fault and back online on 01/04, Inverter C1 failed to restart post transformer inspection and was faulted with a "Fault 0020" fault code and after technician powercycled, inverter resumed its production. 4.Inverters C6 & D5 tripped offline at 14:30 on 01/18 due to Steady state GFCI fault and self-resolved on 01/19. 5.Inverter C6 tripped offline at 12:15PM on 01/31. | 1.SR093500 2.SR094025 3.SR094028, SR095517 4.SR095697 5.SR096199 | SR094025 | SR094028 | SR095517 | SR095697 | SR096199
Hamilton Landfill | MA | 39385.7 | 87354.4 | -47968.7 | -54.91% | 0 | 39385.7 |  | 1. Site production was low due to rain/ snow.
Holliston | MA | 79918 | 88133.87 | -8215.87 | -9.322% | 84310.38 | -4392.38 | -5.21% | 1.Inverter 2 right unit has multiple tripping events throughout the month due to low irradiance days. | 1.SR095300, SR095690 | SR095690
Natick HS - Carports | MA | 23101.5 | 43562.15 | -20460.65 | -46.97% | 0 | 23101.5 |  | 1. Site production was low due to rain/ snow.
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site tripped offline on 04/01/24 at 16:00 and still offline. Ameresco received a Scope of Work to conduct repairs on the existing system to prepare it safely for partial re-energization. | 1.SR092249,SR093403 & SR096031 | SR093403 | SR096031
Palmer - Boston Rd. | MA | 34752 | 49692.76 | -14940.76 | -30.07% | 45090 | -10338 | -22.93% | 1.The site tripped offline at 22:54 on 01/29 due to an open SEL relay caused by a utility power under-voltage loss. It was brought back online at 13:30 on 01/30 after the technician closed the relay and re-energized the site. | 1.SR096132
Shirley Bartkus | MA | 52517.5578 | 87390.5 | -34872.9422 | -39.9% | 65151 | -12633.4422 | -19.39% | 1. Inverter 34 tripped offline at 03:15 PM on 01/02 and was RMA'd. The technician brought it back online at 01:45 PM on 01/09 by replacing the inverter. 2. Inverter 12 started late for production on 01/04 and 01/05 and went offline on 01/06. On 01/07, technicians confirmed that the inverter had been RMA'd and brought it back online at 02:15 PM on 01/10 by replacing it with a new one. 3. Site tripped offline at 02:24 AM on 01/22 due to a missing Phase A voltage. The technician brought it back online at 08:27 AM on 01/22 by re-energizing the site. 4.Inverter 27 has been offline since 09/05/2024 and is currently being RMA'd. | 1.SR095279 2.SR095309,SR095058 3.SR095843 4.SR089983 | SR095309 | SR095058 | SR095843 | SR089983
Stoughton | MA | 42082 | 42134.57 | -52.57 | -0.1248% | 35429.71 | 6652.29 | 18.78%
Wellfleet Landfill | MA | 37109.9 | 40845.2 | -3735.3 | -9.145% | 0 | 37109.9 |  | 1. Inverters 11 and 12 tripped offline at 09:15 AM on 01/11 due to a generic inverter fault and came back online at 09:00 AM on 01/23. | 1. SR095497
Wilmington Garage & Building 7 | MA | 40128.75 | 74682.38 | -34553.63 | -46.27% | 51215.54 | -11086.79 | -21.65% | 1. Inverter 12 has been RMA'D and offline. 2.Due to snow event, the site has performed very low on 01/11 to 01/30 | 1.SR094678 2.SR096154 | SR096154
Woburn | MA | 70710.5 | 143603 | -72892.5 | -50.76% | 69288.01 | 1422.49 | 2.053% | 1.Inverter 17 is offline since 12/25/2024 due to reporting ARC Protection Fault and technician broought it back online at 08:15AM on 01/06 . 2.Inverter 2 tripped offline on 01/13 and is being RMA'd. The technician stated that the inverters are showing fault codes related to bus overvoltage and arc faults. 3.Inverter 17 tripped offline at 08:45 AM on 01/14, reporting an ARC protection fault. The technician brought it back online at 02:15 PM by clearing the faults. 4.Inverter 3 tripped offline at 07:54 AM on 01/15, reporting an ARC protection fault. The technician brought it back online at 09:00 AM on 01/16 by clearing the fault. 5.Inverter 17 tripped offline at 07:49 AM on 01/16, reporting an ARC protection fault. The technician brought it back online at 01:00 PM by clearing the faults. 6.Inverter 27 tripped offline at 07:46 AM on 01/25 due to an ARC protection fault. The technician brought it back online at 09:45 AM on 01/27 by clearing the fault. | 1.SR095079 2.SR095518 3.SR095538 4.SR095579 5.SR095616 6.SR095972 | SR095518 | SR095538 | SR095579 | SR095616 | SR095972
Friendship Solar 1 | MD | 249779 | 269841.3 | -20062.3 | -7.435% | 251554.7 | -1775.7 | -0.7059% | 1.Inverters 1 to 8 are underperforming by 10KW possibly due to seasonal shading. | 1.SR092108
Friendship Solar 2 | MD | 244225 | 284533.5 | -40308.5 | -14.17% | 248916.6 | -4691.6 | -1.885% | 1. Site production was low due to rain/ snow.
101 Carnegie Center | NJ | 67113.5 | 112416 | -45302.5 | -40.3% | 0 | 67113.5 |  | 1. Inverter 19 tripped offline at 12:30PM on 01/ 11 and back online at 07:00AM on 01/12 due to Generic inverter fault. 2. Inverter 02 tripped offline at 10:45 AM on 01/17 and back online at 07:00 AM on 01/18. Additionally, Inverters 2, 18, and 19 tripped offline at 12:45 PM on 01/18 and back online at 07:00 AM on 01/19 due to a generic fault. | 1. SR095495 2. SR095674 | SR095674
302 Carnegie Center | NJ | 32360.8 | 47003.55 | -14642.75 | -31.15% | 0 | 32360.8 |  | 1. Site production was low due to rain/ snow.
510 Carnegie Center | NJ | 66360.4 | 119861.4 | -53501 | -44.64% | 0 | 66360.4 |  | 1. Inverters 2, 5, 6, 12, and 24 tripped offline at 11:45 AM on 01/11 and back online at 07:00 AM on 01/12. Again, Inverters 1, 2, 5, 6, and 24 tripped offline at 10:30 AM on 01/17 and back online at 07:00 AM on 01/18. Then, Inverters 1, 2, 5, 6, 9, 12, 14, 15, and 24 tripped offline at 12:30 PM on 01/18 and back online at 07:00 AM on 01/19. Lastly, Inverters 2, 5, 6, and 24 tripped offline at 08:15 AM on 01/31 due to a "Generic Inverter Fault. | 1. SR095494
701 Carnegie Center | NJ | 61625.285 | 91246.2 | -29620.915 | -32.46% | 0 | 61625.285 |  | 1. Site production was low due to rain/ snow.
Hudson County Correction | NJ | 85632.077 | 85344.2 | 287.877 | 0.3373% | 86957.91 | -1325.833 | -1.525%
ER Bison Solar | PA | 93337 | 0 | 93337 |  | 100651 | -7314 | -7.267% | 1. Inverter 2 tripped offline at 11:45 AM on 01/07 and back online at 09:15 AM on 01/21. It tripped offline again at 12:15 PM on 01/23 and back online at 10:00 AM on 01/24 due to the grid line voltage over limit fault & broken module and is being RMA'd. | 1. SR095360, SR092627, SR095903 | SR092627 | SR095903
Danville | IL | 235052.1 | 0 | 235052.1 |  | 0 | 235052.1
Camden - Campbell Soup HQ | NJ | 136065 | 211584.3949 | -75519.3949 | -35.69% | 247940.87 | -111875.87 | -45.12% | 1. Meter MTRO1 has no communicatuion whole month due to an faulty meter. Additional troubleshooting is required. The actual energy which we updated was addition of four meters. 2. On 01/27/25, during a PM event, the technician identified 8 faulty modules on the CTC roof that needed replacement. 3. On 01/02 technician was onsite replaced powerhead and communication card for inverters 66 and 67 and they started reporting. 4. Inverter 4-1 was offline since 12/30/24 due to an faulty combiner box. Working with SMA for replacement. | 1. SR094890, SR094283 2. SR095761, PM11788. 3. SR094889 4. SR095199 | SR094283 | SR095761 | SR094889 | SR095199
Westport - Pine Hill | MA
Oaks Landfill - ANEM | MD | 191034.5 | 295011.1 | -103976.6 | -35.24% | 0 |  |  | 1. Inverter C02 didn't started for production and remained offline whole day. On 01/10 technician powercycled and inverter back online at 11:40AM. However inverter again tripped offline at 14:55 on the same day. On 01/23 technician replaced contactors and inverter back online at 11:35AM. | 1. SR095429
Oaks Landfill - CS2 | MD | 204995.4 | 297441.8 | -92446.4 | -31.08% | 0 |  |  | 1. Inverter B8 didn't started for production and after a remote reset inverter back online at 10:40AM on 01/16. However on 01/21 inverter again not started and remained offline whole day. On 01/22 technician troubleshooted and brought inverter back online at 10:40AM. | 1. SR095620
Oaks Landfill - CS1 | MD | 194934.1 | 303478.8 | -108544.7 | -35.77% | 0 |  |  | 1. Site production was low due to rain/ snow.
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Feb
Greenbacker Capital |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 3016821.2016 | 3451366.027 | -434544.8254 | -12.59% | 2547649.923 | 469171.2786 | 18.42% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 6516.625 | 9844.495 | -3327.87 | -33.8% | 9440.373 | -2923.748 | -30.97% | 1. Site production was low due to rain/ snow.
15 Walpole Park South | MA | 21837.25 | 36784.89 | -14947.64 | -40.64% | 32560.05 | -10722.8 | -32.93% | 1. Site production was low due to rain/ snow.
19 Walpole Park South | MA | 12228.625 | 22549.93 | -10321.305 | -45.77% | 20740.84 | -8512.215 | -41.04% | 1. Site production was low due to rain/ snow.
23 Walpole Park South | MA | 16135.25 | 28847.06 | -12711.81 | -44.07% | 26843.33 | -10708.08 | -39.89% | 1.Inverter 2 was being RMA'D and offline since 01/04. 2. Site production was low due to rain/ snow. | 1.SR095312
24 Walpole Park South | MA | 26878.5 | 36446.02 | -9567.52 | -26.25% | 41222.64 | -14344.14 | -34.8% | 1.Inverter 10 has been offline since 06/18/24 due to a relay fault (Fault0100) and is being RMA'd. Upon the technician's arrival on 02/26, the inverter was brought back online at 11:00 AM by replacing the old inverter with a new one. 2. Site production was low due to rain/ snow. | 1.SR089997
25 Walpole Park South | MA | 26057.5 | 44560.8 | -18503.3 | -41.52% | 42155.98 | -16098.48 | -38.19% | 1.Inverter 13 was RMA'd since 08/20/24 due to thermal event in powerhead of the inverter. 2. Site production was low due to rain/ snow. | 1.SR089170, SR095220 | SR095220
3 Walpole Park South | MA | 29594.5 | 56389.79 | -26795.29 | -47.52% | 49000.49 | -19405.99 | -39.6% | 1.Inverter 9 was offline from 11/02/24 due to Protect 0010 fault and is being RMA'd 2. Site production was low due to rain/ snow. | 1.SR089564, SR093404 | SR093404
4 Walpole Park South | MA | 18725 | 32601.8 | -13876.8 | -42.56% | 28311.4 | -9586.4 | -33.86% | 1. Site production was low due to rain/ snow.
Brockton | MA | 40084 | 46732.03 | -6648.03 | -14.23% | 45176.38 | -5092.38 | -11.27% | 1. Site production was low due to rain/ snow.
Canton | MA | 30642 | 51143.48 | -20501.48 | -40.09% | 47910.52 | -17268.52 | -36.04% | 1. Site production was low due to rain/ snow.
Chelsea | MA | 57572 | 85329.99 | -27757.99 | -32.53% | 76722.24 | -19150.24 | -24.96% | 1.Inverter C6 tripped offline at 12:15PM on 01/31 and back online at 07:00AM on 02/01. 2..Inverter B3 is being RMA'd from 12/19/24. | 1.SR096199 2.SR093500 | SR093500
Hamilton Landfill | MA | 37244.9 | 84502.5 | -47257.6 | -55.92% | 0 | 37244.9 |  | 1.The site was in battery mode at 11:00 PM on 01/31. On 02/01, upon the technician's arrival, the site was re-energized and brought back online at 10:45 AM on 02/01. 2. Site production was low due to rain/ snow. | 1.SR096206
Holliston | MA | 58828 | 110053.2 | -51225.2 | -46.55% | 122550.9 | -63722.9 | -52% | 1.Inverter 6 middle unit tripped at 02:45PM reporting DC Isolation fault and back online at 07:15AM on 02/08. | 1.SR096522
Natick HS - Carports | MA | 20164.9 | 49332.8 | -29167.9 | -59.12% | 0 | 20164.9 |  | 1. Site production was low due to rain/ snow.
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site tripped offline on 04/01/24 at 16:00 and still offline. Ameresco received a Scope of Work to conduct repairs on the existing system to prepare it safely for partial re-energization. | 1.SR096031, SR093403 | SR093403
Palmer - Boston Rd. | MA | 44869.5 | 50040.7 | -5171.2 | -10.33% | 62743 | -17873.5 | -28.49% | 1. Site production was low due to rain/ snow.
Shirley Bartkus | MA | 47532.5 | 102227.3 | -54694.8 | -53.5% | 77292 | -29759.5 | -38.5% | 1.Inverter 27 has been offline since 09/05/2024 and is currently being RMA'd. 2. 1. Site production was low due to rain/ snow. | 1.SR089983
Stoughton | MA | 40713.5 | 44340.04 | -3626.54 | -8.179% | 49251.51 | -8538.01 | -17.34% | 1. Site production was low due to rain/ snow.
Wellfleet Landfill | MA | 70649.4 | 63196.6 | 7452.8 | 11.79% | 0 | 70649.4
Wilmington Garage & Building 7 | MA | 24053.5 | 86845 | -62791.5 | -72.3% | 78334.27 | -54280.77 | -69.29% | 1.Inverter 12 has been RMA'D and offline. 2. Site production was low due to rain/ snow. | 1.SR094678
Woburn | MA | 42553 | 149835.2 | -107282.2 | -71.6% | 111577.8 | -69024.8 | -61.86% | 1.Inverter 2 came back online at 10:15 on 02/24 after the technician replaced the faulty powerhead. 2. Site tripped offline at 09:45 on 02/17/25. On 02/18, the technician reset the SEL relay and re-energized the site at 09:15. 3. Site production was low due to rain/ snow. | 1. SR095518 2. SR097183 | SR097183
Friendship Solar 1 | MD | 252166 | 261838.7 | -9672.7 | -3.694% | 309128.4 | -56962.4 | -18.43% | 1. Inverter 4 tripped offline at 15:45 on 02/16/25 and self resolved at 07:00 on 02/17/25 | 1.SR097175
Friendship Solar 2 | MD | 251622 | 269520.3 | -17898.3 | -6.641% | 320858.4 | -69236.4 | -21.58% | 1. Site production was low due to rain/ snow.
101 Carnegie Center | NJ | 100716.62 | 116147.902 | -15431.282 | -13.29% | 0 | 100716.62 |  | 1. Inverter 19 tripped offline at 09:15 on 02/ 06 and back online at 07:00AM on 02/07 due to Generic inverter fault. 2. On 01/15/25, the technician found a faulty module in Inverter 8 string 8-9 during string testing, requiring replacement. 3. Inverters 14, 15, 18, 19 & 21 are tripped offline at 07:45 on 02/26/25 due to a "Generic Inverter Fault"and the technician adjusted the GFCI parameters, bringing them back online at 15:15 the same day. | 1. SR095495 2. SR095573 3. SR095674 | SR095573 | SR095674
302 Carnegie Center | NJ | 44694.589 | 48280.5 | -3585.911 | -7.427% | 0 | 44694.589
510 Carnegie Center | NJ | 109429.522 | 125043.8 | -15614.278 | -12.49% | 0 | 109429.522 |  | 1. Inverters 2, 5, 6, and 24 tripped offline at 08:15 AM on 01/31 due to a "Generic Inverter Fault" and self-resolved on 02/01. Inverters 2 and 24 tripped again at 10:30 on 02/03 and came back online on 02/04. Inverters 2, 5, and 24 tripped at 11:10 on 02/09 and self-resolved on 02/10. On 02/26, Inverters 1, 2, 5, and 14 went offline, and the technician adjusted the GFCI parameters, bringing them back online at 13:15 the same day. | 1. SR095494
701 Carnegie Center | NJ | 85922.263 | 98223 | -12300.737 | -12.52% | 0 | 85922.263 |  | 1. Inverter 4 & 6 tripped offline at 10:45 on 02/27/25 due to an Generic inverter fault. on 02/28, the technician adjusted the parametres and brought back online at 07:00 the same day. | 1. SR097872
Hudson County Correction | NJ | 112037.289 | 99361.98 | 12675.309 | 12.76% | 104683.2 | 7354.089 | 7.025%
ER Bison Solar | PA | 123697 | 0 | 123697 |  | 138798 | -15101 | -10.88% | 1. Site production was low due to rain/ snow.
Danville | IL | 245073.86 | 0 | 245073.86 |  | 0 | 245073.86
Camden - Campbell Soup HQ | NJ | 176271 | 288404.22 | -112133.22 | -38.88% | 330103.7 | -153832.7 | -46.6% | 1. Meter MTRO1 has no communicatuion whole month due to an faulty meter. On 03/10 technican troubleshooted but didnot worked. Meter require replacement. 2. Inverter 4-1 was offline since 12/30/24 due to an faulty combiner box. On 02/03/25, the technician replaced faulty onces with new CB and site brought back online at 07:27 on 02/04. 3. On 01/27/25, during a PM event, the technician identified 8 faulty modules on the CTC roof that needed replacement. 4. On 01/15/25, during a PM event , the technician identified faulty positive DC terminal at Inverter 7-5 and additional troubleshooting is required to restore power. 5. Numerous inverters in the BNB Camden site do not communicate to PowerFactors. Many appear to be duplicates. | 1. SR093773, SR094890 2. SR095199 3. SR095761, PM11788, SR096555 4. SR096557, SR096558, PM11794 5. SR097964 | SR094890 | SR095199 | SR095761 | SR096555 | SR096557 | SR096558 | SR097964
Westport - Pine Hill | MA | 149810.5086 | 177997.7 | -28187.1914 | -15.84% | 422244.5 | -272433.9914 | -64.52% | 1. Site was offline due to faulty utility recloser from 12:30 on 02/17/25 and Eversource Tech was able to close the recloser, site is back online at 15:30 on 02/25/25. | 1. SR097196, SR097608 | SR097608
Oaks Landfill - ANEM | MD | 227626.1 | 255454.2 | -27828.1 | -10.89% | 0 | 227626.1 |  | 1. Site production was low due to rain/ snow.
Oaks Landfill - CS2 | MD | 232986.3 | 257135.7 | -24149.4 | -9.392% | 0 | 232986.3 |  | 1. Inverter B08 experienced late started issue throughout the month and on 02/28 technician troubleshooted but didn't work and inverter IGBT on phase A was being RMA'd. | 1. SR096221
Oaks Landfill - CS1 | MD | 231887.7 | 262354.4 | -30466.7 | -11.61% | 0 | 231887.7 |  | 1. Site production was low due to rain/ snow.
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Mar
Greenbacker Capital |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 5699417.2968 | 5438941.781 | 260475.5158 | 4.789% | 3579098.96 | 2120318.3368 | 59.24% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 15881.3125 | 13711.22 | 2170.0925 | 15.83% | 14665.34 | 1215.9725 | 8.291%
15 Walpole Park South | MA | 55602.25 | 52420.93 | 3181.32 | 6.069% | 51284.97 | 4317.28 | 8.418% | 1.The weather station equipment on the DAS is showing some odd readings | 1.SR070225
19 Walpole Park South | MA | 34560.875 | 32112.47 | 2448.405 | 7.624% | 32649.65 | 1911.225 | 5.854%
23 Walpole Park South | MA | 42986.25 | 41135.6 | 1850.65 | 4.499% | 42820.09 | 166.16 | 0.388% | 1.Inverter 2 was being RMA'D and offline since 01/04. | 1.SR095312
24 Walpole Park South | MA | 69935.75 | 56960.42 | 12975.33 | 22.78% | 65930.88 | 4004.87 | 6.074%
25 Walpole Park South | MA | 65028.5628 | 63346.3 | 1682.2628 | 2.656% | 66893.02 | -1864.4572 | -2.787% | 1.Inverter 13 was RMA'd since 08/20/24 due to thermal event in powerhead of the inverter. | 1.SR095220,SR089170 | SR089170
3 Walpole Park South | MA | 81146.5 | 79301.39 | 1845.11 | 2.327% | 78331.8 | 2814.7 | 3.593% | 1.Inverter 9 was offline from 11/02/24 due to Protect 0010 fault and is being RMA'd . | 1.SR089564, SR093404 | SR093404
4 Walpole Park South | MA | 48608 | 45312.79 | 3295.21 | 7.272% | 44443.09 | 4164.91 | 9.371%
Brockton | MA | 74050 | 64781.95 | 9268.05 | 14.31% | 72718.59 | 1331.41 | 1.831% | 1.The site tripped offline at 04:00 AM on 03/07. Upon the technician's arrival on the same day, it was found that the main breaker had tripped. The site was brought back online at 09:00 AM on 03/07 by closing the main breaker. 2.The site tripped offline at 07:15 AM on 03/09. Upon the technician's arrival on the same day, it was found that the main breaker was open. The site was brought back online at 03:15 PM on 03/09 by closing the main breaker. 3.Inverter 6 tripped offline at 16:30 on 03/11 and reporting an 'Error.' Upon the technician's arrival on 03/12, he re-energized the inverter and brought it back online at 12:45 on 03/12 and the inverter is running with two strings down. 4.Inverter 6 is underperforming by 6KW. | 1.SR098239 2.SR098314 3.SR098404 4.SR099133 | SR098314 | SR098404 | SR099133
Canton | MA | 74662.75 | 71127.05 | 3535.7 | 4.971% | 68863.2 | 5799.55 | 8.422% | 1. Inverter 3 tripped offline at 15:45 on 03/10 due to an ARC fault. Upon the technician's arrival, he cleared the fault and brought it back online at 11:45 on 03/12. | 1.SR098378
Chelsea | MA | 127374 | 120696.5 | 6677.5 | 5.532% | 115863.3 | 11510.7 | 9.935% | 1.The Inverter B3 is being RMA'd since 12/19/24, awaiting Greenbeckers' response to proceed with the replacement of the inverter. | 1.SR093500
Hamilton Landfill | MA | 100039 | 106573.1 | -6534.1 | -6.131% | 0 | 100039
Holliston | MA | 190892 | 179461.6 | 11430.4 | 6.369% | 185164.4 | 5727.6 | 3.093% | 1.Inverter 11 middle unit tripped offline at 13:15 on 03/10, Upon technicians arrival on 03/12 brought it back online at 09:00. 2.Inverter 6 left unit tripped offline at 14:00 on 03/08 ,Upon technicians arrival on 03/12 brought it back online at 08:00. 3.Inverter 1 right unit was underperforming by 15KW from 02/28. | 1.SR098367 2.SR098369 3.SR099134 | SR098369 | SR099134
Natick HS - Carports | MA | 62036.5 | 71227.9 | -9191.4 | -12.9% | 0 | 62036.5 |  | 1. Site production was low on 03/05, 03/16, 03/17 and 03/24 due to bad weather.
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site tripped offline on 04/01/24 at 16:00 and still offline. Ameresco received a Scope of Work to conduct repairs on the existing system to prepare it safely for partial re-energization. | 1.SR096031, SR093403, SR097902, SR098208, SR099015 | SR093403 | SR097902 | SR098208 | SR099015
Palmer - Boston Rd. | MA | 63894.5 | 64442.6 | -548.1 | -0.8505% | 69178 | -5283.5 | -7.638% | 1. The site was offline at 3:00 AM on 03/07 due to the SEL relay being in the open position. After the technician reset the SEL relay, the site came back online at 10:15 AM on 03/08. | 1. SR098246
Shirley Bartkus | MA | 117832.5 | 118581.9 | -749.4 | -0.632% | 98185 | 19647.5 | 20.01% | 1.The site was offline at 10:30 AM to 2:15 PM on 03/07, but it later self-resolved. | 1. SR098268
Stoughton | MA | 89022.5 | 54902.01 | 34120.49 | 62.15% | 78249.83 | 10772.67 | 13.77% | 1. Inverter 7 was offline on multiple days on 03/21, 03/24, and 03/30, due to a bus differential high fault. | 1. SR098865
Wellfleet Landfill | MA | 102954.7 | 92926 | 10028.7 | 10.79% | 0 | 102954.7
Wilmington Garage & Building 7 | MA | 117952.875 | 121692.5 | -3739.625 | -3.073% | 114526.4 | 3426.475 | 2.992% | 1.Inverter 12 has been RMA'D and offline,Awaiting for the Greenbackers approval for the replacement of new inverter. | 1.SR094678
Woburn | MA | 183281 | 189838 | -6557 | -3.454% | 164413.6 | 18867.4 | 11.48%
Friendship Solar 1 | MD | 403852 | 427665.1 | -23813.1 | -5.568% | 437046.2 | -33194.2 | -7.595%
Friendship Solar 2 | MD | 404705 | 431811.1 | -27106.1 | -6.277% | 430790.5 | -26085.5 | -6.055%
101 Carnegie Center | NJ | 174877.234 | 187657.806 | -12780.572 | -6.811% | 0 | 174877.234 |  | 1.Inverter 8 was taken offline by technicians on 03/12 from 13:00 to 13:30 to replace a module in Inverter 8's array. | 1.SR095573
302 Carnegie Center | NJ | 75714.135 | 80222.7 | -4508.565 | -5.62% | 0 | 75714.135 |  | 1.Site was taken offline from 07:00 to 10:30 on 03/15 due to a planned outage. After the outage was completed, the site was re-energized. | 1.SR097601
510 Carnegie Center | NJ | 190586.931 | 205883.2 | -15296.269 | -7.43% | 0 | 190586.931 |  | 1.Site was offline from 22:15 on 03/15 to 07:00 on 03/16 | 1.SR098621
701 Carnegie Center | NJ | 148168 | 164382 | -16214 | -9.864% | 0 | 148168
Hudson County Correction | NJ | 184845.189 | 151457.6 | 33387.589 | 22.04% | 173075.9 | 11769.289 | 6.8% | 1.Inverter 3 was offline from 03/17 due to isolation fault.On 03/19,a technician was able to troubleshoot inverter 3 and it is back online producing on site, however the communication board has been RMA'd and mentioned that inverter 3 will not have communication until the board is replaced. | 1.SR098681
ER Bison Solar | PA | 209695 | 0 | 209695 |  | 195491 | 14204 | 7.266% | 1. Inverter 02 tripped offline at 14:15 on 03/10 due to out of range grid line voltage. On 03/11, a technician found DC voltage present but no AC voltage due to a tripped breaker. After resetting it, the inverter was back online and producing at 10:35 AM 2. Inverter 10 &11 tripped offline at 15:55 on 03/25 due to out of range grid line voltage.And Both the inverters are back online at 17:06 EDT on 03/25. | 1.SR098348 2.SR098978 | SR098978
Danville | IL | 308677.77 | 0 | 308677.77 |  | 0 | 308677.77 |  | 1.Site was offline from 02:35 PM on 03/28 to 01:30 PM on 03/29 due to an utility outage. | 1.SR099112
Camden - Campbell Soup HQ | NJ | 303913 | 471798.8 | -167885.8 | -35.58% | 439964.44 | -136051.44 | -30.92% | 1. Meter MTRO1 has no communicatuion whole month due to an faulty meter. it's needed to be replaced and additional troubleshooting is required to restore communications. 2. On 01/27/25, during a PM event, the technician identified 8 faulty modules on the CTC roof that needed replacement. 3. On 01/15/25, during a PM event , the technician identified faulty positive DC terminal at Inverter 7-5. On 03/10 technician visited the site and Wirebox being RMA'd. Further troubleshoot needed. 4. Several inverters at BNB Camden aren't communicating with PowerFactors, with many duplicates. On 03/10, a technician found comms issues, rewired inverters into a daisy chain, and confirmed comms. Only inverter 02-02 required an RMA'd comm board. Remote access to the CTC roof cell modem was confirmed with Zoë from Greenbacker. A return visit is needed once the RMA'd comm board arrives. | 1. SR093773, SR094890 2. SR095761, PM11788, SR096555 3. SR096557, SR096558, PM11794 4. SR097964 | SR094890 | SR095761 | SR096555 | SR096557 | SR096558 | SR097964
Westport - Pine Hill | MA | 551029.8125 | 533238.7 | 17791.1125 | 3.336% | 538549.76 | 12480.0525 | 2.317%
Oaks Landfill - ANEM | MD | 345718.2 | 380651.9 | -34933.7 | -9.177% | 0 | 345718.2
Oaks Landfill - CS2 | MD | 327686 | 381811.4 | -54125.4 | -14.18% | 0 | 327686 |  | 1.Inverter 8 has been RMA'd since 02/28 and will remain offline.On 03/12, a technician replaced the Phase A IGBT, but the fault remained. On 03/28, a technician replaced the DSP and IF boards but the issue persisted. Technician has reached out to Solectria for assistance, and they confirmed IGBT on phase A has still an issue and need to be replaced along with IGHT to interface ribbon and mentioned Inverter 8 will remain offline until parts are replaced. | 1.SR096221
Oaks Landfill - CS1 | MD | 352207.2 | 381809.245 | -29602.045 | -7.753% | 0 | 352207.2
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Apr
Greenbacker Capital |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 5757250.0876 | 5030180.3633 | 727069.7243 | 14.45% | 4229865.09 | 1527384.9976 | 36.11% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 17430.6875 | 14974.71 | 2455.9775 | 16.4% | 17864.88 | -434.1925 | -2.43% | 1. Inverter 2 is tripping on and offline from 04/02. On 04/09 technician has inspected with the inverter and found no issues on inverter and it requires additional troubleshooting with the Solectria and created a case with them. | 1.SR099342
15 Walpole Park South | MA | 61346.5 | 58290.96 | 3055.54 | 5.242% | 62988.5 | -1642 | -2.607% | 1.The weather station equipment on the DAS is showing some odd readings | 1.SR070225
19 Walpole Park South | MA | 38723.5 | 35777.09 | 2946.41 | 8.235% | 40058.73 | -1335.23 | -3.333%
23 Walpole Park South | MA | 47950.5 | 45953.57 | 1996.93 | 4.346% | 52671.75 | -4721.25 | -8.964% | 1.Inverter 2 was being RMA'D and offline since 01/04. | 1.SR095312
24 Walpole Park South | MA | 79297.25 | 66368.43 | 12928.82 | 19.48% | 81047.66 | -1750.41 | -2.16%
25 Walpole Park South | MA | 72551.9372 | 70550.84 | 2001.0972 | 2.836% | 82096.83 | -9544.8928 | -11.63% | 1.Inverter 13 was RMA'd since 08/20/24 due to thermal event in powerhead of the inverter. | 1.SR095220 , SR089170 | SR089170
3 Walpole Park South | MA | 92536 | 88494.54 | 4041.46 | 4.567% | 98407.39 | -5871.39 | -5.966% | 1. Inverter 14 is experiencing multiple tripping's from 10:36AM on 04/02 due to AC voltages are in range. Self resolved on 04/03 2.Inverter 9 was offline from 11/02/24 due to Protect 0010 fault and is being RMA'd . | 1. SR099314 2. SR089564 , SR093404 | SR089564 | SR093404
4 Walpole Park South | MA | 53698.75 | 50156.83 | 3541.92 | 7.062% | 54177.5 | -478.75 | -0.8837%
Brockton | MA | 87651.5 | 76452.89 | 11198.61 | 14.65% | 90182.96 | -2531.46 | -2.807% | 1.Inverter 6 was underperforming by 5 kW. On 04/14, technicians found and replaced faulty fuses. The inverter is now producing as expected. | 1. SR099133
Canton | MA | 84271 | 78052.84 | 6218.16 | 7.967% | 82093.69 | 2177.31 | 2.652%
Chelsea | MA | 148626 | 141253.6 | 7372.4 | 5.219% | 145954.7 | 2671.3 | 1.83% | 1.The Inverter B3 is being RMA'd since 12/19/24, awaiting Greenbacker's response to proceed with the replacement of the inverter. | 1. SR093500
Hamilton Landfill | MA | 114374.32 | 118843.8 | -4469.48 | -3.761%
Holliston | MA | 220987 | 232448.3 | -11461.3 | -4.931% | 222646.5 | -1659.5 | -0.7454% | 1.Inverter 1 (right unit) was underperforming by 15 kW from 02/28 and experienced multiple tripping events. On 04/23, a technician updated the software and firmware. The inverter is now operating as expected. 2. Inverter 6 (left unit) tripped offline at 16:00 on 04/16. On 04/23, the technician observed Strings 2–7. String 2.7 remains isolated at the combiner box pending further investigation. 3.Inverter 6 right unit tripped offline from 4/25 at 15:00, reporting AC voltage too high. | 1.SR099134 2. SR10005, SR100102 4. SR100488 | SR10005, | SR100102 | SR100488
Natick HS - Carports | MA | 75020.9 | 84347.6 | -9326.7 | -11.06% | N/A
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site tripped offline on 04/01/24 at 16:00 and still offline. Ameresco received a Scope of Work to conduct repairs on the existing system to prepare it safely for partial re-energization. | 1. SR098208 ,SR096031, SR093403, SR097902, SR098208, SR099015 | SR096031 | SR093403 | SR097902 | SR098208 | SR099015
Palmer - Boston Rd. | MA | 71757 | 66418.32 | 5338.68 | 8.038% | 75993 | -4236 | -5.574% | 1. Inverter 9 tripped offline at 15:45 from 04/19 and reporting "Error". On 04/28 technician replaced inverter 9 and updated the serial number with AlsoEnergy and came back online on same day. | 1.SR100025
Shirley Bartkus | MA | 129216.5 | 113056.8 | 16159.7 | 14.29% | 124491 | 4725.5 | 3.796% | 1.Inverter 8 tripped offline at 14:00 on 04/21. On 04/23, a technician troubleshot the inverter, and it came back online. | 1. SR100098
Stoughton | MA | 100062 | 57277.2 | 42784.8 | 74.7% | 98616.66 | 1445.34 | 1.466% | 1.Inverter 7 was offline on multiple days on 04/01 , 04/12, 04/15 due to a bus differential high fault and self-resolved on following days. | 1.SR099721
Wellfleet Landfill | MA | 116013.7 | 126774.4 | -10760.7 | -8.488% | N/A
Wilmington Garage & Building 7 | MA | 143787.75 | 145754.9 | -1967.15 | -1.35% | 142094.1 | 1693.65 | 1.192% | 1.Inverter 12 has been RMA'D and offline from 12/18/2024. Awaiting for the Greenbackers approval for the replacement of new inverter. | 1.SR094678
Woburn | MA | 211624 | 205620.1 | 6003.9 | 2.92% | 200462.1 | 11161.9 | 5.568%
Friendship Solar 1 | MD | 410415 | 431138.7 | -20723.7 | -4.807% | 513850.3 | -103435.3 | -20.13% | 1"Inverters 1 to 6 were producing low output at 66 kW starting at 09:00 AM on 04/08, while the other inverters were producing 125 kW. AC voltages were within range, and the issue self-resolved at 15:50 on the same day. | 1.SR099514
Friendship Solar 2 | MD | 392850 | 430700 | -37850 | -8.788% | 500221.2 | -107371.2 | -21.46% | 1. ATI Tracker 6X motor 3 is stuck at 39.21degrees on 04/02 at 15:15 and tracker3 setpoint is tracking with the peer trackers. Impacting production of the inverters 7,8,9 after the mid day. On 04/15 technicain technician worked on trackers but are still experiencing issue, requires further troubleshooting. 2.Inverters 7 to 12 and 16 have been producing lower output at 66 kW since 04/08, compared to their peer inverters. Their internal temperatures are also lower than those of the normally operating inverters. Inverters 10 to 12 and 16 self-resolved on the same day, while inverters 7 to 9 remain underperforming, likely due to a tracker issue. | 1.SR099517 2.SR099512 | SR099512
101 Carnegie Center | NJ | 8598.37 | 9359.61 | -761.24 | -8.133% | N/A |  |  | 1.Site was offline at 15:30 on 04/02 due to the switchgear has dried out, but is rusty. The site will remain offline pending repairs to prevent water intrusion. | 1.SR099808
302 Carnegie Center | NJ | 75065.2 | 78635.6 | -3570.4 | -4.54% | N/A
510 Carnegie Center | NJ | 191332.14 | 206221.44 | -14889.3 | -7.22% | N/A
701 Carnegie Center | NJ | 148093.07 | 165557.03 | -17463.96 | -10.55% | N/A
Hudson County Correction | NJ | 196136.4199 | 206152.9 | -10016.4801 | -4.859% | 218963.9 | -22827.4801 | -10.43% | 1.Inverter 3 was offline from 03/17 due to isolation fault.On 03/19,a technician was able to troubleshoot inverter 3 and it is back online producing on site, however the communication board has been RMA'd and mentioned that inverter 3 will not have communication until the board is replaced. On 04/24 new inverter and the left unit is being RMA'd due to thermal event and middle and right units are online and producing, due to error in the inverter right unit production is not capturing. Additional troubleshooting requires to get the inverter into fully operational. 2.Inverter 18 is derating by approximately 13 kW compared to peers and reporting "External fan error" from 04/25 at 13:15 . Self resolved on 04/27 | 1.SR098681 , SR100367 2. SR100422 | SR100367 | SR100422
ER Bison Solar | PA | 210689 | 0 | 210689 |  | 216099 | -5410 | -2.503%
Danville | IL | 317870.75 | 0 | 317870.75 |  | N/A
Camden - Campbell Soup HQ | NJ | 307862 | 540245.5113 | -232383.5113 | -43.01% | 540594.74 | -232732.74 | -43.05% | 1. Meter MTRO1 has no communicatuion whole month due to an faulty meter. it's needed to be replaced and additional troubleshooting is required to restore communications. 2. On 01/27/25, during a PM event, the technician identified 8 faulty modules on the CTC roof that needed replacement. 3. On 01/15/25, during a PM event , the technician identified faulty positive DC terminal at Inverter 7-5. On 03/10 technician visited the site and Wirebox being RMA'd. Further troubleshoot needed. 4. Several inverters at BNB Camden aren't communicating with PowerFactors, with many duplicates. On 03/10, a technician found comms issues, rewired inverters into a daisy chain, and confirmed comms. Only inverter 02-02 required an RMA'd comm board. Remote access to the CTC roof cell modem was confirmed with Zoë from Greenbacker. A return visit is needed once the RMA'd comm board arrives. | 1. SR093773, SR094890 2. SR095761, PM11788, SR096555 3. SR096557, SR096558, PM11794 4. SR097964 | SR094890 | SR095761 | SR096555 | SR096557 | SR096558 | SR097964
Westport - Pine Hill | MA | 553297 | N/A |  |  | 568288 | -14991 | -2.638% | 1. Inverters 14–22 and 24–26 did not start production on 04/03. Inverters 21–22 and 24–26 showed fault activity. All inverters were back online by 12:30PM on the same day | 1. SR099355
Oaks Landfill - ANEM | MD | 327800.23 | 360342.22 | -32541.99 | -9.031% | N/A
Oaks Landfill - CS2 | MD | 314572.289 | 362480.951 | -47908.662 | -13.22% | N/A |  |  | 1.Inverter 8 has been RMA'd since 02/28 and will remain offline.On 03/12, a technician replaced the Phase A IGBT, but the fault remained. On 03/28, a technician replaced the DSP and IF boards but the issue persisted. Technician has reached out to Solectria for assistance, and they confirmed IGBT on phase A has still an issue and need to be replaced along with IGHT to interface ribbon and mentioned Inverter 8 will remain offline until parts are replaced. On 04/28 Replaced inverter CTs, inverter came back online at 11:00AM. | 1. SR096221
Oaks Landfill - CS1 | MD | 335741.824 | 362478.681 | -26736.857 | -7.376% | N/A
Plympton - Upland Solar - PV & BESS (IRA) | MA

## May
Greenbacker Capital |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 6440601.3376 | 5691590.5207 | 749010.8169 | 13.16% | 5611330.29 | 829271.0476 | 14.78%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 17203.25 | 15001.07 | 2202.18 | 14.68% | 20052.08 | -2848.83 | -14.21% | 1.Site production was low due to rain/snow
15 Walpole Park South | MA | 59750 | 56670.34 | 3079.66 | 5.434% | 71158.2 | -11408.2 | -16.03% | 1.Site production was low due to rain/snow
19 Walpole Park South | MA | 37901.5 | 35216.59 | 2684.91 | 7.624% | 45131.29 | -7229.79 | -16.02% | 1.Site production was low due to rain/snow
23 Walpole Park South | MA | 46911 | 45692.54 | 1218.46 | 2.667% | 59661.02 | -12750.02 | -21.37% | 1.Inverter 2 was being RMA'd and offline since 01/04 | 1.SR095312
24 Walpole Park South | MA | 76807.1575 | 63676.02 | 13131.1375 | 20.62% | 91695.8 | -14888.6425 | -16.24% | 1.Site production was low due to rain/snow
25 Walpole Park South | MA | 70780 | 68916.45 | 1863.55 | 2.704% | 92909.61 | -22129.61 | -23.82% | 1.Inverter 13 was RMA'd since 08/20/24 due to thermal event in powerhead of the inverter. | 1.SR089170,SR095220 | SR095220
3 Walpole Park South | MA | 92356.5 | 86038.81 | 6317.69 | 7.343% | 111378.9 | -19022.4 | -17.08% | 1.Site production was low due to rain/snow
4 Walpole Park South | MA | 52249.25 | 48130.67 | 4118.58 | 8.557% | 60816.56 | -8567.31 | -14.09% | 1.Inverter 9 was offline from 11/02/24 due to Protect 0010 fault and is being RMA'd . | 1.SR093404,SR089564 | SR089564
Brockton | MA | 89623.5 | 77995.23 | 11628.27 | 14.91% | 103286.1 | -13662.6 | -13.23% | 1.Site production was low due to rain/snow
Canton | MA | 81933.75 | 75433.98 | 6499.77 | 8.617% | 102038.9 | -20105.15 | -19.7% | 1.Site production was low due to rain/snow
Chelsea | MA | 144715 | 135571.1 | 9143.9 | 6.745% | 163526 | -18811 | -11.5%
Hamilton Landfill | MA | 116749.25 | 122098.24 | -5348.99 | -4.381% | N/A |  |  | 1.Site was tripped offline at 17:30 on 05/22 and was on "Battery Mode".On 05/23 technician checked in and reset SEL after which site was issolved and site was back online at 09:00 on 05/23. | 1.SR101866
Holliston | MA | 204073 | 235790.7 | -31717.7 | -13.45% | 280158.3 | -76085.3 | -27.16% | 1. Inverters 6 and 8 went offline at 14:00 on 05/05 due to "AC voltage too high". The technician later replaced a faulty MC4 connector, and the inverters came back online at 09:40 on 05/07. 2. Inverter 8 (right unit) tripped offline at 16:00 on 05/03 due to "AC voltage too high". A technician, with support from Solectria, later adjusted all parameters, and the inverter resumed normal operation at 09:15 on 05/07. 3. Inverter 2 (left and right units) briefly tripped during periods of high irradiance at multiple instances around 12:00 on 05/14. Later, a technician on site reset the country code, and all three units resumed production at 11:15 on 05/16. 4. Inverter 11 (middle unit) tripped offline at 15:30 on 05/13 due to '3-Phase Possible Arc Detection'; a technician re-energized it, and it resumed normal production from 09:00 on 05/16. It tripped offline again at 12:15 on 05/26 and was re-energized by a technician on 05/30, coming back online at 13:15 on the same day. 5. Inverter 6 left unit tripped offline at 16:50 on 05/14 and later inverter stared producing normally from 09:15 on 05/23. 6.Inverter 8 (left and right units) tripped offline at 16:30 on 05/16. Later, a technician on site on 05/23 re-energized the inverter. The left unit came back online at 09:15 on 05/23, and the right unit is being RMA'd. 7. Inverter 2 right unit did not start production on 05/19 but came online after a remote reset at 11:45; it tripped offline again at 07:00 on 05/21 due to a 'Low Voltage Fault' and resumed operation at 09:00 on 05/22, though it has a history of late starts. 8. Inverter 10 middle unit has been producing low during peak hours since 05/22 due to an 'External Fan Fault,' and the fan is being RMA'd. 9.Inverter 6 right unit tripped offline at 16:30 on 05/25 due to 'AC Voltage Too High.' A technician later power-cycled the inverter on 05/30, and it came back online at 09:45 on the same day. 10. Inverter 8 right and left units tripped offline at 12:53 on 05/26 due to '3-Phase Possible Arc Detection' and are currently being RMA'd. 11. Inverter 1 right unit has been tripping on and off during high irradiance since 05/26 and is currently being RMA'd. 12. Inverter 9 right unit has been tripping on and off since 05/27 and is currently being RMA'd. | 1. SR100488 2. SR101380 3. SR101381 4. SR101443, SR101950 5. SR101655 6. SR101656 7. SR101674, SR101815 8. SR101858 9. SR101930 10. SR101949 11. SR101976 12. SR101977 | SR101380 | SR101381 | SR101443 | SR101950 | SR101655 | SR101656 | SR101674 | SR101815 | SR101858 | SR101930 | SR101949 | SR101976 | SR101977
Natick HS - Carports | MA | 72747.352 | 81077.694 | -8330.342 | -10.27%
Norton | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site tripped offline on 04/01/24 at 16:00 and still offline. Ameresco received a Scope of Work to conduct repairs on the existing system to prepare it safely for partial re-energization. | 1.SR101769,SR098208 ,SR096031, SR093403, SR097902, SR098208, SR099015 | SR098208 | SR096031 | SR093403 | SR097902 | SR098208 | SR099015
Palmer - Boston Rd. | MA | 68131 | 58922.82 | 9208.18 | 15.63% | 81652 | -13521 | -16.56% | 1.Inverter-17 tripped offline at 16:26 on 05/15 due to high residual current.On 05/16 technician attempted to interface with inverter through several methods but was unsuccessful.On 05/20 technician with the SMA support had resolved the issue and inverter was back online at 17:30 on 05/20. | 1.SR101576
Shirley Bartkus | MA | 34798 | 92842.06 | -58044.06 | -62.52% | 135175 | -100377 | -74.26% | 1.Site was tripped offline at 12:30 and was back online at 16:45 on 05/04.Site was tripped offline at 10:30 on 05/07 after technician checked in stabilized C phase voltages site was auto recolsed and was back online at 05:15 on 05/08. 2.Site tripped offline at 11:30 on 05/10 and was back online at 20:45 on 05/10,Site tripped offline at 08:15 on 05/11 and was back online at 19:45 on 05/11,Site tripped offline at 09:00 on 05/12 and was back online at 22:30 on 05/12,Site tripped offline at 08:15 on 05/13 and was back online at 20:15 on 05/13,Site tripped offline at 10:00 on 05/14 and was back online at 23:00 on 05/14,Site tripped offline at 11:30 on 05/15 and was back online at 02:00 on 05/15,Site tripped offline at 05:45 on 05/17 and was back online at 23:00 on 05/17,Site tripped offline at 08:00 on 05/18 and was back online at 22:15 on 05/18,Site tripped offline at 09:45 on 05/19 and was back online at 17:15 on 05/19,Site tripped offline at 10:15 on 05/20 and was back online at 18:15 on 05/20,Site tripped offline at 12:45 on 05/23 and was back online at 18:30 on 05/23,Site tripped offline at 10:15 on 05/24 and was back online at 20:30 on 05/24,Site tripped offline at 08:15 on 05/25 and was back online at 20:30 on 05/25,Site tripped offline at 08:15 on 05/26 and was back online at 21:30 on 05/26,Site tripped offline at 08:30 on 05/27 and was back online at 22:45 on 05/27,Site tripped offline at 07:30 on 05/28 and was back online at 23:00 on 05/28,Site tripped offline at 07:45 on 05/29 and was back online at 00:45 on 05/30 after S3 Power replaced the recloser. | 1.SR100989 2.SR101269 | SR101269
Stoughton | MA | 99048 | 56128.29 | 42919.71 | 76.47% | 112975.9 | -13927.9 | -12.33% | 1. Inverter 7 tripped offline at 07:00 on 05/10 and reporting "bus differential high fault". and later self resolved and back online at 07:00 on 05/11. | 1. SR099721
Wellfleet Landfill | MA | 134879.04 | 140535.096 | -5656.056 | -4.025% | N/A |  |  | 1. The site tripped offline at 10:15 on 05/22. Additionally, all the inverters were reporting a 'Generic inverter fault.' Later, a technician checked in on 05/22 and power-cycled all the inverters. All the inverters were then back online by 14:15 on 05/22. 2. Inverter 6 is derating at 39 kW on 05/27 and reporting "Fan fault " later self resolved and back online on 05/28. | 1. SR101843 2. SR101988 | SR101988
Wilmington Garage & Building 7 | MA | 135928.75 | 138958.5 | -3029.75 | -2.18% | 179515.6 | -43586.85 | -24.28% | 1. Inverter 13 tripped offline at 09:30 on 05/05, reporting an arc protection fault. After a technician checked the site on 05/06 and inspected the string and cleared the arc fault, the inverter was brought back online at 10:30 on 05/06. 2. Inverter 12 had been offline since 12/18/2024. A technician checked the site on 05/06 and re-energized the inverter, bringing it back online at 10:30 on 05/06. However, it tripped offline again at 07:00 on 05/08. The inverter is currently under RMA. 3. Inverter 3 tripped offline at 13:40, reporting 'Relay fault - Fault0100.' After the technician checked the site on 06/02, it was found that the AC filter had failed. The inverter is currently under RMA. | 1. SR101014 2. SR094678, SR101014 3. SR101984 | SR094678 | SR101014 | SR101984
Woburn | MA | 200396 | 190361.5 | 10034.5 | 5.271% | 255073 | -54677 | -21.44%
Friendship Solar 1 | MD | 424170 | 449813.8 | -25643.8 | -5.701% | 573700.1 | -149530.1 | -26.06%
Friendship Solar 2 | MD | 407433 | 448067.2 | -40634.2 | -9.069% | 563512.2 | -156079.2 | -27.7% | 1. ATI Tracker 6X motor 3 is stuck at 39.21degrees on 04/02 at 15:15 and tracker3 setpoint is tracking with the peer trackers. Impacting production of the inverters 7,8,9 after the mid day. On 04/15 technicain worked on trackers but are still experiencing issue, requires further troubleshooting. | 1.SR099517
101 Carnegie Center | NJ | 0 | 0 | 0 |  | N/A |  |  | 1.Site was offline at 15:30 on 04/02 due to the switchgear has dried out, but is rusty. The site will remain offline pending repairs to prevent water intrusion. | 1.SR099808, SR102263 | SR102263
302 Carnegie Center | NJ | 76268.029 | 74823.408 | 1444.621 | 1.931% | N/A
510 Carnegie Center | NJ | 197541.614 | 214328.97 | -16787.356 | -7.833% | N/A
701 Carnegie Center | NJ | 152829.22 | 173131.719 | -20302.499 | -11.73% | N/A
Hudson County Correction | NJ | 199202.4631 | 200509.3 | -1306.8369 | -0.6518% | 246912.8 | -47710.3369 | -19.32% | 1. Inverter 3 and its left unit have been under RMA since 04/24 due to a thermal event, and the right unit has been offline since 04/24. The parts are under replacement. | 1.SR098681 , SR100367 | SR100367
ER Bison Solar | PA | 181513 | 0 | 181513 |  | 238828 | -57315 | -24% | 1. Inverter 11 tripped offline at 17:30 on 05/10 and reporting the fault "Bus Imbalance - Protect0070". A technician visited the site on 05/15 and found that the power head had a permanent fault and has been RMA'd. The technician returned to the site on 05/27, replaced the power head, and re-energized the inverter. The inverter was back online at 10:15 on 05/27. | 1. SR101270
Danville | IL | 370476.387 | N/A |  |  | N/A |  |  | 1. Inverter 14 has been underperforming by 4 kW compared to its peer inverters since 05/22 due to a string down. | 1. SR101887
Camden - Campbell Soup HQ | NJ | 311575 | 523613.4863 | -212038.4863 | -40.5% | 613173.27 | -301598.27 | -49.19% | 1. Meter MTRO1 has no communicatuion whole month due to an faulty meter. it's needed to be replaced and additional troubleshooting is required to restore communications. 2. On 01/27/25, during a PM event, the technician identified 8 faulty modules on the CTC roof that needed replacement. 3. On 01/15/25, during a PM event , the technician identified faulty positive DC terminal at Inverter 7-5. On 03/10 technician visited the site and Wirebox being RMA'd. Further troubleshoot needed. 4. Several inverters at BNB Camden aren't communicating with PowerFactors, with many duplicates. On 03/10, a technician found comms issues, rewired inverters into a daisy chain, and confirmed comms. Only inverter 02-02 required an RMA'd comm board. Remote access to the CTC roof cell modem was confirmed with Zoë from Greenbacker. A return visit is needed once the RMA'd comm board arrives. 5. Pad 9 Inverter 1 tripped offline on 05/02. It was later remotely reset and brought back online the same day. 6. The site was taken offline from 07:50 to 02:15 on 05/03 due to a technician performing work on the inverters and meter. | 1. SR094890, SR093773, 2. SR095761, PM11788, SR096555 3. SR096557, SR096558, PM11794 4. SR097964 5. SR100899 6. SR094890, SR100899, SR098933 | SR093773 | SR095761 | SR096555 | SR096557 | SR096558 | SR097964 | SR100899 | SR094890 | SR100899 | SR098933
Westport - Pine Hill | MA | 598098 | N/A |  |  | 675183.16 | -77085.16 | -11.42% | 1. Inverters 14–26 tripped offline at 07:00 on 05/22, possibly due to a breaker trip. A technician checked the site on 05/23, and after adjusting the ISO parameters, the inverters were back online at 06:00 on 05/23. | 1. SR101856
Oaks Landfill - ANEM | MD | 330959.217 | 363582.9994 | -32623.7824 | -8.973% | N/A |  |  | 1. Inverters CO1, CO6, CO7, CO11, CO12 tripped offline at 17:30 on 05/16 later self resolved and back online at 07:00 on 05/17. | 1. SR101611
Oaks Landfill - CS2 | MD | 337324.638 | 367081.712 | -29757.074 | -8.106% | N/A |  |  | 1. Inverter B08 experienced multiple tripping events and reported a "Critical Internal Hardware Failure" starting on 05/03. The issue later self-resolved, and the inverter returned to normal operation on 05/05. Additionally, Inverter B08 again experienced multiple tripping events, reporting "Critical Internal Hardware Failure (8002h)" starting on 05/08. On 05/22, Solectria technicians reset the inverter and adjusted its settings. The inverter returned to normal operation later that day. 2. Inverters BO1, BO2, BO5, BO6 and BO7 to BO12 tripped offline at 17:30 on 05/16 and later self resolved at 07:00 on 05/16. | 1. SR100965, SR101170 2. SR101613 | SR101170 | SR101613
Oaks Landfill - CS1 | MD | 340690.47 | 367079.142 | -26388.672 | -7.189% | N/A |  |  | 1. Inverters AO1, AO2, AO3, AO7, AO8 tripped offline at 17:30 on 05/16 later self resolved and back online at 07:00 on 05/17. | 1. SR101612
Plympton - Upland Solar - PV & BESS (IRA) | MA | 675539 | 684501.084 | -8962.084 | -1.309% | 733816.5 | -58277.5 | -7.942% | 1.Inverter 12 was offline from 12:09 on 05/26. On 05/27, the technician contacted CPS support and CPS team confirmed the issue and advised swapping the unit with another inverter to determine if the problem was related to the powerhead. They also indicated that further troubleshooting would be required. Inverter 12 has been under the RMA process since 05/30. 2.Site had multiple trippings on 05/23 | 1.SR101952

## Jun
Greenbacker Capital |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 7151459.6589 | 6725438.1724 | 426021.4865 | 6.334% | 6218386.15 | 933073.5089 | 15.01%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA | 18400 | 17913.74 | 486.26 | 2.714% | 20616.23 | -2216.23 | -10.75% | 1. Inverter 1 tripped offline at 14:30 from 06/24 and reporting "Grid Relay Error - Protect0020. Inverter is being RMA'd. | 1.SR103463
15 Walpole Park South | MA | 68928 | 65669.01 | 3258.99 | 4.963% | 72904.19 | -3976.19 | -5.454%
19 Walpole Park South | MA | 43383.25 | 40137.63 | 3245.62 | 8.086% | 46403.23 | -3019.98 | -6.508%
23 Walpole Park South | MA | 54242.25 | 53408.95 | 833.3 | 1.56% | 61140.12 | -6897.87 | -11.28% | 1.Inverter 2 was being RMA'd and offline since 01/04 | 1.SR095312
24 Walpole Park South | MA | 88969.8425 | 76860.19 | 12109.6525 | 15.76% | 93947.49 | -4977.6475 | -5.298%
25 Walpole Park South | MA | 81562.5 | 81180.88 | 381.62 | 0.4701% | 95151.08 | -13588.58 | -14.28% | 1.Inverter 13 was RMA'd since 08/20/24 due to thermal event in powerhead of the inverter. | 1.SR089170,SR095220 | SR095220
3 Walpole Park South | MA | 106786.5 | 104346 | 2440.5 | 2.339% | 114922.9 | -8136.4 | -7.08% | 1.Inverter 9 was offline from 11/02/24 due to Protect 0010 fault and is being RMA'd . | 1.SR093404,SR089564 | SR089564
4 Walpole Park South | MA | 60227 | 56103.45 | 4123.55 | 7.35% | 62625.19 | -2398.19 | -3.829%
Brockton | MA | 99513 | 86975.77 | 12537.23 | 14.41% | 105560 | -6047 | -5.728% | 1. Inverter 13 was underperforming by 4kW since 06/11. Will investigate during next PM. 2. Inverter 10 tripped offline at 8:00AM on 06/26. Scheduled dispatch on 07/01 | 1. SR103002 2. SR103598 | SR103598
Canton | MA | 94800 | 86873.94 | 7926.06 | 9.124% | 100923.9 | -6123.9 | -6.068%
Chelsea | MA | 163439 | 157297.9 | 6141.1 | 3.904% | 167426.6 | -3987.6 | -2.382% | 1. Inverter B3 loosing communication intermittently and being RMA'd since 12/19. 2. Inverters A1 to A4 stopped communicating at 12:30 on 06/24, production cannot be verified. Inverters back online at 11:45 on 06/26. | 1. SR093500 2. SR103483 | SR103483
Hamilton Landfill | MA | 130165.96 | 136601.24 | -6435.28 | -4.711% | N/A
Holliston | MA | 226544 | 287247.9 | -60703.9 | -21.13% | 281631.8 | -55087.8 | -19.56% | 1. Inverter 8 right unit being RMA'd since 05/23 2. Inverter 10 middleunit fan was replaced on 06/25 and inverter started producing at its capacity. 3. Inverter 1 right unit was replaced and re-energized on 06/25 and inverter started producing at its capacity. 04. Inverter 9 right unit has been tripping on and off since 05/27 and is currently being RMA'd. 5. Inverter 6 right unit tripped offline at 14:15 on 06/2. Will troubleshoot in combined dispatches. 6. Inverter 11 middle unit tripped offline at 15:00 on 06/05. Unit lock was removed and is cycling on and off. Pending next steps from SE. 7. Inverter 9 middle unit tripped offline at 13:00 on 6/20 and back online on 06/30. | 1. SR101656 2. SR101858 3. SR101976 4. SR101977 5. SR102370 6. SR102560 7. SR103297 | SR101858 | SR101976 | SR101977 | SR102370 | SR102560 | SR103297
Natick HS - Carports | MA | 83630.029 | 97231.438 | -13601.409 | -13.99% | N/A
Norton | MA | 36513.4999 | 291741.2 | -255227.7001 | -87.48% | 599800.2 | -563286.7001 | -93.91% | 1. The site has been offline since 04/01/24. On 06/11, 06/12, and 06/13, technicians worked on the re-energization process, and on 06/16, the site was partially re-energized. 2. Inverter 2 was offline on 06/12 with F63 fault. On 06/20 PE technician disconneced the inverter 2 and combiner boxes related to it. Further troubleshoot required. | 1. SR098208 2. SR103072, SR102884 | SR103072 | SR102884
Palmer - Boston Rd. | MA | 79858.5 | 65606.45 | 14252.05 | 21.72% | 84844 | -4985.5 | -5.876% | 1.Multiple inverters had experienced tripping events on 06/13 due to technician was onsite for preventive maintenance. | 1.PM11337
Shirley Bartkus | MA | 127539 | 104461.5 | 23077.5 | 22.09% | 145881 | -18342 | -12.57% | 1. Inverters 35-40 tripped offline at 12:30 on 06/25 and back online on 06/26. 2. Inverters 35-40 tripped offline at 11:00 on 06/27. Need to replace a trip unit on breaker. | 1. SR103539 2. SR103727 | SR103727
Stoughton | MA | 110018 | 72767.74 | 37250.26 | 51.19% | 111961.8 | -1943.8 | -1.736% | 1.Inverter 7 has been offline since 06/01 and is being RMA'd. It will remain offline throughout the month | 1.SR102989
Wellfleet Landfill | MA | 140687.793 | 154673.19 | -13985.397 | -9.042% | N/A
Wilmington Garage & Building 7 | MA | 149306.125 | 161361.1 | -12054.975 | -7.471% | 176620.5 | -27314.375 | -15.47% | 1. Inverter 3 was offline since 05/27, on 06/04 inverter was RMA'd. 2. Inverter 1 tripped offline at 6:30 on 06/03 and back online at 8:45 on 06/04. | 1. SR101984, SR102369 2. SR102365 | SR102369 | SR102365
Woburn | MA | 233898.3644 | 219532.5 | 14365.8644 | 6.544% | 248509.7 | -14611.3356 | -5.88%
Friendship Solar 1 | MD | 482191 | 472697.1 | 9493.9 | 2.008% | 575811.7 | -93620.7 | -16.26% | 1. Site production was low on 06/08, 06/16 and 06/27 due to rain.
Friendship Solar 2 | MD | 461893 | 489968.4 | -28075.4 | -5.73% | 571049.5 | -109156.5 | -19.12% | 1. On 04/02 at 15:15, ATI Tracker 6X motor 3 became stuck at 39.21 degrees. Tracker 3’s setpoint is still tracking with the peer trackers, but the mechanical issue is impacting the production of inverters 7, 8, and 9, particularly after midday. We will investigate further during the next onsite visit. | 1. SR099517
101 Carnegie Center | NJ | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was offline since 04/02 and will remains offline until further repair to be completed. | 1. SR103030, SR102263 | SR102263
302 Carnegie Center | NJ | 84258.117 | 79858.786 | 4399.331 | 5.509% | N/A
510 Carnegie Center | NJ | 214712.439 | 238390.919 | -23678.48 | -9.933% | N/A
701 Carnegie Center | NJ | 164770.632 | 189887.218 | -25116.586 | -13.23% | N/A |  |  | 1. Inverter 18 communication was stopped at 7:00 on 06/09 and restored on 06/10. | 1. SR102734
Hudson County Correction | NJ | 212262.3071 | 205394.4 | 6867.9071 | 3.344% | 247311.5 | -35049.1929 | -14.17% | 1. Inverter 3 and its left unit have been under RMA since 04/24 due to a thermal event, and the right unit has been offline since 04/24. The parts are under replacement. 2. Inverter 18 was derating on high irradiance days since 04/25. Waiting to hear back from solectria. 3. Inverter 19 tripped offline at 7:45 on 06/25 and back online on 06/30. | 1. SR100367 2. SR100422 3. SR103520 | SR100422 | SR103520
ER Bison Solar | PA | 212581 | 200043.6 | 12537.4 | 6.267% | 250270 | -37689 | -15.06% | 1. Inverter 9 was derating at 75.20kW from 12:00 on 06/24. Waiting response from GB for approval to dispatch. | 1. SR103402
Danville | IL | 369453.579 | N/A |  |  | N/A |  |  | 1. Inverter 2 dropped a string on 06/02 and on 06/04 fuses were replaced. 2. Inverter 11 dropped a string on 06/21 and on 06/25 fuses were replaced. | 1. SR102373 2. SR103289 | SR103289
Camden - Campbell Soup HQ | NJ | 344125 | 544716.3194 | -200591.3194 | -36.82% | 559434.52 | -215309.52 | -38.49% | 1. Several inverters at BNB Camden aren’t communicating with PowerFactors, with many duplicates. On 03/10, a tech rewired them in a daisy chain and restored comms; only inverter 02-02 needs an RMA’d comm board. Remote access to the CTC roof modem was confirmed with Zoë from Greenbacker. Parts have arrived and need dispatching. | 1. SR097964
Westport - Pine Hill | MA | 606202 | N/A |  |  | 691456 | -85254 | -12.33% | 1. All inverters had experienced tripping events on 06/04, 06/05 due to technician was onsite for preventive maintenance. | 1. PM12227
Oaks Landfill - ANEM | MD | 366070.345 | 400449.393 | -34379.048 | -8.585% | N/A |  |  | 1. Inverter C02 didn't started for production due to open phase fault on 06/15 and back online on 06/16. | 1. SR102988
Oaks Landfill - CS2 | MD | 382635.574 | 403800.155 | -21164.581 | -5.241% | N/A
Oaks Landfill - CS1 | MD | 378098.052 | 403798.029 | -25699.977 | -6.365% | N/A
Plympton - Upland Solar - PV & BESS (IRA) | MA | 673794 | 678442.135 | -4648.135 | -0.6851% | 732183 | -58389 | -7.975% | 1. Inverter 31 was derating 75.10kW from 12:30 on 06/24 due to Fan error. The fan has been RMA'd on 06/25. 2. Inverter 26 was derating 74kW from 13:15 on 06/12 due to Fan error. The fan has been RMA'd on 06/16. | 1. SR103415 2. SR102968 | SR102968

## Jul
Greenbacker Capital | [5 empty] | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA
15 Walpole Park South | MA
19 Walpole Park South | MA
23 Walpole Park South | MA
24 Walpole Park South | MA
25 Walpole Park South | MA
3 Walpole Park South | MA
4 Walpole Park South | MA
Brockton | MA
Canton | MA
Chelsea | MA
Hamilton Landfill | MA
Holliston | MA
Natick HS - Carports | MA
Norton | MA
Palmer - Boston Rd. | MA
Shirley Bartkus | MA
Stoughton | MA
Wellfleet Landfill | MA
Wilmington Garage & Building 7 | MA
Woburn | MA
Friendship Solar 1 | MD
Friendship Solar 2 | MD
101 Carnegie Center | NJ
302 Carnegie Center | NJ
510 Carnegie Center | NJ
701 Carnegie Center | NJ
Hudson County Correction | NJ
ER Bison Solar | PA
Danville | IL
Camden - Campbell Soup HQ | NJ
Westport - Pine Hill | MA
Oaks Landfill - ANEM | MD
Oaks Landfill - CS2 | MD
Oaks Landfill - CS1 | MD
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Aug
Greenbacker Capital |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA
15 Walpole Park South | MA
19 Walpole Park South | MA
23 Walpole Park South | MA
24 Walpole Park South | MA
25 Walpole Park South | MA
3 Walpole Park South | MA
4 Walpole Park South | MA
Brockton | MA
Canton | MA
Chelsea | MA
Hamilton Landfill | MA
Holliston | MA
Natick HS - Carports | MA
Norton | MA
Palmer - Boston Rd. | MA
Shirley Bartkus | MA
Stoughton | MA
Wellfleet Landfill | MA
Wilmington Garage & Building 7 | MA
Woburn | MA
Friendship Solar 1 | MD
Friendship Solar 2 | MD
101 Carnegie Center | NJ
302 Carnegie Center | NJ
510 Carnegie Center | NJ
701 Carnegie Center | NJ
Hudson County Correction | NJ
ER Bison Solar | PA
Danville | IL
Camden - Campbell Soup HQ | NJ
Westport - Pine Hill | MA
Oaks Landfill - ANEM | MD
Oaks Landfill - CS2 | MD
Oaks Landfill - CS1 | MD
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Sep
Greenbacker Capital |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA
15 Walpole Park South | MA
19 Walpole Park South | MA
23 Walpole Park South | MA
24 Walpole Park South | MA
25 Walpole Park South | MA
3 Walpole Park South | MA
4 Walpole Park South | MA
Brockton | MA
Canton | MA
Chelsea | MA
Hamilton Landfill | MA
Holliston | MA
Natick HS - Carports | MA
Norton | MA
Palmer - Boston Rd. | MA
Shirley Bartkus | MA
Stoughton | MA
Wellfleet Landfill | MA
Wilmington Garage & Building 7 | MA
Woburn | MA
Friendship Solar 1 | MD
Friendship Solar 2 | MD
101 Carnegie Center | NJ
302 Carnegie Center | NJ
510 Carnegie Center | NJ
701 Carnegie Center | NJ
Hudson County Correction | NJ
ER Bison Solar | PA
Danville | IL
Camden - Campbell Soup HQ | NJ
Westport - Pine Hill | MA
Oaks Landfill - ANEM | MD
Oaks Landfill - CS2 | MD
Oaks Landfill - CS1 | MD
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Oct
Greenbacker Capital |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA
15 Walpole Park South | MA
19 Walpole Park South | MA
23 Walpole Park South | MA
24 Walpole Park South | MA
25 Walpole Park South | MA
3 Walpole Park South | MA
4 Walpole Park South | MA
Brockton | MA
Canton | MA
Chelsea | MA
Hamilton Landfill | MA
Holliston | MA
Natick HS - Carports | MA
Norton | MA
Palmer - Boston Rd. | MA
Shirley Bartkus | MA
Stoughton | MA
Wellfleet Landfill | MA
Wilmington Garage & Building 7 | MA
Woburn | MA
Friendship Solar 1 | MD
Friendship Solar 2 | MD
101 Carnegie Center | NJ
302 Carnegie Center | NJ
510 Carnegie Center | NJ
701 Carnegie Center | NJ
Hudson County Correction | NJ
ER Bison Solar | PA
Danville | IL
Camden - Campbell Soup HQ | NJ
Westport - Pine Hill | MA
Oaks Landfill - ANEM | MD
Oaks Landfill - CS2 | MD
Oaks Landfill - CS1 | MD
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Nov
Greenbacker Capital |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA
15 Walpole Park South | MA
19 Walpole Park South | MA
23 Walpole Park South | MA
24 Walpole Park South | MA
25 Walpole Park South | MA
3 Walpole Park South | MA
4 Walpole Park South | MA
Brockton | MA
Canton | MA
Chelsea | MA
Hamilton Landfill | MA
Holliston | MA
Natick HS - Carports | MA
Norton | MA
Palmer - Boston Rd. | MA
Shirley Bartkus | MA
Stoughton | MA
Wellfleet Landfill | MA
Wilmington Garage & Building 7 | MA
Woburn | MA
Friendship Solar 1 | MD
Friendship Solar 2 | MD
101 Carnegie Center | NJ
302 Carnegie Center | NJ
510 Carnegie Center | NJ
701 Carnegie Center | NJ
Hudson County Correction | NJ
ER Bison Solar | PA
Danville | IL
Camden - Campbell Soup HQ | NJ
Westport - Pine Hill | MA
Oaks Landfill - ANEM | MD
Oaks Landfill - CS2 | MD
Oaks Landfill - CS1 | MD
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Dec
Greenbacker Capital |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
10 Walpole Park South | MA
15 Walpole Park South | MA
19 Walpole Park South | MA
23 Walpole Park South | MA
24 Walpole Park South | MA
25 Walpole Park South | MA
3 Walpole Park South | MA
4 Walpole Park South | MA
Brockton | MA
Canton | MA
Chelsea | MA
Hamilton Landfill | MA
Holliston | MA
Natick HS - Carports | MA
Norton | MA
Palmer - Boston Rd. | MA
Shirley Bartkus | MA
Stoughton | MA
Wellfleet Landfill | MA
Wilmington Garage & Building 7 | MA
Woburn | MA
Friendship Solar 1 | MD
Friendship Solar 2 | MD
101 Carnegie Center | NJ
302 Carnegie Center | NJ
510 Carnegie Center | NJ
701 Carnegie Center | NJ
Hudson County Correction | NJ
ER Bison Solar | PA
Danville | IL
Camden - Campbell Soup HQ | NJ
Westport - Pine Hill | MA
Oaks Landfill - ANEM | MD
Oaks Landfill - CS2 | MD
Oaks Landfill - CS1 | MD
Plympton - Upland Solar - PV & BESS (IRA) | MA

## Sites
Portfolio: | Greenbacker Capital
Site DAS Name | Site | State | Update | DAS
10 Walpole Park South [0664] | 10 Walpole Park South | MA | AEF | PowerTrack
15 Walpole Park South [0668] | 15 Walpole Park South | MA | AEF | PowerTrack
19 Walpole Park South [0670] | 19 Walpole Park South | MA | AEF | PowerTrack
23 Walpole Park South [0676] | 23 Walpole Park South | MA | AEF | PowerTrack
24 Walpole Park South [0667] | 24 Walpole Park South | MA | AEF | PowerTrack
25 Walpole Park South [0665] | 25 Walpole Park South | MA | AEF | PowerTrack
3 Walpole Park South [0666] | 3 Walpole Park South | MA | AEF | PowerTrack
4 Walpole Park South [0669] | 4 Walpole Park South | MA | AEF | PowerTrack
Brockton [0662] | Brockton | MA | AEF | PowerTrack
Canton [0672] | Canton | MA | AEF | PowerTrack
Chelsea [0663] | Chelsea | MA | AEF | PowerTrack
Hamilton MA Landfill | Hamilton Landfill | MA |  | InAccess
Holliston [0674] | Holliston | MA | AEF | PowerTrack
MA: Natick HS - Carports | Natick HS - Carports | MA |  | InAccess
Norton [0671] | Norton | MA | AEF | PowerTrack
Palmer - Boston Rd. [0637] | Palmer - Boston Rd. | MA | AEF | PowerTrack
Shirley Bartkus [0632] | Shirley Bartkus | MA | AE | PowerTrack
Stoughton [0661] | Stoughton | MA | AEF | PowerTrack
MA: Wellfleet Landfill | Wellfleet Landfill | MA |  | InAccess
Wilmington Garage & Building 7 [0675] | Wilmington Garage & Building 7 | MA | AEF | PowerTrack
Woburn [0673] | Woburn | MA | AEF | PowerTrack
Friendship Solar 1 [0569] | Friendship Solar 1 | MD | AEF | PowerTrack
Friendship Solar 2 [0570] | Friendship Solar 2 | MD | AEF | PowerTrack
101 Carnegie Center | 101 Carnegie Center | NJ |  | InAccess
302 Carnegie Center | 302 Carnegie Center | NJ |  | InAccess
510 Carnegie Center | 510 Carnegie Center | NJ |  | InAccess
701 Carnegie Center | 701 Carnegie Center | NJ |  | InAccess
Hudson County Correction [0470] | Hudson County Correction | NJ | AEF | PowerTrack
ER Bison Solar [0371] | ER Bison Solar | PA | AEF | PowerTrack
Danville | Danville | IL |  | InAccess
Camden - Campbell Soup HQ | Camden - Campbell Soup HQ | NJ |  | PowerFactor
Pine Hill [0702] | Westport - Pine Hill | MA | AF | PowerTrack
Gaithersburg - Oaks C ANEM | Oaks Landfill - ANEM | MD |  | InAccess
Gaithersburg - Oaks A CS1 | Oaks Landfill - CS2 | MD |  | InAccess
Gaithersburg - Oaks B CS2 | Oaks Landfill - CS1 | MD |  | InAccess
Plympton - Upland Solar - PV & BESS (IRA) | Plympton - Upland Solar - PV & BESS (IRA) | MA |  | Acelerex