## Year to Date
Luminace |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 10030261.5047 | 10663128.5192 | -632867.0145 | -5.935% | 20609383.27 | -10579121.7653 | -51.33%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 284237.8504 | 181763.78 | 102474.0704 | 56.38% | 187096.3 | -18750.7 | -10.02%
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 32042.4562 | -32042.4562 | -100% | 3597486.88 | -3597486.88 | -100%
Berkeley - NJ-22-C894 Berkeley II | NJ | 1377151.3791 | 1059585.6 | 317565.7791 | 29.97% | 3598341 | -2221189.6209 | -61.73%
BEMS Landfill East | NJ | 2909 | 1288954.451 | -1286045.451 | -99.77% | 3616910.09 | -3614001.09 | -99.92%
Southampton - BEMS West NJ-22-C898 | NJ | 2846384 | 3223393.7 | -377009.7 | -11.7% | 3445536 | -599152 | -17.39%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 42321.8117 | 0 | 42321.8117 |  | 0 | 0
Lakewood Township - Public Works | NJ | 728615.0885 | 0 | 728615.0885 |  | 1205948 | -477332.9115 | -39.58%
Canby - Dover - OR-23-C003 | OR | 1059524.378 | 1010842.3 | 48682.078 | 4.816% | 1019387 | 40137.378 | 3.937%
Estacada - Clayfield - OR-23-C001 | OR | 1217604.408 | 1107693.5 | 109910.908 | 9.923% | 1101450 | 116154.408 | 10.55%
Willamina - Waterford - OR-23-C006 | OR | 449018.424 | 862021.177 | -413002.753 | -47.91% | 938139 | -489120.576 | -52.14%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 1425196.633 | 1339749.9 | 85446.733 | 6.378% | 1362976 | 62220.633 | 4.565%
OR-23-C002 SPI - Cork Solar | OR | 597298.532 | 557081.655 | 40216.877 | 7.219% | 536113 | 61185.532 | 11.41%

## 1st Qtr
Luminace |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1526713.3764 | 1623475.4862 | -96762.1098 | -5.96% | 5982362.51 | -4455649.1336 | -74.48%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 115892.2504 | 0 | 115892.2504 |  | 0 | 0
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 32042.4562 | -32042.4562 | -100% | 1495580.21 | -1495580.21 | -100%
Berkeley - NJ-22-C894 Berkeley II | NJ | 109808.1055 | 271422.9 | -161614.7945 | -59.54% | 1480295 | -1370486.8945 | -92.58%
BEMS Landfill East | NJ | 0 | 13254.93 | -13254.93 | -100% | 1554068.3 | -1554068.3 | -100%
Southampton - BEMS West NJ-22-C898 | NJ | 1043156 | 1306755.2 | -263599.2 | -20.17% | 1352961 | -309805 | -22.9%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 13246.3581 | 0 | 13246.3581 |  | 0 | 0
Lakewood Township - Public Works | NJ | 244610.6624 | 0 | 244610.6624 |  | 99458 | 145152.6624 | 145.9%
Canby - Dover - OR-23-C003 | OR | 0 | 0 | 0 |  | 0 | 0
Estacada - Clayfield - OR-23-C001 | OR | 0 | 0 | 0 |  | 0 | 0
Willamina - Waterford - OR-23-C006 | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C005 Solops SPI - Belvedere Solar | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C002 SPI - Cork Solar | OR | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Luminace |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 8503548.1283 | 9039653.033 | -536104.9047 | -5.931% | 14627020.76 | -6123472.6317 | -41.86%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 168345.6 | 181763.78 | -13418.18 | -7.382% | 187096.3 | -18750.7 | -10.02%
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 2101906.67 | -2101906.67 | -100%
Berkeley - NJ-22-C894 Berkeley II | NJ | 1267343.2736 | 788162.7 | 479180.5736 | 60.8% | 2118046 | -850702.7264 | -40.16%
BEMS Landfill East | NJ | 2909 | 1275699.521 | -1272790.521 | -99.77% | 2062841.79 | -2059932.79 | -99.86%
Southampton - BEMS West NJ-22-C898 | NJ | 1803228 | 1916638.5 | -113410.5 | -5.917% | 2092575 | -289347 | -13.83%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 29075.4536 | 0 | 29075.4536 |  | 0 | 0
Lakewood Township - Public Works | NJ | 484004.4261 | 0 | 484004.4261 |  | 1106490 | -622485.5739 | -56.26%
Canby - Dover - OR-23-C003 | OR | 1059524.378 | 1010842.3 | 48682.078 | 4.816% | 1019387 | 40137.378 | 3.937%
Estacada - Clayfield - OR-23-C001 | OR | 1217604.408 | 1107693.5 | 109910.908 | 9.923% | 1101450 | 116154.408 | 10.55%
Willamina - Waterford - OR-23-C006 | OR | 449018.424 | 862021.177 | -413002.753 | -47.91% | 938139 | -489120.576 | -52.14%
OR-23-C005 Solops SPI - Belvedere Solar | OR | 1425196.633 | 1339749.9 | 85446.733 | 6.378% | 1362976 | 62220.633 | 4.565%
OR-23-C002 SPI - Cork Solar | OR | 597298.532 | 557081.655 | 40216.877 | 7.219% | 536113 | 61185.532 | 11.41%

## 3rd Qtr
Luminace |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 0 | 0 | 0 |  | 0 | 0
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 0 | 0
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | 0 | 0 |  | 0 | 0
BEMS Landfill East | NJ | 0 | 0 | 0 |  | 0 | 0
Southampton - BEMS West NJ-22-C898 | NJ | 0 | 0 | 0 |  | 0 | 0
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 0 | 0 | 0 |  | 0 | 0
Lakewood Township - Public Works | NJ | 0 | 0 | 0 |  | 0 | 0
Canby - Dover - OR-23-C003 | OR | 0 | 0 | 0 |  | 0 | 0
Estacada - Clayfield - OR-23-C001 | OR | 0 | 0 | 0 |  | 0 | 0
Willamina - Waterford - OR-23-C006 | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C005 Solops SPI - Belvedere Solar | OR | 0 | 0 | 0 |  | 0 | 0
OR-23-C002 SPI - Cork Solar | OR | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Luminace |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Raymond Ed Re-Development - DC-23-0001 | DC | 0 | 0 | 0 |  | 0 | 0
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 0 | 0
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | 0 | 0 |  | 0 | 0
BEMS Landfill East | NJ | 0 | 0 | 0 |  | 0 | 0
Southampton - BEMS West NJ-22-C898 | NJ | 0 | 0 | 0 |  | 0 | 0
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ |  | 0 |  |  | 0 | 0
Lakewood Township - Public Works | NJ |  | 0 |  |  | 0 | 0
Canby - Dover - OR-23-C003 | OR |  | 0 |  |  | 0 | 0
Estacada - Clayfield - OR-23-C001 | OR |  | 0 |  |  | 0 | 0
Willamina - Waterford - OR-23-C006 | OR |  | 0 |  |  | 0 | 0
OR-23-C005 Solops SPI - Belvedere Solar | OR |  | 0 |  |  | 0 | 0
OR-23-C002 SPI - Cork Solar | OR |  | 0 |  |  | 0 | 0

## Jan
Luminace |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 391768.8975 | 660242.88 | -268473.9825 | -40.66% | 1616542 | -1224773.1025 | -75.77% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 14808.792 | N/A |  |  | N/A |  |  | 1. CSS resolved the DAS issues on 01/03, and M0 started reporting the production on 01/03. However, M1 is reporting negative values. As per the drawings, the site capacity is 365 kW, but meter M0 is reporting 295 kW, and M1 is reporting -295 kW. We have consider M0 production as total site production. Reached out to AE #557940 | 1.SR094989, SR096863 | SR096863
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 31205.78 | -31205.78 | -100% | 412354 | -412354 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1. SR093414
Berkeley - NJ-22-C894 Berkeley II | NJ | 109808.1055 | 271422.9 | -161614.7945 | -59.54% | 406892 | -297083.8945 | -73.01% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1. SR093414
BEMS Landfill East | NJ | 0 | 0 | 0 |  | 435058 | -435058 | -100% | 1.Utility company has shut down site since 06/11/24. | 1.SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 267152 | 357614.2 | -90462.2 | -25.3% | 362238 | -95086 | -26.25% | 1.Site tripped offline at 2:30AM on 01/21 due to Phase A voltage missing Fault and back online at 10AM on 01/30. | 1.SR095756
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter M1 is reporting negative values from 01/03 we have consider M0 production as total site production.

## Feb
Luminace |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 431689.124 | 397154.4762 | 34534.6478 | 8.696% | 1851765.4 | -1420076.276 | -76.69% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 27512.157 | N/A |  |  | N/A |  |  | 1.M1 meter is reporting negative values from 01/03 and through out the Month. AE says likely an onsite issue and to swap CT lead polarity. 2.Site stopped communicating from 02/26 due to some DAS equipment was RMA'd. CSS is about to do capacity test at site after DAS issues resolved. 3. Expected and forecasted data are unavailable. | 1.SR096863 2.SR094989, SR097768 | SR094989 | SR097768
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 836.6762 | -836.6762 | -100% | 461858.4 | -461858.4 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1.SR093413
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | N/A |  |  | 456469 | -456469 | -100% | 1. Site is dealing with utility-related issue throughout the month, and the EPC team is currently addressing the issue. | 1.SR093414
BEMS Landfill East | NJ | 0 | N/A |  |  | 498875 | -498875 | -100% | 1.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 306069 | 396317.8 | -90248.8 | -22.77% | 403220 | -97151 | -24.09% | 1. Site was tripped offline at 12:15AM on 02/22 due to Phase A voltage missing fault and back online at 11:45AM on 02/28. | 1.SR097638
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 4807.5 | N/A |  |  | N/A |  |  | 1. Expected and forecasted data are unavailable.
Lakewood Township - Public Works | NJ | 93300.467 | N/A |  |  | 31343 | 61957.467 | 197.7% | 1. Forecasted data was very low and expected data are unavailable.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since meter M1 is reporting negative values from 01/03 we have consider M0 production as total site production.

## Mar
Luminace |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 703255.355 | 566078.13 | 137177.225 | 24.23% | 2514055.11 | -1810799.755 | -72.03% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 73571.3014 | N/A |  |  | N/A |  |  | 1.Site communications are back at 11:45AM on 03/25 after RMA installation. 2. We don't have expected and forecasted energy values for this site. | 1.SR094989,SR097768 | SR097768
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | N/A |  |  | 621367.81 | -621367.81 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098409,SR093413 | SR093413
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | N/A |  |  | 616934 | -616934 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098411,SR093414 | SR093414
BEMS Landfill East | NJ | 0 | 13254.93 | -13254.93 | -100% | 620135.3 | -620135.3 | -100% | 1.The site communication was back at 10:15AM and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 469935 | 552823.2 | -82888.2 | -14.99% | 587503 | -117568 | -20.01% | 1.Site tripped offline 18:15 on 03/05 and back online at 12:45 on 03/14. | 1.SR097638
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 8438.8581 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 151310.1954 | N/A |  |  | 68115 | 83195.1954 | 122.1% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## Apr
Luminace |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 854032.0153 | 717297.95 | 136734.0653 | 19.06% | 2800077.99 | -1946045.9747 | -69.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 54203.1 | 57596.35 | -3393.25 | -5.891% | 56794.59 | -2591.49 | -4.563%
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 676075 | -676075 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1. SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 0 | 0 | 0 |  | 676850 | -676850 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1. SR098411
BEMS Landfill East | NJ | 0 | 12059.7 | -12059.7 | -100% | 651557.4 | -651557.4 | -100% | 1.The site communication was back at 10:15AM and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 635861 | 647641.9 | -11780.9 | -1.819% | 658293 | -22432 | -3.408%
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 9269.4465 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 154698.4688 | N/A |  |  | 80508 | 74190.4688 | 92.15% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## May
Luminace |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 3877714.643 | 3723083.84 | 154630.803 | 4.153% | 5379743.8 | -1502029.157 | -27.92%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 54648.5 | 59815.54 | -5167.04 | -8.638% | 63486.3 | -8837.8 | -13.92% | 1. Low production due to rain
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 710210 | -710210 | -100% | 1.The site is dealing with utility-related issues due to damaged CTs and PTs in their metering bank, as has been the case throughout the month. The EPC team is currently addressing the issue. | 1.SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 701245.2736 | 191085.9 | 510159.3736 | 267% | 710606 | -9360.7264 | -1.317% | 1.The site was dealing with utility-related issues due to damaged CTs and PTs in their metering bank.Site was back online at 16:00EDT on 05/20. | 1.SR098411
BEMS Landfill East | NJ | 0 | 586005 | -586005 | -100% | 695675.5 | -695675.5 | -100% | 1.The site communication was back at 10:15 and again stopped communication on 03/04 at 15:00 due to an issue with the MV breaker on the skid. The team is currently working with SMA to resolve the issue and is testing the IKI relay. Additionally, a single-phase witness test under load with the utility is pending prior to re-energization. 2.Utility company has shut down site since 06/11/24 due to the solar causing an issue with the grid. | 1.SR098408 2.SR086098 | SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 628239 | 645088.6 | -16849.6 | -2.612% | 704768 | -76529 | -10.86% | 1. Low production due to rain
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 9749.9441 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 157465.6563 | N/A |  |  | 92403 | 65062.6563 | 70.41% | 1. The forecasted values have been updated by AE, but they appear to be low.
Canby - Dover - OR-23-C003 | OR | 499021.269 | 471441.3 | 27579.969 | 5.85% | 494897 | 4124.269 | 0.8334% | 1. Multiple trackers had been stuck since 04/03 and started tracking again on 05/22. 2. Inverters 7, 8, and 16 are experiencing morning shading, with inverter 8 in particular not reaching its full production until 09:45. | 1. SR101115 2. SR101155 | SR101155
Estacada - Clayfield - OR-23-C001 | OR | 554193.004 | 515253.5 | 38939.504 | 7.557% | 532245 | 21948.004 | 4.124% | 1. Multiple trackers had been stuck since 05/07 and started tracking again on 05/22. 2. The site tripped offline at 14:00 on 05/12 and came back online at 09:00 on 05/13. | 1. SR101126 2. SR101287 | SR101287
Willamina - Waterford - OR-23-C006 | OR | 345311.5 | 387541.9 | -42230.4 | -10.9% | 464151 | -118839.5 | -25.6% | 1. All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. 2. The site tripped offline at 10:00 on 05/23 and came back online at 11:15 on 05/29. | 1. SR101124 2. SR101894 | SR101894
OR-23-C005 Solops SPI - Belvedere Solar | OR | 641330.014 | 599695.6 | 41634.414 | 6.943% | 653170 | -11839.986 | -1.813% | 1. Site tripped offline at 16:07 on 05/15 and came back online at 08:30 on 05/20. | 1. SR101566
OR-23-C002 SPI - Cork Solar | OR | 286510.482 | 267156.5 | 19353.982 | 7.244% | 258132 | 28378.482 | 10.99%

## Jun
Luminace |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 3771801.47 | 4599271.243 | -827469.773 | -17.99% | 6447198.97 | -2675397.5 | -41.5%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC | 59494 | 64351.89 | -4857.89 | -7.549% | 66815.41 | -7321.41 | -10.96% | 1. Site has low production on 06/08, 06/26, 06/15, 06/16, 06/17, 06/27 due to low irradiance.
Berkeley - NJ-22-C893 Berkeley I | NJ | 0 | 0 | 0 |  | 715621.67 | -715621.67 | -100% | 1.Site was offline for whole month. | 1.SR098409
Berkeley - NJ-22-C894 Berkeley II | NJ | 566098 | 597076.8 | -30978.8 | -5.188% | 730590 | -164492 | -22.51% | 1.Site tripped offline since 13:00 on 06/27. | 1.SR103839
BEMS Landfill East | NJ | 2909 | 677634.821 | -674725.821 | -99.57% | 715608.89 | -712699.89 | -99.59% | 1.Site was offline for whole month. | 1.SR098408, SR086098
Southampton - BEMS West NJ-22-C898 | NJ | 539128 | 623908 | -84780 | -13.59% | 729514 | -190386 | -26.1% | 1.Site tripped offline at 14:45 on 06/05 and was back online at 16:15 on 06/05,again tripped offline at 07:45 on 06/08 reporting reporting "Missing Phase A Voltage" and was back online at 10:00 on 06/09,again tripped offline at 23:45 on 06/10 and was back online at 08:15 on 06/12,again tripped offline at 20:00 on 06/14 and remained offline throughout the month. | 1.SR102671
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ | 10056.063 | N/A |  |  | N/A
Lakewood Township - Public Works | NJ | 171840.301 | N/A |  |  | 933579 | -761738.699 | -81.59% | 1.Inverter 2.3 was underperforming by 6KW since 06/01 during peak hours and remained the same throughout the month | 1.SR103097
Canby - Dover - OR-23-C003 | OR | 560503.109 | 539401 | 21102.109 | 3.912% | 524490 | 36013.109 | 6.866%
Estacada - Clayfield - OR-23-C001 | OR | 663411.404 | 592440 | 70971.404 | 11.98% | 569205 | 94206.404 | 16.55% | 1.Tracker motor 68 was struck at -58 degrees at 08:30 pdt on 06/10 and was back at 13:45 pdt on 06/24 | 1.SR103219
Willamina - Waterford - OR-23-C006 | OR | 103706.924 | 474479.277 | -370772.353 | -78.14% | 473988 | -370281.076 | -78.12% | 1.All inverters are power limited to 85kW. Per As-Builts, they should be running at 122kW. | 1.SR101124
OR-23-C005 Solops SPI - Belvedere Solar | OR | 783866.619 | 740054.3 | 43812.319 | 5.92% | 709806 | 74060.619 | 10.43%
OR-23-C002 SPI - Cork Solar | OR | 310788.05 | 289925.155 | 20862.895 | 7.196% | 277981 | 32807.05 | 11.8%

## Jul
Luminace |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## Aug
Luminace |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## Sep
Luminace |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## Oct
Luminace |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## Nov
Luminace |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## Dec
Luminace |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Raymond Ed Re-Development - DC-23-0001 | DC
Berkeley - NJ-22-C893 Berkeley I | NJ
Berkeley - NJ-22-C894 Berkeley II | NJ
BEMS Landfill East | NJ
Southampton - BEMS West NJ-22-C898 | NJ
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ
Lakewood Township - Public Works | NJ
Canby - Dover - OR-23-C003 | OR
Estacada - Clayfield - OR-23-C001 | OR
Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR
OR-23-C002 SPI - Cork Solar | OR

## Sites
Portfolio: | Luminace
Site DAS Name | Site | State | Update | DAS
DC-23-0001 - Raymond Elementary Redev | Raymond Ed Re-Development - DC-23-0001 | DC | AEF | PowerTrack
NJ-22-C893 - CS Energy - Berkeley I | Berkeley - NJ-22-C893 Berkeley I | NJ | AEF | PowerTrack
NJ-22-C894 - CS Energy - Berkeley II | Berkeley - NJ-22-C894 Berkeley II | NJ | AEF | PowerTrack
Southampton - BEMS East NJ-22-C897 | BEMS Landfill East | NJ |  | PowerTrack
NJ-22-C898 - BEMS Landfill West | Southampton - BEMS West NJ-22-C898 | NJ | AEF | PowerTrack
Lakewood Twp - Emergency Services Dev - NJ-23-0008 | Lakewood Twp - Emergency Services Dev - NJ-23-0008 | NJ |  | PowerTrack
Lakewood Township - Public Works | Lakewood Township - Public Works | NJ |  | PowerTrack
OR-23-C003 Dover - SPI | Canby - Dover - OR-23-C003 | OR | AEF | PowerTrack
OR-23-C001 SPI - Clayfield Solar | Estacada - Clayfield - OR-23-C001 | OR | AEF | PowerTrack
SPI - Waterford Solar | Willamina - Waterford - OR-23-C006 | OR
OR-23-C005 Solops SPI - Belvedere Solar | OR-23-C005 Solops SPI - Belvedere Solar | OR | AEF
Molalla - Cork - OR-23-C002 | OR-23-C002 SPI - Cork Solar | OR