## Year to Date
Pardee (ENCAP) |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 2461304.2056 | 2597681.875 | -136377.6694 | -5.25% | 2830280.818 | -368976.6124 | -13.04%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: ASU - Pardee - Discovery Hall | AZ | 51914.5 | 46097.713 | 5816.787 | 12.62% | 59484.469 | -7569.969 | -12.73%
AZ: ASU - Pardee - Farrington | AZ | 237622.5806 | 207312.58 | 30310.0006 | 14.62% | 223950.06 | 2231.0835 | 0.9962%
AZ: ASU - Pardee - Macro Tech. | AZ | 528765.375 | 767014.8 | -238249.425 | -31.06% | 816459.74 | -104884.365 | -12.85%
AZ: ASU - Pardee - McCord Hall | AZ | 70159.625 | 61426.166 | 8733.459 | 14.22% | 80304.123 | -2559.483 | -3.187%
AZ: NAU - SF Garage | AZ | 484700 | 481141.676 | 3558.324 | 0.7396% | 464419.726 | 9573.347 | 2.061%
AZ: ASU - Pardee - Parking Lot 11 | AZ | 138702.75 | 146734.57 | -8031.82 | -5.474% | 133470.31 | 20474.6975 | 15.34%
AZ: ASU - Pardee - Parking Lot 19 | AZ | 214482.25 | 190535.2 | 23947.05 | 12.57% | 197636.13 | 27095.305 | 13.71%
AZ: ASU - Pardee - Parking Lot 41 | AZ | 186711 | 170555.45 | 16155.55 | 9.472% | 200570.59 | -4433.79 | -2.211%
AZ: ASU - Pardee - Parking Lot 58 | AZ | 174547.25 | 167202.33 | 7344.92 | 4.393% | 219352.16 | 8278.2 | 3.774%
AZ: ASU - Pardee - Parking Lot 59S | AZ | 203345.375 | 169696.07 | 33649.305 | 19.83% | 215423.51 | -14901.55 | -6.917%
AZ: ASU - Pardee - Sun Devil Complex | AZ | 170353.5 | 189965.32 | -19611.82 | -10.32% | 219210 | -17260 | -7.874%

## 1st Qtr
Pardee (ENCAP) |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1004744.636 | 1086389.238 | -81644.602 | -7.515% | 1083575.165 | -78830.529 | -7.275%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: ASU - Pardee - Discovery Hall | AZ | 21298.125 | 18845.884 | 2452.241 | 13.01% | 23742.099 | -2443.974 | -10.29%
AZ: ASU - Pardee - Farrington | AZ | 90404.8235 | 87040.22 | 3364.6035 | 3.866% | 88173.74 | 2231.0835 | 2.53%
AZ: ASU - Pardee - Macro Tech. | AZ | 214085.875 | 326130.6 | -112044.725 | -34.36% | 318970.24 | -104884.365 | -32.88%
AZ: ASU - Pardee - McCord Hall | AZ | 29492.25 | 23630.756 | 5861.494 | 24.8% | 32051.733 | -2559.483 | -7.985%
AZ: NAU - SF Garage | AZ | 180392 | 194414.138 | -14022.138 | -7.213% | 170818.653 | 9573.347 | 5.604%
AZ: ASU - Pardee - Parking Lot 11 | AZ | 64410.1875 | 60049.91 | 4360.2775 | 7.261% | 43935.49 | 20474.6975 | 46.6%
AZ: ASU - Pardee - Parking Lot 19 | AZ | 92152.625 | 84699.63 | 7452.995 | 8.799% | 65057.32 | 27095.305 | 41.65%
AZ: ASU - Pardee - Parking Lot 41 | AZ | 74533.5 | 72187.7 | 2345.8 | 3.25% | 78967.29 | -4433.79 | -5.615%
AZ: ASU - Pardee - Parking Lot 58 | AZ | 91159.5 | 73363.57 | 17795.93 | 24.26% | 82881.3 | 8278.2 | 9.988%
AZ: ASU - Pardee - Parking Lot 59S | AZ | 75749.75 | 67144.1 | 8605.65 | 12.82% | 90651.3 | -14901.55 | -16.44%
AZ: ASU - Pardee - Sun Devil Complex | AZ | 71066 | 78882.73 | -7816.73 | -9.909% | 88326 | -17260 | -19.54%

## 2nd Qtr
Pardee (ENCAP) |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 1456559.5696 | 1511292.637 | -54733.0674 | -3.622% | 1746705.653 | -290146.0834 | -16.61%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: ASU - Pardee - Discovery Hall | AZ | 30616.375 | 27251.829 | 3364.546 | 12.35% | 35742.37 | -5125.995 | -14.34%
AZ: ASU - Pardee - Farrington | AZ | 147217.7571 | 120272.36 | 26945.3971 | 22.4% | 135776.32 | 11441.4371 | 8.427%
AZ: ASU - Pardee - Macro Tech. | AZ | 314679.5 | 440884.2 | -126204.7 | -28.63% | 497489.5 | -182810 | -36.75%
AZ: ASU - Pardee - McCord Hall | AZ | 40667.375 | 37795.41 | 2871.965 | 7.599% | 48252.39 | -7585.015 | -15.72%
AZ: NAU - SF Garage | AZ | 304308 | 286727.538 | 17580.462 | 6.131% | 293601.073 | 10706.927 | 3.647%
AZ: ASU - Pardee - Parking Lot 11 | AZ | 74292.5625 | 86684.66 | -12392.0975 | -14.3% | 89534.82 | -15242.2575 | -17.02%
AZ: ASU - Pardee - Parking Lot 19 | AZ | 122329.625 | 105835.57 | 16494.055 | 15.58% | 132578.81 | -10249.185 | -7.731%
AZ: ASU - Pardee - Parking Lot 41 | AZ | 112177.5 | 98367.75 | 13809.75 | 14.04% | 121603.3 | -9425.8 | -7.751%
AZ: ASU - Pardee - Parking Lot 58 | AZ | 83387.75 | 93838.76 | -10451.01 | -11.14% | 136470.86 | -53083.11 | -38.9%
AZ: ASU - Pardee - Parking Lot 59S | AZ | 127595.625 | 102551.97 | 25043.655 | 24.42% | 124772.21 | 2823.415 | 2.263%
AZ: ASU - Pardee - Sun Devil Complex | AZ | 99287.5 | 111082.59 | -11795.09 | -10.62% | 130884 | -31596.5 | -24.14%

## 3rd Qtr
Pardee (ENCAP) |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: ASU - Pardee - Discovery Hall | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Farrington | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Macro Tech. | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - McCord Hall | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: NAU - SF Garage | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 11 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 19 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 41 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 58 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 59S | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Sun Devil Complex | AZ | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Pardee (ENCAP) |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: ASU - Pardee - Discovery Hall | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Farrington | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Macro Tech. | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - McCord Hall | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: NAU - SF Garage | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 11 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 19 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 41 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 58 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Parking Lot 59S | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: ASU - Pardee - Sun Devil Complex | AZ | 0 | 0 | 0 |  | 0 | 0

## Jan
Pardee (ENCAP) |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 288814.3755 | 316487.484 | -27673.1085 | -8.744% | 295930.845 | -7116.4695 | -2.405%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ | 5916.75 | 5538.374 | 378.376 | 6.832% | 6580.477 | -663.727 | -10.09% | 1. Inverter is producing at maximum 40 kW throughout the month compared to its capacity 50kW due to seasonal underperformance | 1. SR099649
AZ: ASU - Pardee - Farrington | AZ | 17359.0005 | 25551.77 | -8192.7695 | -32.06% | 24198.86 | -6839.8595 | -28.27% | 1. Meter CT was replaced on 01/13 and AlsoEnergy was able to regain meter communication from 12:00 PM on 01/13 | 1. SR094972
AZ: ASU - Pardee - Macro Tech. | AZ | 76476.625 | 96023.1 | -19546.475 | -20.36% | 89844.16 | -13367.535 | -14.88% | 1.Inverter 4 was offline from 01/21 and came back online on 01/24 at 10:30 after the blown fuse was replaced. 2. Inverter 4 offline from 01/25 and came back online on 01/29 at 10:45 after the blown fuse was replaced. | 1. SR095814 2.SR096012 , SR096160
AZ: ASU - Pardee - McCord Hall | AZ | 8385.875 | 6453.786 | 1932.089 | 29.94% | 8884.123 | -498.248 | -5.608%
AZ: NAU - SF Garage | AZ | 52716 | 57354.054 | -4638.054 | -8.087% | 45999.135 | 6716.865 | 14.6%
AZ: ASU - Pardee - Parking Lot 11 | AZ | 18327.75 | 17757.76 | 569.99 | 3.21% | 10305.89 | 8021.86 | 77.84%
AZ: ASU - Pardee - Parking Lot 19 | AZ | 26035.5 | 25220.52 | 814.98 | 3.231% | 15260.94 | 10774.56 | 70.6%
AZ: ASU - Pardee - Parking Lot 41 | AZ | 19602.125 | 21279.74 | -1677.615 | -7.884% | 21672.34 | -2070.215 | -9.552% | 1. Inverter 2 was underperforming 20kW down compared to inverter 1 due to L1 SP320 cartilage needs replacement and found active ground fault on CB 2-2 string 5. | 1. PM4031, SR086964, SR086966
AZ: ASU - Pardee - Parking Lot 58 | AZ | 25842.75 | 19977.46 | 5865.29 | 29.36% | 22973.07 | 2869.68 | 12.49%
AZ: ASU - Pardee - Parking Lot 59S | AZ | 20102.5 | 18284.13 | 1818.37 | 9.945% | 25126.85 | -5024.35 | -20% | 1.Inverter 1 is underperforming by 12kW down from 08:00 AM to 12:30 PM due to seasonal shading | 1. SR099639
AZ: ASU - Pardee - Sun Devil Complex | AZ | 18049.5 | 23046.79 | -4997.29 | -21.68% | 25085 | -7035.5 | -28.05% | 1. Inverter 1 was offline from 07:00 on 01/06 to 12:00pm on 01/24 due to failed PWR DIST Card | 1. SR094724

## Feb
Pardee (ENCAP) |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 332166.0784 | 336249.9 | -4083.8216 | -1.215% | 336219.701 | -4053.6226 | -1.206%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ | 6598.875 | 5712.358 | 886.517 | 15.52% | 7494.711 | -895.836 | -11.95% | 1. Inverter is producing at maximum 40 kW throughout the month compared to its capacity 50kW due to seasonal underperformance | 1. SR099649
AZ: ASU - Pardee - Farrington | AZ | 31007.3284 | 26810.49 | 4196.8384 | 15.65% | 27770.28 | 3237.0484 | 11.66%
AZ: ASU - Pardee - Macro Tech. | AZ | 72327.375 | 99628.9 | -27301.525 | -27.4% | 97007.78 | -24680.405 | -25.44% | 1. Inverter 4 was tripped offline at 18:15 on 02/16 due to control card assembly plus backplane. 2. Inverter 2 and meter 2 stopped communication at 11:50AM on 02/20 tech suggested that replacing the Vlink MESR901 serial server. | 1. SR095814, SR096160, SR096012 2. SR097592 | SR096160 | SR096012 | SR097592
AZ: ASU - Pardee - McCord Hall | AZ | 9147.5 | 7200.132 | 1947.368 | 27.05% | 10117.14 | -969.64 | -9.584%
AZ: NAU - SF Garage | AZ | 60795 | 63728.1 | -2933.1 | -4.603% | 53900.3 | 6894.7 | 12.79%
AZ: ASU - Pardee - Parking Lot 11 | AZ | 20052.5 | 18203.32 | 1849.18 | 10.16% | 13387.73 | 6664.77 | 49.78%
AZ: ASU - Pardee - Parking Lot 19 | AZ | 28758 | 25680.77 | 3077.23 | 11.98% | 19823.29 | 8934.71 | 45.07%
AZ: ASU - Pardee - Parking Lot 41 | AZ | 23110.25 | 22043 | 1067.25 | 4.842% | 24870.34 | -1760.09 | -7.077% | 1.Inverter 2 is underperforming by 20kW down due to shading related issue. | 1. SR096743
AZ: ASU - Pardee - Parking Lot 58 | AZ | 28384.25 | 22538.77 | 5845.48 | 25.94% | 26162.83 | 2221.42 | 8.491%
AZ: ASU - Pardee - Parking Lot 59S | AZ | 23550 | 20628.14 | 2921.86 | 14.16% | 28615.3 | -5065.3 | -17.7% | 1.Inverter 1 is underperforming by 12kW down from 08:00 AM to 12:30 PM due to seasonal shading | 1. SR099639
AZ: ASU - Pardee - Sun Devil Complex | AZ | 28435 | 24075.92 | 4359.08 | 18.11% | 27070 | 1365 | 5.042% | 1. Inverter 2 having multiple tripping events on 02/25 and 02/27. | 1. SR097804

## Mar
Pardee (ENCAP) |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 383764.1821 | 433651.854 | -49887.6719 | -11.5% | 451424.619 | -67660.4369 | -14.99%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ | 8782.5 | 7595.152 | 1187.348 | 15.63% | 9666.911 | -884.411 | -9.149%
AZ: ASU - Pardee - Farrington | AZ | 42038.4946 | 34677.96 | 7360.5346 | 21.23% | 36204.6 | 5833.8946 | 16.11%
AZ: ASU - Pardee - Macro Tech. | AZ | 65281.875 | 130478.6 | -65196.725 | -49.97% | 132118.3 | -66836.425 | -50.59% | 1.Inverter 4 was offline from 18:20 on 02/16 to 22:20 on 03/25. On 03/25, a Bold technician was onsite to replace the controller card and Upon arrival he found a worn DC shunt harness, which was requested for replacement. The inverter went offline again at 18:45 on 03/26 and requires additional components for full restoration. 2. Inverter 2 and meter 2 stopped communicating at 11:50AM on 02/20 and production can't be confirmed.On 02/24 upon troubleshooting ,technician recommends replacing the Vlink MESR901 serial server | 1.SR096012,SR096160 2.SR097592 | SR096160 | SR097592
AZ: ASU - Pardee - McCord Hall | AZ | 11958.875 | 9976.838 | 1982.037 | 19.87% | 13050.47 | -1091.595 | -8.364%
AZ: NAU - SF Garage | AZ | 66881 | 73331.984 | -6450.984 | -8.797% | 70919.218 | -4038.218 | -5.694%
AZ: ASU - Pardee - Parking Lot 11 | AZ | 26029.9375 | 24088.83 | 1941.1075 | 8.058% | 20241.87 | 5788.0675 | 28.59%
AZ: ASU - Pardee - Parking Lot 19 | AZ | 37359.125 | 33798.34 | 3560.785 | 10.54% | 29973.09 | 7386.035 | 24.64%
AZ: ASU - Pardee - Parking Lot 41 | AZ | 31821.125 | 28864.96 | 2956.165 | 10.24% | 32424.61 | -603.485 | -1.861% | 1.Inverter 2 is underperforming by approximately 20 kW, likely due to shading related issues | 1.SR096743
AZ: ASU - Pardee - Parking Lot 58 | AZ | 36932.5 | 30847.34 | 6085.16 | 19.73% | 33745.4 | 3187.1 | 9.445% | 1. A canopy strike was reported on 01/17, prompting immediate dispatch to secure the parking lot array and document the damages. Dispatch is scheduled to return on 04/10 to install five modules, reconnect homeruns, and re-energize the string. | 1.SR095815
AZ: ASU - Pardee - Parking Lot 59S | AZ | 32097.25 | 28231.83 | 3865.42 | 13.69% | 36909.15 | -4811.9 | -13.04% | 1.Inverter 1 is underperforming by 12kW down from 08:00 AM to 12:30 PM due to seasonal shading | 1. SR099639
AZ: ASU - Pardee - Sun Devil Complex | AZ | 24581.5 | 31760.02 | -7178.52 | -22.6% | 36171 | -11589.5 | -32.04% | 1. Inverter 2 tripped offline at 15:45 on 03/02 and was restored at 16:10 on 03/03 after a technician restart. It went offline again on 03/23 due to a "Watchdog Timer Fault." On 03/24, technicians confirmed the fault is related to internal monitoring and can be triggered by grid voltage fluctuations. The inverter was power cycled and back online at 09:10 AM on 03/24. 2. Inverter 1 tripped offline at 13:00 on 03/15/25 due to a ground fault. On 03/18, the technician observed heat marks on several Trina modules, likely impacted by recent heavy rain. A follow-up visit is required, along with replacement of 5A fuses. | 1.SR097804,SR098900 2.SR098620 | SR098900 | SR098620

## Apr
Pardee (ENCAP) |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 431830.9865 | 489908.589 | -58077.6025 | -11.85% | 544650.24 | -112819.2535 | -20.71%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ | 9782.375 | 8774.748 | 1007.627 | 11.48% | 11388.88 | -1606.505 | -14.11% | 1. Site has low production on 04/13, 04/14 due to low irradance.
AZ: ASU - Pardee - Farrington | AZ | 46470.174 | 38869.66 | 7600.514 | 19.55% | 43012.94 | 3457.234 | 8.038%
AZ: ASU - Pardee - Macro Tech. | AZ | 67915.125 | 144722.4 | -76807.275 | -53.07% | 157794.1 | -89878.975 | -56.96% | 1. Inverters 5 and 6 have started having multiple trips at peak production hours due to overheating from 04/09 to 04/11 and later technician cleaned the filters of the inverters and reinstalled them. 2. Inverter 4 was offline from 18:20 on 02/16 to 22:20 on 03/25. On 03/25, a Bold technician was onsite to replace the controller card and Upon arrival he found a worn DC shunt harness, which was requested for replacement. The inverter went offline again at 18:45 on 03/26 and requires additional components for full restoration. 3. Inverter 2 and meter 2 stopped communicating at 11:50AM on 02/20 and production can't be confirmed.On 02/24 upon troubleshooting ,technician recommends replacing the Vlink MESR901 serial server | 1. SR099674 2. SR096012,SR096160 3. SR097592 | SR096012 | SR096160 | SR097592
AZ: ASU - Pardee - McCord Hall | AZ | 13171.5 | 11671.52 | 1499.98 | 12.85% | 15375.47 | -2203.97 | -14.33% | 1. Site has low production on 04/13, 04/14 due to low irradance.
AZ: NAU - SF Garage | AZ | 89072 | 89135.321 | -63.321 | -0.07104% | 87478.27 | 1593.73 | 1.822% | 1. Inverter 1C is producing low, possibly down a string from 04/24. | 1. SR100105
AZ: ASU - Pardee - Parking Lot 11 | AZ | 28647.6875 | 27500.1 | 1147.5875 | 4.173% | 26607.96 | 2039.7275 | 7.666% | 1. Inverter 1 dropped by 33 kW at 12:15 pm MST on 04/30 due to CB down. 2. Inverter 2 is down a CB or has some bypassed modules according to the drawing since 04/30. Inverter 2 started tripping on and off from 04/09 to 04/25. | 1. SR100774 2. SR100778, SR099610 | SR100778 | SR099610
AZ: ASU - Pardee - Parking Lot 19 | AZ | 41390.5 | 35772.43 | 5618.07 | 15.71% | 39398.62 | 1991.88 | 5.056%
AZ: ASU - Pardee - Parking Lot 41 | AZ | 35712.125 | 32036.25 | 3675.875 | 11.47% | 38522.63 | -2810.505 | -7.296% | 1. Inverter 2 underperforming by 5 kW due to CB 2.2 string 5 has a ground fault. | 1. SR100174
AZ: ASU - Pardee - Parking Lot 58 | AZ | 36448 | 31437.97 | 5010.03 | 15.94% | 43485.95 | -7037.95 | -16.18% | 1. A canopy strike was reported on 01/17, prompting immediate dispatch to secure the parking lot array and document the damages. Dispatch is scheduled to return on 04/10 to install five modules, reconnect homeruns, and re-energize the string. | 1. SR095815
AZ: ASU - Pardee - Parking Lot 59S | AZ | 40972.5 | 34352.71 | 6619.79 | 19.27% | 39758.42 | 1214.08 | 3.054% | 1. Inverter 1 is underperforming by approximately 12kW down from 08:00 to 12:30 on 04/10 due to seasonal shading. | 1. SR099639
AZ: ASU - Pardee - Sun Devil Complex | AZ | 22249 | 35635.48 | -13386.48 | -37.57% | 41827 | -19578 | -46.81% | 1. Inverter 1 tripped offline at 13:00 on 03/15/25 due to a ground fault. On 03/18, the technician found heat marks on several Trina modules, likely from recent heavy rain. A follow-up was needed to replace 5A fuses. On 04/17, string testing began; ground faults were found across all DC strings. Defective modules were bypassed using jumpers. By 04/18, CB-1, CB-2, and CB-3 were cleared of ground faults. A ground fault board and 3A fuse were replaced, DC conductors reconnected, and the inverter power-cycled at 10:45. 2. Inverter 1 is down 2–3 strings. Modules were bypassed on 04/17–04/18. Client declined to pay for replacements. 3. Inverter 2 has been tripping on and offline, likely due to heat (cell temps ≥95°F since 04/14). It went offline on 04/15, was power-cycled back online on 04/17, and tripped again on 04/20. On 04/22, fault 0080 appeared; technician reseated the ribbon cable and cleaned the controller card per Bold's advice. It restarted but later showed fault 0011. On 04/24, after further testing, a new fault appeared. Bold reviewed logs on 04/25 and advised swapping parts with Inverter 1. After swapping, inverter tripped again at 13:30 with PS10 fault. Bold confirmed the issue is due to a faulty power distribution board and will provide a quote and remained offline through the month. 4. 3 Modules, procurement in process. | 1. SR098620 2. SR100058, SR98620 3. SR099782, SR100047, PM9663 4. SR100349, PM9663 | SR100058 | SR98620 | SR099782 | SR100047 | SR100349

## May
Pardee (ENCAP) |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 501084.6063 | 514814.129 | -13729.5227 | -2.667% | 611602.759 | -110518.1527 | -18.07%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ | 10488.875 | 9328.885 | 1159.99 | 12.43% | 12503.43 | -2014.555 | -16.11% | 1. Site has low production on 05/06, 05/12 due to low irradiance. 2.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: ASU - Pardee - Farrington | AZ | 50567.7313 | 41070.7 | 9497.0313 | 23.12% | 47556.58 | 3011.1513 | 6.332%
AZ: ASU - Pardee - Macro Tech. | AZ | 113365.125 | 148776.3 | -35411.175 | -23.8% | 171785.3 | -58420.175 | -34.01% | 1. Inverter 4 was offline from 02/16 until 10:45 on 05/05. After the technician replaced the DC shunt harness, AC disconnect rod and lever, and four filters, it went offline again at 19:00 on 05/05. It came back online at 07:00 on 05/10, then went offline once more on 05/11 and self-resolved by 14:00 on 05/12. 2. Inverter 5 &6 is offline from 05:00 on 05/06 to 06:00 on 05/10 and Inverter 3 offline from 07:00 on 05/08 to 07:00 on 05/10. These inverters have self-resolved. 3. Inverters 5 and 6 are derating midday by 50kW at peak production at the hours of 11:00 to 15:45 from 5/21/25 and on 05/30, the technician inspected and as per Blod renewables cleaned the inverter filters thoroughly and reinstalled the filters and confirmed that airflow was restored to optimal levels. 4. Inverter 2 and meter 2 stopped communicating at 11:50AM on 02/20 and production can't be confirmed.On 02/24 upon troubleshooting ,technician recommends replacing the Vlink MESR901 serial server | 1. SR101060, SR101332, SR096160 & SR102080 2. SR101060, SR101332 3. SR101859 4. SR102524, SR097592 | SR101332 | SR096160 | SR102080 | SR101060 | SR101332 | SR101859 | SR102524 | SR097592
AZ: ASU - Pardee - McCord Hall | AZ | 13858 | 12984.95 | 873.05 | 6.724% | 16879.68 | -3021.68 | -17.9% | 1. Site was taken offline from 09:23 to 11:45 on 05/22 for Preventative maintenance. 2.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance. | 1. PM10595, SR102079
AZ: NAU - SF Garage | AZ | 106384 | 98956.114 | 7427.886 | 7.506% | 104975.109 | 1408.891 | 1.342% | 1. Inverter 1C has been underperforming, possibly due to a string issue since 04/24. On 05/16, the technician found string #2's fuse holder open, disconnecting it from the inverter. The technician closed the fuse holder and reconnected the string | 1. SR101409, SR100105 | SR100105
AZ: ASU - Pardee - Parking Lot 11 | AZ | 23313.75 | 29914.1 | -6600.35 | -22.06% | 31776 | -8462.25 | -26.63% | 1. Inverter 1 dropped 33 kW at 12:15 PM MST on 04/30 due to a tripped circuit breaker; awaiting correct T-Blocks for restoration. 2. Inverter 2 is down due to a tripped CB or bypassed modules. On 05/01, the technician found CB-2 conductor showed overheating damage and a broken module was found.The site was taken offline on 05/01 from 11:45 to 12:30. The site was offline from 09:00 to 11:30 on 05/16 to replace the damaged conductor and module; Inverter 1 also needs fan, fuse, and DC block replacements. Inverter 2 was tripping on and off for whole month. 3. On 05/22, the String 2 0vdc - string 6 negative conductor is frayed will need to troubleshoot technician found during Annual Preventative Maintenance Inspection. | 1. SR100774 2. SR100778 3. SR101850, PM10032 | SR100778 | SR101850
AZ: ASU - Pardee - Parking Lot 19 | AZ | 42888.875 | 35841.24 | 7047.635 | 19.66% | 47053.07 | -4164.195 | -8.85% | 1. Site was offline from 13:23 to 13:57 on 05/01 to replace inverter filters 2. On 05/24, Inverter 2 underperformed by 20 kW compared to peers. On 05/27, the technician inspected the unit and found no visible damage or faults. Power output was low but matched the peer inverter. No active alarms were reported. The inverter is overheating due to temperatures above 100°F. A shading structure is recommended. | 1. SR099846 2. SR101951, SR102330 and PM8480 | SR101951 | SR102330
AZ: ASU - Pardee - Parking Lot 41 | AZ | 38351.25 | 33576.23 | 4775.02 | 14.22% | 42592.42 | -4241.17 | -9.958% | 1. Inverter 2 underperforming by 5 kW due to a CB 2.2 string 5 has a ground fault. 2. Inveter 1 was offline from 15:00 to 15:40 and Inverter 2 was from 14:44 to 15:21 on 05/01 to replace inverter filters | 1. SR100174 2. SR099847 | SR099847
AZ: ASU - Pardee - Parking Lot 58 | AZ | 23218.75 | 31718.46 | -8499.71 | -26.8% | 47739.77 | -24521.02 | -51.36% | 1. Inverter 3 tripped offline at 10:15 on 05/08 due to a "Faulted voltage fault" and remained offline through the month. On 05/14, the technician found a blown fuse on phase C and irregular behavior on phase 2. Inverters 1 and 2 are connected to parking lot 59, and inverters 3 and 4 to lot 58, but AlsoEnergy shows the opposite configuration. Updates are pending on hardware repair and monitoring correction. | 1. SR101590, SR101591 & PM10037 | SR101591
AZ: ASU - Pardee - Parking Lot 59S | AZ | 43614.75 | 34664.03 | 8950.72 | 25.82% | 43647.4 | -32.65 | -0.0748%
AZ: ASU - Pardee - Sun Devil Complex | AZ | 35033.5 | 37983.12 | -2949.62 | -7.766% | 45094 | -10060.5 | -22.31% | 1. Inverter 2 was offline from 13:30 on 04/25 to 10:45 on 05/13 2. 3 Modules, procurement in process. | 1. SR100047, PM9663 2. SR100349, PM9663 | SR100349

## Jun
Pardee (ENCAP) |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 523643.9769 | 506569.919 | 17074.0579 | 3.371% | 590452.654 | -66808.6771 | -11.31%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ | 10345.125 | 9148.196 | 1196.929 | 13.08% | 11850.06 | -1504.935 | -12.7% | 1. Site has low production on 06/01, due to low irradiance. 2.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: ASU - Pardee - Farrington | AZ | 50179.8519 | 40332 | 9847.8519 | 24.42% | 45206.8 | 4973.0519 | 11%
AZ: ASU - Pardee - Macro Tech. | AZ | 133399.25 | 147385.5 | -13986.25 | -9.49% | 167910.1 | -34510.85 | -20.55% | 1. Inverter 2 and meter 2 stopped communicating at 11:50AM on 02/20 and production can't be confirmed.On 02/24 upon troubleshooting ,technician recommends replacing the Vlink MESR901 serial server. Replacement parts are currently pending. 2. Inverters 5 and 6 are derating midday by 50kW at peak production at the hours from 06/06, on 06/20 the technician was onsite and no damages or faults found on the inverters as they continue to derate. He contacted the manufacturer, and they requested the log files for the inverters which he sent for review. and invereters are derated throughout the month. | 1. SR102524, SR097592 2. SR101859, SR103044 | SR097592 | SR101859 | SR103044
AZ: ASU - Pardee - McCord Hall | AZ | 13637.875 | 13138.94 | 498.935 | 3.797% | 15997.24 | -2359.365 | -14.75% | 1. Site has low production on 06/01, due to low irradiance. 2.As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
AZ: NAU - SF Garage | AZ | 108852 | 98636.103 | 10215.897 | 10.36% | 101147.694 | 7704.306 | 7.617%
AZ: ASU - Pardee - Parking Lot 11 | AZ | 22331.125 | 29270.46 | -6939.335 | -23.71% | 31150.86 | -8819.735 | -28.31% | 1. Inverter 1 dropped 33 kW at 12:15 PM MST on 04/30 due to a tripped circuit breaker; awaiting correct T-Blocks for restoration. Bold Renewables for parts procurement pending. 2. On 05/22, the String 2 0vdc - string 6 negative conductor is frayed will need to troubleshoot technician found during Annual Preventative Maintenance Inspection. on 06/17 technician was on site and replaced a fuse on CB 2-2 and retightened terminations and CB 2-2 is back to normal operational. | 1. SR100774, SR103110 2. SR101850, PM10032 | SR103110 | SR101850
AZ: ASU - Pardee - Parking Lot 19 | AZ | 38050.25 | 34221.9 | 3828.35 | 11.19% | 46127.12 | -8076.87 | -17.51% | 1. On 05/24, Inverter 2 underperformed by 20 kW compared to peers. On 05/27, the technician inspected the unit and found no visible damage or faults. Power output was low but matched the peer inverter. No active alarms were reported. The inverter is overheating due to temperatures above 100°F. A shading structure is recommended. and parts are under replacement. | 1. SR101951, SR102330 and PM8480 | SR102330
AZ: ASU - Pardee - Parking Lot 41 | AZ | 38114.125 | 32755.27 | 5358.855 | 16.36% | 40488.25 | -2374.125 | -5.864% | 1. Inverter 2 underperforming by 5 kW and CB 2.2 string 5 has a ground fault. | 1. SR100174
AZ: ASU - Pardee - Parking Lot 58 | AZ | 23721 | 30682.33 | -6961.33 | -22.69% | 45245.14 | -21524.14 | -47.57% | 1. Inverter 3 tripped offline at 10:15 on 05/08 due to a "Faulted voltage fault" and back online at 09:00 on 06/23. | 1. SR101590, SR101591, SR101406. | SR101591 | SR101406
AZ: ASU - Pardee - Parking Lot 59S | AZ | 43008.375 | 33535.23 | 9473.145 | 28.25% | 41366.39 | 1641.985 | 3.969%
AZ: ASU - Pardee - Sun Devil Complex | AZ | 42005 | 37463.99 | 4541.01 | 12.12% | 43963 | -1958 | -4.454%

## Jul
Pardee (ENCAP) |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ
AZ: ASU - Pardee - Farrington | AZ
AZ: ASU - Pardee - Macro Tech. | AZ
AZ: ASU - Pardee - McCord Hall | AZ
AZ: NAU - SF Garage | AZ
AZ: ASU - Pardee - Parking Lot 11 | AZ
AZ: ASU - Pardee - Parking Lot 19 | AZ
AZ: ASU - Pardee - Parking Lot 41 | AZ
AZ: ASU - Pardee - Parking Lot 58 | AZ
AZ: ASU - Pardee - Parking Lot 59S | AZ
AZ: ASU - Pardee - Sun Devil Complex | AZ

## Aug
Pardee (ENCAP) |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ
AZ: ASU - Pardee - Farrington | AZ
AZ: ASU - Pardee - Macro Tech. | AZ
AZ: ASU - Pardee - McCord Hall | AZ
AZ: NAU - SF Garage | AZ
AZ: ASU - Pardee - Parking Lot 11 | AZ
AZ: ASU - Pardee - Parking Lot 19 | AZ
AZ: ASU - Pardee - Parking Lot 41 | AZ
AZ: ASU - Pardee - Parking Lot 58 | AZ
AZ: ASU - Pardee - Parking Lot 59S | AZ
AZ: ASU - Pardee - Sun Devil Complex | AZ

## Sep
Pardee (ENCAP) |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ
AZ: ASU - Pardee - Farrington | AZ
AZ: ASU - Pardee - Macro Tech. | AZ
AZ: ASU - Pardee - McCord Hall | AZ
AZ: NAU - SF Garage | AZ
AZ: ASU - Pardee - Parking Lot 11 | AZ
AZ: ASU - Pardee - Parking Lot 19 | AZ
AZ: ASU - Pardee - Parking Lot 41 | AZ
AZ: ASU - Pardee - Parking Lot 58 | AZ
AZ: ASU - Pardee - Parking Lot 59S | AZ
AZ: ASU - Pardee - Sun Devil Complex | AZ

## Oct
Pardee (ENCAP) |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ
AZ: ASU - Pardee - Farrington | AZ
AZ: ASU - Pardee - Macro Tech. | AZ
AZ: ASU - Pardee - McCord Hall | AZ
AZ: NAU - SF Garage | AZ
AZ: ASU - Pardee - Parking Lot 11 | AZ
AZ: ASU - Pardee - Parking Lot 19 | AZ
AZ: ASU - Pardee - Parking Lot 41 | AZ
AZ: ASU - Pardee - Parking Lot 58 | AZ
AZ: ASU - Pardee - Parking Lot 59S | AZ
AZ: ASU - Pardee - Sun Devil Complex | AZ
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual data is taken from inverters data since meter lost communication from 08/22

## Sites
Portfolio: | Pardee (ENCAP)
Site DAS Name | Site | State | Update | DAS
AZ: ASU - Pardee - Discovery Hall | AZ: ASU - Pardee - Discovery Hall | AZ
AZ: ASU - Pardee - Farrington | AZ: ASU - Pardee - Farrington | AZ
AZ: ASU - Pardee - Macro Tech. | AZ: ASU - Pardee - Macro Tech. | AZ
AZ: ASU - Pardee - McCord Hall | AZ: ASU - Pardee - McCord Hall | AZ
AZ: NAU - SF Garage | AZ: NAU - SF Garage | AZ
AZ: ASU - Pardee - Parking Lot 11 | AZ: ASU - Pardee - Parking Lot 11 | AZ
AZ: ASU - Pardee - Parking Lot 19 | AZ: ASU - Pardee - Parking Lot 19 | AZ
AZ: ASU - Pardee - Parking Lot 41 | AZ: ASU - Pardee - Parking Lot 41 | AZ
AZ: ASU - Pardee - Parking Lot 58 | AZ: ASU - Pardee - Parking Lot 58 | AZ
AZ: ASU - Pardee - Parking Lot 59S | AZ: ASU - Pardee - Parking Lot 59S | AZ
AZ: ASU - Pardee - Sun Devil Complex | AZ: ASU - Pardee - Sun Devil Complex | AZ

## Nov
Pardee (ENCAP) |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ
AZ: ASU - Pardee - Farrington | AZ
AZ: ASU - Pardee - Macro Tech. | AZ
AZ: ASU - Pardee - McCord Hall | AZ
AZ: NAU - SF Garage | AZ
AZ: ASU - Pardee - Parking Lot 11 | AZ
AZ: ASU - Pardee - Parking Lot 19 | AZ
AZ: ASU - Pardee - Parking Lot 41 | AZ
AZ: ASU - Pardee - Parking Lot 58 | AZ
AZ: ASU - Pardee - Parking Lot 59S | AZ
AZ: ASU - Pardee - Sun Devil Complex | AZ
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual data is taken from inverters data since meter lost communication from 08/22

## Dec
Pardee (ENCAP) |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: ASU - Pardee - Discovery Hall | AZ
AZ: ASU - Pardee - Farrington | AZ
AZ: ASU - Pardee - Macro Tech. | AZ
AZ: ASU - Pardee - McCord Hall | AZ
AZ: NAU - SF Garage | AZ
AZ: ASU - Pardee - Parking Lot 11 | AZ
AZ: ASU - Pardee - Parking Lot 19 | AZ
AZ: ASU - Pardee - Parking Lot 41 | AZ
AZ: ASU - Pardee - Parking Lot 58 | AZ
AZ: ASU - Pardee - Parking Lot 59S | AZ
AZ: ASU - Pardee - Sun Devil Complex | AZ
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual data is taken from inverters data since meter lost communication from 08/22