## Year to Date
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 211433 | 0 | 211433 | 0% | 266579.029 | -55146.029 | -20.69%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 211433 | 0 | 211433 |  | 266579.029 | -55146.029 | -20.69%

## 1st Qtr
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 62685.56 | 0 | 62685.56 | 0% | 95137.67 | -32452.11 | -34.11%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 62685.56 | 0 | 62685.56 |  | 95137.67 | -32452.11 | -34.11%

## 2nd Qtr
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 148747.44 | 0 | 148747.44 | 0% | 171441.359 | -22693.919 | -13.24%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 148747.44 | 0 | 148747.44 |  | 171441.359 | -22693.919 | -13.24%

## 3rd Qtr
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 0 | 0 | 0 |  | 0 | 0

## Jan
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 14501.82 | 0 | 14501.82 | 0% | 21275.77 | -6773.95 | -31.84%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 14501.82 | N/A |  |  | 21275.77 | -6773.95 | -31.84% | 1. Inverter 6 has been tripping on and off throughout the month due to a "DC injection fault" in SolarEdge portal. 2. Inverter 1 requires a new relay board and fan 3. Low generation due to weather/snow. | 1. SR098945 2. SR094603 | SR094603

## Feb
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 5822.47 | 0 | 5822.47 | 0% | 30103.22 | -24280.75 | -80.66%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 5822.47 | N/A |  |  | 30103.22 | -24280.75 | -80.66% | 1. Inverter 1 requires a new relay board and fan. 2. Inverter 6 has been tripping on and off throughout the month due to a "DC injection fault" in SolarEdge portal. 3. Low generation due to weather/snow. | 1. SR094603 2. SR098945 | SR098945

## Mar
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 42361.27 | 0 | 42361.27 | 0% | 43758.68 | -1397.41 | -3.193%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 42361.27 | N/A |  |  | 43758.68 | -1397.41 | -3.193% | 1. The inverter 3 tripped offline at 06:45 AM on 03/06, reporting a "VinP Max" error. After inspection, the technician observed that a large amount of rain and snowmelt was causing insulation faults in the inverter. After troubleshooting, the inverter was back online at 12:00 PM on 03/06. 2. Inverter 6 has been tripping on and off throughout the month due to a "DC injection fault" in SolarEdge portal and Also Energy portal. 3. Inverter 1 requires a new relay board and fan. | 1. SR098206 2. SR098945 3. SR094603 | SR098945 | SR094603

## Apr
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 48045.84 | 0 | 48045.84 | 0% | 50356.404 | -2310.564 | -4.588%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 48045.84 | N/A |  |  | 50356.404 | -2310.564 | -4.588% | 1. Inverter 6 has been tripping on and off throughout the month due to a "DC injection fault" in SolarEdge portal and Also Energy portal. | 1. SR098945

## May
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 44905.75 | 0 | 44905.75 | 0% | 59923.825 | -15018.075 | -25.06%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 44905.75 | N/A |  |  | 59923.825 | -15018.075 | -25.06% | 1. Inverter 6 has been tripping on and off throughout the month due to a "DC injection fault" in SolarEdge portal and Also Energy portal. | 1. SR098945

## Jun
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 55795.85 | 0 | 55795.85 | 0% | 61161.13 | -5365.28 | -8.772%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | 55795.85 | N/A |  |  | 61161.13 | -5365.28 | -8.772% | 1. Inverter 6 has been tripping on and off throughout the month due to a "DC injection fault" in SolarEdge portal and Also Energy portal. 2. Inverter 7 has multiple tripping's since 06/11.on 06/16 technician was updated the firmware, set country code and paired optimizers . then inverter is running as expected. | 1. SR098945, SR103041 2. SR102915 | SR103041 | SR102915

## Jul
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA |  | 0

## Aug
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA |  | 0

## Sep
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA |  | 0

## Oct
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA |  | 0

## Nov
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA |  | 0

## Dec
MA: Leominster - 1776 Lock Dr - Rapco Horizon |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA |  | 0

## Sites
Portfolio: | MA: Leominster - 1776 Lock Dr - Rapco Horizon
Site DAS Name | Site | State | Update | DAS
Rapco Horizon - 1776 Lock Dr | MA: Leominster - 1776 Lock Dr - Rapco Horizon | MA | AF | PowerTrack