## Year to Date
AB CarVal |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 12232640.7034 | 15942459.6079 | -3709818.9045 | -23.27% | 16168749.4 | -3936108.6966 | -24.34%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 775506 | 810337.697 | -34831.697 | -4.298% | 726216.9 | 49289.1 | 6.787%
Bakersfield - 100 Basic School Rd | CA | 2749226.4665 | 2476003.6 | 273222.8665 | 11.03% | 2623010.6 | 126215.8665 | 4.812%
Fresno - 2685 Cornelia Ave | CA | 2561171 | 4716317 | -2155146 | -45.7% | 5078948 | -2517777 | -49.57%
San Juaquin - S. Placer & W. Adams | CA | 1857715.7083 | 2062015.1 | -204299.3917 | -9.908% | 1834917.4 | 22798.3083 | 1.242%
Charlemont - 0 Tea St | MA | 181386 | 940745.9592 | -759359.9592 | -80.72% | 864647.5 | -683261.5 | -79.02%
Amherst - 740 Belchertown Rd | MA | 769133 | 994560.4431 | -225427.4431 | -22.67% | 936702 | -167569 | -17.89%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 2117077.5286 | 2051748.2212 | 65329.3074 | 3.184% | 2226965 | -109887.4714 | -4.934%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 1221425 | 1890731.5875 | -669306.5875 | -35.4% | 1877342 | -655917 | -34.94%

## 1st Qtr
AB CarVal |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 12232640.7034 | 15942459.6079 | -3709818.9045 | -23.27% | 16168749.4 | -3936108.6966 | -24.34%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 775506 | 810337.697 | -34831.697 | -4.298% | 726216.9 | 49289.1 | 6.787%
Bakersfield - 100 Basic School Rd | CA | 2749226.4665 | 2476003.6 | 273222.8665 | 11.03% | 2623010.6 | 126215.8665 | 4.812%
Fresno - 2685 Cornelia Ave | CA | 2561171 | 4716317 | -2155146 | -45.7% | 5078948 | -2517777 | -49.57%
San Juaquin - S. Placer & W. Adams | CA | 1857715.7083 | 2062015.1 | -204299.3917 | -9.908% | 1834917.4 | 22798.3083 | 1.242%
Charlemont - 0 Tea St | MA | 181386 | 940745.9592 | -759359.9592 | -80.72% | 864647.5 | -683261.5 | -79.02%
Amherst - 740 Belchertown Rd | MA | 769133 | 994560.4431 | -225427.4431 | -22.67% | 936702 | -167569 | -17.89%
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 2117077.5286 | 2051748.2212 | 65329.3074 | 3.184% | 2226965 | -109887.4714 | -4.934%
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 1221425 | 1890731.5875 | -669306.5875 | -35.4% | 1877342 | -655917 | -34.94%

## 2nd Qtr
AB CarVal |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 0 | 0 | 0 |  | 0 | 0
Bakersfield - 100 Basic School Rd | CA | 0 | 0 | 0 |  | 0 | 0
Fresno - 2685 Cornelia Ave | CA | 0 | 0 | 0 |  | 0 | 0
San Juaquin - S. Placer & W. Adams | CA | 0 | 0 | 0 |  | 0 | 0
Charlemont - 0 Tea St | MA | 0 | 0 | 0 |  | 0 | 0
Amherst - 740 Belchertown Rd | MA | 0 | 0 | 0 |  | 0 | 0
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 0 | 0 | 0 |  | 0 | 0
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
AB CarVal |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 0 | 0 | 0 |  | 0 | 0
Bakersfield - 100 Basic School Rd | CA | 0 | 0 | 0 |  | 0 | 0
Fresno - 2685 Cornelia Ave | CA | 0 | 0 | 0 |  | 0 | 0
San Juaquin - S. Placer & W. Adams | CA | 0 | 0 | 0 |  | 0 | 0
Charlemont - 0 Tea St | MA | 0 | 0 | 0 |  | 0 | 0
Amherst - 740 Belchertown Rd | MA | 0 | 0 | 0 |  | 0 | 0
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 0 | 0 | 0 |  | 0 | 0
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
AB CarVal |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Fairhaven - 279 Mill Rd | MA | 0 | 0 | 0 |  | 0 | 0
Bakersfield - 100 Basic School Rd | CA | 0 | 0 | 0 |  | 0 | 0
Fresno - 2685 Cornelia Ave | CA | 0 | 0 | 0 |  | 0 | 0
San Juaquin - S. Placer & W. Adams | CA | 0 | 0 | 0 |  | 0 | 0
Charlemont - 0 Tea St | MA | 0 | 0 | 0 |  | 0 | 0
Amherst - 740 Belchertown Rd | MA | 0 | 0 | 0 |  | 0 | 0
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 0 | 0 | 0 |  | 0 | 0
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 0 | 0 | 0 |  | 0 | 0

## Jan
AB CarVal |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 3950905.2386 | 4602075.2571 | -651170.0185 | -14.15% | 3574033.6 | 376871.6386 | 10.54%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 212302 | 243217.7892 | -30915.7892 | -12.71% | 174518.6 | 37783.4 | 21.65%
Bakersfield - 100 Basic School Rd | CA | 876708.0303 | 547801 | 328907.0303 | 60.04% | 621297.8 | 255410.2303 | 41.11% | 1.The weather station stopped communicating from 12:30 AM on 01/16/25 due to the SCADA server and Watchdog not running on the server end,later back online at 10:00 AM on 01/27/25. 2. Inverter 1.2 has been derating by 80 kW at 13:30 on 01/28/25 and has self resolved at 6:30am on 01/29/25 due to Internal fan fault | 1. SR095612 2. SR096082 | SR096082
Fresno - 2685 Cornelia Ave | CA | 1178944 | 1571662 | -392718 | -24.99% | 1030154 | 148790 | 14.44% | 1. The site experienced frequent outages throughout the month due to PG&E curtailments. 2. Tracker controller 3, tracker set position 2 reporting erroneous value and tracker position motor 2 was stuck at 50.76 Degrees. Tracker need New encoder. 3. Site was offline from 13:00 to 14:30 on 01/16 4.Combiner boxes 1.19, 1.21, 1.23, 1.25, 1.27, 3.20, 3.22, 3.24, 3.26, 3.28, are underperforming from 12/23/24. Will Investigate during PM inspection 5. Inverter 3 is started late and reporting reversed branch overcurrent on 01/02, 01/03 , 01/17 | 1.SR095240 2. SR094675 3.SR095640 4. SR095229 5. SR094991 | SR094675 | SR095640 | SR095229 | SR094991
San Juaquin - S. Placer & W. Adams | CA | 522765.2083 | 599049.6 | -76284.3917 | -12.73% | 380972.2 | 141793.0083 | 37.22% | 1. Inverter 6 is being RMA'd due to internal board failure. 2. Site was tripped offline on 12/31/24 at 14:00 and came back online on 01/02/25 at 12:00 after the technician re-energized the site and corrected the incorrect Grid Connect rule for Inverter 1. 3. Inverter 1 is started late for production at 8:30AM on 01/17 due to an momentary Isolation Error. | 1.SR095174, SR095112 2. SR095204 3. SR095076 | SR095112 | SR095204 | SR095076
Charlemont - 0 Tea St | MA | 99864 | 266325.2017 | -166461.2017 | -62.5% | 193054 | -93190 | -48.27% | 1. Site was brought back online at 1:15PM on 01/08/25 after the SMA technician repalced the AC control board. 2. Inverter tripped offline at 14:25 on 01/30 later remotely closed at 16:00 on 01/30 | 1.SR093625 2.SR096136 | SR096136
Amherst - 740 Belchertown Rd | MA | 189777 | 290332.7247 | -100555.7247 | -34.63% | 205706 | -15929 | -7.744% | 1.Low generation due to weather/snow.
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 582212 | 571527.0279 | 10684.9721 | 1.87% | 539970 | 42242 | 7.823% | 1. Site was tripped offline at 10:30AM on 01/02/2025. It was brought back online at 2:35PM on same day after technician closing the SEL relay. | 1. SR095236
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 288333 | 512159.9137 | -223826.9137 | -43.7% | 428361 | -140028 | -32.69% | 1. Site was offline at 8:40 AM on 01/15/25. It was brought back online, and communication was restored at 7:05 AM on 01/16/25 after the technician power-cycled the Dell Data Processor on 01/18/25. 2. Inverters have been offline since 01/23/25 and PE brought all DC converters online by replacing the softcharge contactors on 01/24/25. 3. Inverter 2 tripped offline at 15:50 on 01/29 due to loose fiber optic cable causing a false F25 fault which opens the AC breaker and was brought back online on 01/30/25 after the technician charged the main AC breaker. | 1. SR095594 2. SR095883 3. SR096095 | SR095883 | SR096095

## Feb
AB CarVal |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 3635954.5 | 4695270.9438 | -1059316.4438 | -22.56% | 4970555.5 | -1334601 | -26.85%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 239618 | 252478.3854 | -12860.3854 | -5.094% | 233283.2 | 6334.8 | 2.715%
Bakersfield - 100 Basic School Rd | CA | 814344 | 819337.6 | -4993.6 | -0.6095% | 818347.8 | -4003.8 | -0.4893% | 1. Inverter 1.2 was derated by 80KW on 02/21 due to Intermal fan fault error and is being RMA'D by CES. 2.Inverters 1.1, 2.4, 2.5, 2.6 have consistent late starts on multiple days of the Month due to Isolation or ground fault. On 02/20 technician arrived and stated that multiple modules were broken and need to be replaced. 3.Site stopped communicating from 12:15PM to 17:45PM on 02/27. Energy data was not backfilled. | 1.SR096082 2.SR096248 3.SR097890 | SR096248 | SR097890
Fresno - 2685 Cornelia Ave | CA | 785248 | 1206122 | -420874 | -34.89% | 1544081 | -758833 | -49.14% | 1. The site experienced frequent outages throughout the month due to PG&E curtailments. 2. Inverter 3 tracker controller 3 motor 2 position stuck at 50.76 Degrees. Tracker need New encoder. On 02/07 Tech replaced encoder on tracker 2. After replacing encoder, tech logged into PLC and cleared encoder fault. Array began tracking correctly. Tech also found tracker 3 motor 4 array to be stuck in the east position. Tech troubleshot motor control box and cleared fault 3.Inverter 3 has multiple tripping events through out the month due to Reverse Branch Overcurrent fault and tripped offline from 02/24 at 14:30 due to DC over current fault. On 02/25 tech checked in and stated that Ground fault fuses needed. 4.Tracker 3 motor 4 is stuck at 51.83 degrees; setpoint is -52 degrees from 02/02 due to Critical torque tube failure and encoder needs to be replaced. 5.Site has stopped communicating at 14:15 on 02/26 due to ground fuse blown and after tech turned DC and AC power back on and aux cabinet power returned, and communications restored at 11:30 on 02/27. | 1.SR095240 2.SR094675 3.SR094991, SR097738 & SR097867 4.SR096704 5.SR097845 | SR094675 | SR094991 | SR097738 | SR097867 | SR096704 | SR097845
San Juaquin - S. Placer & W. Adams | CA | 527379.5 | 594082.8 | -66703.3 | -11.23% | 562070.1 | -34690.6 | -6.172% | 1.Inverter 6 is being RMA'd due to internal board failure since 12/27/24 and back online at 14:45 on 02/27/25 after tech replaced RMA'd Inverter with new inverter. 2.Site tripped offline at 8:45AM on 02/05 and back online at 11:45AM on 02/07 after tech closed the reclouser and re-enerzised the site. | 1.SR095174, SR095112 2.SR096337 | SR095112 | SR096337
Charlemont - 0 Tea St | MA | 18183 | 294907.1728 | -276724.1728 | -93.83% | 262008.4 | -243825.4 | -93.06% | 1. Inverter was tripping on/off on 02/01 & 02/02 due to contact fault in the DCs.Site was taken offline from 09:50 to 10:20 on 02/04 due to technician checked-in to perform hard resets of all SMA devices,power cycled the inverter at the start/stop switch, all DC/DC combiners were power cycled at the start/stop switch and internal AC breaker later meter stopped communicating from 02/06 to 02/08 but production can be confirmed at inverter level, due to that Actual energy was low. Inverter was offline from 02/13 and back online at 14:05 on 02/19. Site was taken offline from 13:40 to 15:00 on 02/20 due to technician on site to repair the Inverter. Again tripped offline from 02/20 at 15:30 due to AC Separating Point fault till date. 2.Site was offline on 02/18 due to utility outage and back online at 14:05 on 02/19 after technician re-enerzised. | 1.SR096224 2.SR097244
Amherst - 740 Belchertown Rd | MA | 189719 | 310307.2138 | -120588.2138 | -38.86% | 282634 | -92915 | -32.87% | 1.The underperformance is due to a weather event, and no outage events were observed during the month of February.
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 662855 | 626007.4576 | 36847.5424 | 5.886% | 692519 | -29664 | -4.283% | 1. Inverter 2 was taken offline from 3:20 PM to 4:55 PM on 02/19/25 by the PE technician to inspect the PE retrofit snow kit. | 1. SR097528
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 398608 | 592028.3142 | -193420.3142 | -32.67% | 575612 | -177004 | -30.75% | 1. Site was taken offline by Eversource for maintenance work from 02/03/25 to 02/06/25. The utility restored the system each afternoon and took it offline again the next day during this period. 2. Inverter 1 & 2 tripped offline at 02:30PM on 02/06/25 due to a F154:Fb DC Breaker 2 fault. On 02/07/25, the technician went through the recommended PE reset procedure of keying off the inverter, the inverter was keyed back on at 03:15 and was able to clear the fault and begin producing power at the expected rate the same day. 3. Inverter module 4 was offline on 02/20/25. The technician re-enabled module 4 and brought it back online at 12:45 the same day. | 1. SR096254 2. SR096363 3. SR097551 | SR096363 | SR097551

## Mar
AB CarVal |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 4645780.9648 | 6645113.407 | -1999332.4422 | -30.09% | 7624160.3 | -2978379.3352 | -39.07%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA | 323586 | 314641.5225 | 8944.4775 | 2.843% | 318415.1 | 5170.9 | 1.624% | 1.Site tripped offline at 14:40 on 03/13 and back online at 12:15PM on 03/14 after technician reset SEL Relay. | 1.SR098555
Bakersfield - 100 Basic School Rd | CA | 1058174.4362 | 1108865 | -50690.5638 | -4.571% | 1183365 | -125190.5638 | -10.58% | 1.Inverter 1.2 was RMA'D from 02/21 and on 03/21 technician replaced RMA'D inverter with new chint inverter. 2.Inverters 1.1, 2.4, 2.5, 2.6 have consistent late starts on multiple days of the month due to Isolation or ground fault. 3.Tracker Controller 2 Motor 2 is stuck at 8:15AM on 03/03 and back in track at 7:45AM on 03/05. | 1.SR096082 2.SR098340 3.SR097932 | SR098340 | SR097932
Fresno - 2685 Cornelia Ave | CA | 596979 | 1938533 | -1341554 | -69.2% | 2504713 | -1907734 | -76.17% | 1. Inverter 1 has been underproducing by 500 kW compared to Inverter 2 since 03/25/25. On 03/28/25, the technician performed inverter testing and noticed a white sedan with two individuals working on wire maintenance in the array. This may have impacted combiner production, and the underperformance decreased to 200 kW, it requiresadditional troubleshooting. 2. Tracker 3 motor 4 is stuck at 51.83 degrees; setpoint is -52 degrees from 02/02 due to Critical torque tube failure and encoder needs to be replaced. 3. Inverter 3 is offline at 14:30 from 02/24, through out the month due to ground fault and parts being replaced. 4. The site experienced frequent curtailments throughout the month from PG&E. 5. Tracker controller 1 tracker position motor 1 is stuck at -39.20 degrees at 07:45 on 03/31 | 1. SR098969 2. SR096704 3. SR097867, SR097738 4. SR095240, SR098618 5. SR099296 | SR096704 | SR097867 | SR097738 | SR095240 | SR098618 | SR099296
San Juaquin - S. Placer & W. Adams | CA | 807571 | 868882.7 | -61311.7 | -7.056% | 891875.1 | -84304.1 | -9.452% | 1. Inverter 6 was offline from 06:00 AM to 07:00 AM on 03/04 and later self-resolved. 2. Inverters 1 to 5 and 8 to 13 tripped offline from 12:15 PM to 15:45 PM on 03/05 due to a technician being on site. | 1. SR095174 2. SR095174 | SR095174
Charlemont - 0 Tea St | MA | 63339 | 379513.5847 | -316174.5847 | -83.31% | 409585.1 | -346246.1 | -84.54% | 1.Inverter 1 tripped offline at 03:25PM on 02/20 due to AC Separating Point fault and back online at 10:40AM on 03/03 after both ameresco and SMA technicians repaired. Inverter again tripped offline at 12PM on 03/04 due to AC Separating Point fault and back online at 10AM on 03/25 after technician repiared a loose control wire on AC breaker was causing intermittent issues. Inverter was offline from 12:20 to 14:40 due to pilot deployment on 03/27. Again tripped offline at 10AM on 03/31 to finish pending pilot deployment. | 1.SR096224, SR098038 & SR099232 | SR098038 | SR099232
Amherst - 740 Belchertown Rd | MA | 389637 | 393920.5046 | -4283.5046 | -1.087% | 448362 | -58725 | -13.1% | 1.Site tripped offline from 9:25 to 13:55 on 03/13. Due to technician on site | 1.PM10676
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA | 872010.5286 | 854213.7357 | 17796.7929 | 2.083% | 994476 | -122465.4714 | -12.31% | 1.Site was offline from 12:25 to 14:20 on 03/20 due to Utility Outage. | 1.SR098832
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA | 534484 | 786543.3596 | -252059.3596 | -32.05% | 873369 | -338885 | -38.8% | 1.The site was offline from 08:45 AM to 03:35 PM on 03/03 due to a planned utility outage. 2.Site has low production on 03/05, 03/06 , 03/16, 03/17, 03/24,03/30 due to bad weather. | 1. SR097990

## Apr
AB CarVal |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## May
AB CarVal |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Jun
AB CarVal |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Jul
AB CarVal |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Aug
AB CarVal |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Sep
AB CarVal |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Oct
AB CarVal |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Nov
AB CarVal |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Dec
AB CarVal |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Fairhaven - 279 Mill Rd | MA
Bakersfield - 100 Basic School Rd | CA
Fresno - 2685 Cornelia Ave | CA
San Juaquin - S. Placer & W. Adams | CA
Charlemont - 0 Tea St | MA
Amherst - 740 Belchertown Rd | MA
Ludlow - Huxley 1 & 2 - 504 Fuller St | MA
Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA

## Sites
Portfolio: | AB CarVal
Site DAS Name | Site | State | Update | DAS
001 - Fairhaven | MA: Fairhaven - 279 Mill Rd | MA |  | PowerFactors
AFTW Solar - Wheeler | Bakersfield - 100 Basic School Rd | CA | AEF | Also Energy API
Fresno 14MW Solar - CAISO - AB Carval | Fresno - 2685 Cornelia Ave | CA | AEF | Also Energy API
JID - Crystal Farms Local Solar | San Juaquin - S. Placer & W. Adams | CA | AEF | Also Energy API
002 - Charlemont | Charlemont - 0 Tea St | MA |  | PowerFactors
003 - Town of Amherst | Amherst - 740 Belchertown Rd | MA |  | PowerFactors
004 - Huxley | Ludlow - Huxley 1 & 2 - 504 Fuller St | MA |  | PowerFactors
005 - Beacon | Easthampton - Beacon 1 & 2 - 540 Florence Rd | MA |  | PowerFactors