## Year to Date
Bradford - 256 Presidential Dr |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1294062.5886 | 1382229.2395 | -88166.6509 | -6.379% | 1600941.7 | -306879.1114 | -19.17%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bradford - 256 Presidential Dr | MA | 1294062.5886 | 1382229.2395 | -88166.6509 | -6.379% | 1600941.7 | -306879.1114 | -19.17%

## 1st Qtr
Bradford - 256 Presidential Dr |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1294062.5886 | 1382229.2395 | -88166.6509 | -6.379% | 1600941.7 | -306879.1114 | -19.17%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bradford - 256 Presidential Dr | MA | 1294062.5886 | 1382229.2395 | -88166.6509 | -6.379% | 1600941.7 | -306879.1114 | -19.17%

## 2nd Qtr
Bradford - 256 Presidential Dr |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bradford - 256 Presidential Dr | MA | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
Bradford - 256 Presidential Dr |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bradford - 256 Presidential Dr | MA | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Bradford - 256 Presidential Dr |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bradford - 256 Presidential Dr | MA | 0 | 0 | 0 |  | 0 | 0

## Jan
Bradford - 256 Presidential Dr |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 306816.5886 | 339000.3324 | -32183.7438 | -9.494% | 401656.5 | -94839.9114 | -23.61%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA | 306816.5886 | 339000.3324 | -32183.7438 | -9.494% | 401656.5 | -94839.9114 | -23.61% | 1.Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2. Low generation due to rain/snow. | 1.SR096051

## Feb
Bradford - 256 Presidential Dr |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 341831 | 434992 | -93161 | -21.42% | 529201.8 | -187370.8 | -35.41%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA | 341831 | 434992 | -93161 | -21.42% | 529201.8 | -187370.8 | -35.41% | 1.Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2.Inverter 84 was not communicating from 02/02, after tehnician powercycled inverter regained communication on 02/24 at 11:00AM. | 1.SR096051,SR097794 2.SR097657 | SR097794 | SR097657

## Mar
Bradford - 256 Presidential Dr |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 645415 | 608236.9071 | 37178.0929 | 6.112% | 670083.4 | -24668.4 | -3.681%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA | 645415 | 608236.9071 | 37178.0929 | 6.112% | 670083.4 | -24668.4 | -3.681% | 1. Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2. Site had brief outage in between 12:20PM to 12:25PM. But inverters 1 to 4, 42 and 104 was not came back online. Inverters self resolved and started for production on 03/08. 3. Inverters 1 to 55 stopped communicating at 12:45 on 03/14, production not confirmed. On 03/18 technician powercyled DAS and comms were restored. | 1. SR096051,SR097794, SR099300 2. SR098265 3. SR098601 | SR097794 | SR099300 | SR098265 | SR098601

## Apr
Bradford - 256 Presidential Dr |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## May
Bradford - 256 Presidential Dr |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Jun
Bradford - 256 Presidential Dr |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Jul
Bradford - 256 Presidential Dr |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Aug
Bradford - 256 Presidential Dr |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Sep
Bradford - 256 Presidential Dr |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Oct
Bradford - 256 Presidential Dr |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Nov
Bradford - 256 Presidential Dr |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Dec
Bradford - 256 Presidential Dr |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bradford - 256 Presidential Dr | MA |  | 0

## Sites
Portfolio: | Bradford - 256 Presidential Dr
Site DAS Name | Site | State | Update | DAS
006 - Bradford O&M | Bradford - 256 Presidential Dr | MA | AF | PF Drive