## Year to Date
Crawford Realty |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 89024.2499 | 0 | 89024.2499 | 0% | 158659.02 | -69634.7701 | -43.89%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 89024.2499 | 0 | 89024.2499 |  | 158659.02 | -69634.7701 | -43.89%

## 1st Qtr
Crawford Realty |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 89024.2499 | 0 | 89024.2499 | 0% | 158659.02 | -69634.7701 | -43.89%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 89024.2499 | 0 | 89024.2499 |  | 158659.02 | -69634.7701 | -43.89%

## 2nd Qtr
Crawford Realty |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
Crawford Realty |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Crawford Realty |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: Leominster - Crawford Realty | MA | 0 | 0 | 0 |  | 0 | 0

## Jan
Crawford Realty |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 22114.98 | 0 | 22114.98 | 0% | 41708.07 | -19593.09 | -46.98%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 22114.98 | N/A |  |  | 41708.07 | -19593.09 | -46.98% | 1. Inverter 4 stopped communicating at 10:36 AM on 08/16/24 in SolarEdge, currently production cannot be confirmed as the Site expired in AlsoEnergy. The inverter was replaced on 10/18/24. But still not communicating. 2. Low generation due to weather/snow. | 1. SR098937

## Feb
Crawford Realty |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 6301.1099 | 0 | 6301.1099 | 0% | 49081.57 | -42780.4601 | -87.16%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 6301.1099 | N/A |  |  | 49081.57 | -42780.4601 | -87.16% | 1. Inverter 4 stopped communicating at 10:36 AM on 08/16/24 in SolarEdge, currently production cannot be confirmed as the Site expired in AlsoEnergy. The inverter was replaced on 10/18/24. But still not communicating. 2. Low generation due to weather/snow. | 1. SR098937

## Mar
Crawford Realty |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 60608.16 | 0 | 60608.16 | 0% | 67869.38 | -7261.22 | -10.7%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA | 60608.16 | N/A |  |  | 67869.38 | -7261.22 | -10.7% | 1. Inverter 4 stopped communicating at 10:36 AM on 08/16/24 in SolarEdge, currently production cannot be confirmed as the Site expired in AlsoEnergy. The inverter was replaced on 10/18/24. But communication issue still persist, on 03/26 technician updated serial number and inverter comms were restored. 2. Inverter 3 central unit went offline on 03/25 due to an isolation fault. A technician found no visible damage but, after troubleshooting and consulting with Solaredge, suspected that recent heavy rains may have caused water intrusion in one or more MC4 connectors, leading to the fault. Central unit started for production on 03/26. | 1. SR098937 2. SR098962 | SR098962

## Apr
Crawford Realty |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## May
Crawford Realty |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Jun
Crawford Realty |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Jul
Crawford Realty |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Aug
Crawford Realty |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Sep
Crawford Realty |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Oct
Crawford Realty |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Nov
Crawford Realty |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Dec
Crawford Realty |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: Leominster - Crawford Realty | MA |  | 0

## Sites
Portfolio: | Crawford Realty
Site DAS Name | Site | State | Update | DAS
101 Crawford | MA: Leominster - Crawford Realty | MA | AF | PowerTrack