## Year to Date
Lodestar |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 25154290.5705 | 26938175.0585 | -1783884.4879 | -6.622% | 26347828.58 | -1193538.0095 | -4.53%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 440390 | 609848.9 | -169458.9 | -27.79% | 563586.14 | -123196.14 | -21.86%
Bunce | CT | 957913.5 | 899505.1 | 58408.4 | 6.493% | 0 | 0
Norcap North | CT | 1019250 | 1251758.4 | -232508.4 | -18.57% | 1055251.1 | -36001.1 | -3.412%
Norcap South | CT | 1100981.5 | 1343052.7 | -242071.2 | -18.02% | 1008560.7 | 92420.8 | 9.164%
Platt Hill | CT | 946328 | 1233927.8 | -287599.8 | -23.31% | 1268563.1 | -322235.1 | -25.4%
Powder Hill | CT | 997258 | 1126924.1 | -129666.1 | -11.51% | 850246 | 147012 | 17.29%
Sand Road | CT | 1015972 | 1037382.1 | -21410.1 | -2.064% | 930335.2 | 85636.8 | 9.205%
Suffield | CT | 1011980 | 1105331.4 | -93351.4 | -8.446% | 1090180.1 | -78200.1 | -7.173%
Ashby-Duffy | MA | 876865 | 1344846 | -467981 | -34.8% | 999287.5 | -122422.5 | -12.25%
Ashland | MA | 892635 | 1165263.5 | -272628.5 | -23.4% | 1062015.6 | -169380.6 | -15.95%
Barrington | MA | 189205.5 | 142406.05 | 46799.45 | 32.86% | 245659.4 | -56453.9 | -22.98%
Bedford - 205 Burlington Rd | MA | 54600 | 0 | 54600 |  | 0 | 0
Billerica - 6 Cook Street | MA | 47090 | 0 | 47090 |  | 0 | 0
Billerica - 780 Boston Road | MA | 52916 | 0 | 52916 |  | 0 | 0
Cheshire | MA | 188108.0388 | 244473.56 | -56365.5212 | -23.06% | 170701.65 | 17406.3888 | 10.2%
Lilly Lane | MA | 463602.5 | 511452.29 | -47849.79 | -9.356% | 583603 | -120000.5 | -20.56%
Monument Valley | MA | 884487.785 | 433141.68 | 451346.105 | 104.2% | 0 | 380364
Nationwide | MA | 1278264 | 1677477.2 | -399213.2 | -23.8% | 1628612.2 | -350348.2 | -21.51%
Pulpit Hill | MA | 2110386.25 | 2355777.8 | -245391.55 | -10.42% | 2282645.1 | -172258.85 | -7.546%
Sandwich | MA | 1496062 | 0 | 1496062 |  | 1742814 | -246752 | -14.16%
Sturbridge Barn | MA | 482878.5 | 588373.2 | -105494.7 | -17.93% | 606454.8 | -123576.3 | -20.38%
Sturbridge Garage | MA | 236374 | 279553.9 | -43179.9 | -15.45% | 288275.4 | -51901.4 | -18%
Halsey Valley | NY | 2506574 | 2655422.8 | -148848.8 | -5.605% | 2610133 | -103559 | -3.968%
Hunt Creek | NY | 1589666 | 1911885.8 | -322219.8 | -16.85% | 1781389 | -191723 | -10.76%
Smith Creek | NY | 1917529 | 2105655 | -188126 | -8.934% | 2214482.7 | -296953.7 | -13.41%
Bradford - 256 Presidential Dr | MA | 1294062.5 | 1382228.9071 | -88166.4071 | -6.379% | 1600941.7 | -306879.2 | -19.17%
Charlton – 111 Brookfield Road - Bus Lot | MA | 145538 | 128503.3843 | 17034.6157 | 13.26% | 198897.25 | -53359.25 | -26.83%
Charlton – 154 Center Depot Road KMARD | MA | 106050 | 176882.001 | -70832.001 | -40.04% | 192235.16 | -86185.16 | -44.83%
Charlton – 142A Brookfield Rd (Mitchell) | MA | 139150 | 187579.0295 | -48429.0295 | -25.82% | 200400.58 | -61250.58 | -30.56%
Great Barrington – 3 Nolan Drive | MA | 250735.4967 | 358533.4373 | -107797.9406 | -30.07% | 397534.78 | -146799.2833 | -36.93%
Stockbridge – 92 State Line Road Truck Stop | MA | 461438 | 680989.0193 | -219551.0193 | -32.24% | 775023.42 | -313585.42 | -40.46%

## 1st Qtr
Lodestar |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 16452264.0705 | 19010660.0585 | -2558395.9879 | -13.46% | 18375451.88 | -1923187.8095 | -10.47%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 268344 | 421750.9 | -153406.9 | -36.37% | 378669.74 | -110325.74 | -29.14%
Bunce | CT | 601753.5 | 684621.1 | -82867.6 | -12.1% | 0 | 0
Norcap North | CT | 665544 | 901318.4 | -235774.4 | -26.16% | 696719.6 | -31175.6 | -4.475%
Norcap South | CT | 722340.5 | 975622.9 | -253282.4 | -25.96% | 656577.7 | 65762.8 | 10.02%
Platt Hill | CT | 558121 | 824707.8 | -266586.8 | -32.33% | 857153.4 | -299032.4 | -34.89%
Powder Hill | CT | 636559 | 764818.1 | -128259.1 | -16.77% | 566964 | 69595 | 12.28%
Sand Road | CT | 629363 | 693953.2 | -64590.2 | -9.308% | 602989 | 26374 | 4.374%
Suffield | CT | 646808 | 747386.4 | -100578.4 | -13.46% | 728845.7 | -82037.7 | -11.26%
Ashby-Duffy | MA | 531938 | 986411 | -454473 | -46.07% | 648393.4 | -116455.4 | -17.96%
Ashland | MA | 531484 | 790545.5 | -259061.5 | -32.77% | 680224.1 | -148740.1 | -21.87%
Barrington | MA | 112260.5 | 75219.05 | 37041.45 | 49.24% | 159190 | -46929.5 | -29.48%
Bedford - 205 Burlington Rd | MA | 54600 | 0 | 54600 |  | 0 | 0
Billerica - 6 Cook Street | MA | 47090 | 0 | 47090 |  | 0 | 0
Billerica - 780 Boston Road | MA | 52916 | 0 | 52916 |  | 0 | 0
Cheshire | MA | 105971.0388 | 161225.96 | -55254.9212 | -34.27% | 105817.65 | 153.3888 | 0.145%
Lilly Lane | MA | 287612.5 | 337821.29 | -50208.79 | -14.86% | 405645 | -118032.5 | -29.1%
Monument Valley | MA | 504123.785 | 150513.18 | 353610.605 | 234.9% | 0 | 0
Nationwide | MA | 727663 | 1141247.2 | -413584.2 | -36.24% | 1092285.2 | -364622.2 | -33.38%
Pulpit Hill | MA | 1299577.25 | 1581139.1 | -281561.85 | -17.81% | 1505519.1 | -205941.85 | -13.68%
Sandwich | MA | 953865 | 0 | 953865 |  | 1158752 | -204887 | -17.68%
Sturbridge Barn | MA | 306719.5 | 405365.2 | -98645.7 | -24.34% | 415888.3 | -109168.8 | -26.25%
Sturbridge Garage | MA | 150401.5 | 193175.9 | -42774.4 | -22.14% | 200379.4 | -49977.9 | -24.94%
Halsey Valley | NY | 1532926 | 1689825.8 | -156899.8 | -9.285% | 1609000 | -76074 | -4.728%
Hunt Creek | NY | 937590 | 1217312.3 | -279722.3 | -22.98% | 1067900 | -130310 | -12.2%
Smith Creek | NY | 1189719 | 1351964 | -162245 | -12% | 1473505.7 | -283786.7 | -19.26%
Bradford - 256 Presidential Dr | MA | 1294062.5 | 1382228.9071 | -88166.4071 | -6.379% | 1600941.7 | -306879.2 | -19.17%
Charlton – 111 Brookfield Road - Bus Lot | MA | 145538 | 128503.3843 | 17034.6157 | 13.26% | 198897.25 | -53359.25 | -26.83%
Charlton – 154 Center Depot Road KMARD | MA | 106050 | 176882.001 | -70832.001 | -40.04% | 192235.16 | -86185.16 | -44.83%
Charlton – 142A Brookfield Rd (Mitchell) | MA | 139150 | 187579.0295 | -48429.0295 | -25.82% | 200400.58 | -61250.58 | -30.56%
Great Barrington – 3 Nolan Drive | MA | 250735.4967 | 358533.4373 | -107797.9406 | -30.07% | 397534.78 | -146799.2833 | -36.93%
Stockbridge – 92 State Line Road Truck Stop | MA | 461438 | 680989.0193 | -219551.0193 | -32.24% | 775023.42 | -313585.42 | -40.46%

## 2nd Qtr
Lodestar |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 0 | 0 | 0 |  | 0 | 0
Bunce | CT | 0 | 0 | 0 |  | 0 | 0
Norcap North | CT | 0 | 0 | 0 |  | 0 | 0
Norcap South | CT | 0 | 0 | 0 |  | 0 | 0
Platt Hill | CT | 0 | 0 | 0 |  | 0 | 0
Powder Hill | CT | 0 | 0 | 0 |  | 0 | 0
Sand Road | CT | 0 | 0 | 0 |  | 0 | 0
Suffield | CT | 0 | 0 | 0 |  | 0 | 0
Ashby-Duffy | MA | 0 | 0 | 0 |  | 0 | 0
Ashland | MA | 0 | 0 | 0 |  | 0 | 0
Barrington | MA | 0 | 0 | 0 |  | 0 | 0
Bedford - 205 Burlington Rd | MA | 0 | 0 | 0 |  | 0 | 0
Billerica - 6 Cook Street | MA | 0 | 0 | 0 |  | 0 | 0
Billerica - 780 Boston Road | MA | 0 | 0 | 0 |  | 0 | 0
Cheshire | MA | 0 | 0 | 0 |  | 0 | 0
Lilly Lane | MA | 0 | 0 | 0 |  | 0 | 0
Monument Valley | MA | 0 | 0 | 0 |  | 0 | 0
Nationwide | MA | 0 | 0 | 0 |  | 0 | 0
Pulpit Hill | MA | 0 | 0 | 0 |  | 0 | 0
Sandwich | MA | 0 | 0 | 0 |  | 0 | 0
Sturbridge Barn | MA | 0 | 0 | 0 |  | 0 | 0
Sturbridge Garage | MA | 0 | 0 | 0 |  | 0 | 0
Halsey Valley | NY | 0 | 0 | 0 |  | 0 | 0
Hunt Creek | NY | 0 | 0 | 0 |  | 0 | 0
Smith Creek | NY | 0 | 0 | 0 |  | 0 | 0
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## 3rd Qtr
Lodestar |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 8702026.5 | 7927515 | 774511.5 | 9.77% | 7972376.7 | 729649.8 | 9.152%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 172046 | 188098 | -16052 | -8.534% | 184916.4 | -12870.4 | -6.96%
Bunce | CT | 356160 | 214884 | 141276 | 65.75% | 0 | 0
Norcap North | CT | 353706 | 350440 | 3266 | 0.932% | 358531.5 | -4825.5 | -1.346%
Norcap South | CT | 378641 | 367429.8 | 11211.2 | 3.051% | 351983 | 26658 | 7.574%
Platt Hill | CT | 388207 | 409220 | -21013 | -5.135% | 411409.7 | -23202.7 | -5.64%
Powder Hill | CT | 360699 | 362106 | -1407 | -0.3886% | 283282 | 77417 | 27.33%
Sand Road | CT | 386609 | 343428.9 | 43180.1 | 12.57% | 327346.2 | 59262.8 | 18.1%
Suffield | CT | 365172 | 357945 | 7227 | 2.019% | 361334.4 | 3837.6 | 1.062%
Ashby-Duffy | MA | 344927 | 358435 | -13508 | -3.769% | 350894.1 | -5967.1 | -1.701%
Ashland | MA | 361151 | 374718 | -13567 | -3.621% | 381791.5 | -20640.5 | -5.406%
Barrington | MA | 76945 | 67187 | 9758 | 14.52% | 86469.4 | -9524.4 | -11.01%
Bedford - 205 Burlington Rd | MA | 0 | 0 | 0 |  | 0 | 0
Billerica - 6 Cook Street | MA | 0 | 0 | 0 |  | 0 | 0
Billerica - 780 Boston Road | MA | 0 | 0 | 0 |  | 0 | 0
Cheshire | MA | 82137 | 83247.6 | -1110.6 | -1.334% | 64884 | 17253 | 26.59%
Lilly Lane | MA | 175990 | 173631 | 2359 | 1.359% | 177958 | -1968 | -1.106%
Monument Valley | MA | 380364 | 282628.5 | 97735.5 | 34.58% | 0 | 380364
Nationwide | MA | 550601 | 536230 | 14371 | 2.68% | 536327 | 14274 | 2.661%
Pulpit Hill | MA | 810809 | 774638.7 | 36170.3 | 4.669% | 777126 | 33683 | 4.334%
Sandwich | MA | 542197 | 0 | 542197 |  | 584062 | -41865 | -7.168%
Sturbridge Barn | MA | 176159 | 183008 | -6849 | -3.742% | 190566.5 | -14407.5 | -7.56%
Sturbridge Garage | MA | 85972.5 | 86378 | -405.5 | -0.4694% | 87896 | -1923.5 | -2.188%
Halsey Valley | NY | 973648 | 965597 | 8051 | 0.8338% | 1001133 | -27485 | -2.745%
Hunt Creek | NY | 652076 | 694573.5 | -42497.5 | -6.119% | 713489 | -61413 | -8.607%
Smith Creek | NY | 727810 | 753691 | -25881 | -3.434% | 740977 | -13167 | -1.777%
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## 4th Qtr
Lodestar |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Barkhamsted | CT | 0 | 0 | 0 |  | 0 | 0
Bunce | CT | 0 | 0 | 0 |  | 0 | 0
Norcap North | CT | 0 | 0 | 0 |  | 0 | 0
Norcap South | CT | 0 | 0 | 0 |  | 0 | 0
Platt Hill | CT | 0 | 0 | 0 |  | 0 | 0
Powder Hill | CT | 0 | 0 | 0 |  | 0 | 0
Sand Road | CT | 0 | 0 | 0 |  | 0 | 0
Suffield | CT | 0 | 0 | 0 |  | 0 | 0
Ashby-Duffy | MA | 0 | 0 | 0 |  | 0 | 0
Ashland | MA | 0 | 0 | 0 |  | 0 | 0
Barrington | MA | 0 | 0 | 0 |  | 0 | 0
Bedford - 205 Burlington Rd | MA | 0 | 0 | 0 |  | 0 | 0
Billerica - 6 Cook Street | MA | 0 | 0 | 0 |  | 0 | 0
Billerica - 780 Boston Road | MA | 0 | 0 | 0 |  | 0 | 0
Cheshire | MA | 0 | 0 | 0 |  | 0 | 0
Lilly Lane | MA | 0 | 0 | 0 |  | 0 | 0
Monument Valley | MA | 0 | 0 | 0 |  | 0 | 0
Nationwide | MA | 0 | 0 | 0 |  | 0 | 0
Pulpit Hill | MA | 0 | 0 | 0 |  | 0 | 0
Sandwich | MA | 0 | 0 | 0 |  | 0 | 0
Sturbridge Barn | MA | 0 | 0 | 0 |  | 0 | 0
Sturbridge Garage | MA | 0 | 0 | 0 |  | 0 | 0
Halsey Valley | NY | 0 | 0 | 0 |  | 0 | 0
Hunt Creek | NY | 0 | 0 | 0 |  | 0 | 0
Smith Creek | NY | 0 | 0 | 0 |  | 0 | 0
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Jan
Lodestar |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 3838099.3873 | 5382433.8674 | -1544334.4801 | -28.69% | 4641331.91 | -803232.5227 | -17.31%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 42488 | 130906.1 | -88418.1 | -67.54% | 95618.24 | -53130.24 | -55.56% | 1. Combiner Boxes 1.2 (DCP 1), 1.3 (DCP 7), 1.5 (DCP 14), 1.7 (DCP 10), 1.10 (DCP 4), 1.11 (DCP 11), and 1.15 (DCP 12) have been offline since 12/22/24. On 01/02/25, the technician discovered blown glass fuses. As per Shoals' instructions, parts are needed to bring them back online, and they have remained offline throughout the month. 2. Combiner 1.14 (DCP-3) is showing constant value of 312Amps from 08/30 due to a faulty CT. 3. All inverters tripped on and off on 01/09 and 01/10, with Inverter 1.5 tripped offline at 10:30 AM on 01/09. On 01/11, the PE technician restored only Inverter 1.1, while the others remained offline. On 01/13, the PE technician worked on all inverters, brought Inverter 1.5 back online at 16:30. The remaining inverters were restored on 01/14/25. | 1.SR095215 2.SR089788 3.SR095444
Bunce | CT | 147884 | 196766.8 | -48882.8 | -24.84% | N/A |  |  | 1. Inverters 10,11 and 13 are started late for production at 11:45AM on 01/17 due to insulation fault. 2. Low generation due to rain/snow. | 1. SR095646
Norcap North | CT | 162639 | 288186.5 | -125547.5 | -43.56% | 178945.5 | -16306.5 | -9.113% | 1. Inverter 12 came back online at 13:30 on 01/02. The technician investigated the issue and cleared the fault. 2. Inverters 14 to 17 tripped offline at 11:45AM on 01/26. The technician replaced the shunt trip for HP1 with HP4. The inverters came back online at 11:15AM on 01/27. 3. Inverter 25 has been intermittently offline for the whole month due to a bus differential fault. Solectria has issued an RMA for the inverter. 4. Inverter 30 started production late at 13:15 on 01/27. The technician resolved the issue with Solectria. Solectria will issue an RMA if the inverter trips again. | 1. SR095170 2. SR095990 3. SR096190, SR094843 4. SR096007
Norcap South | CT | 184293.5 | 319084.7 | -134791.2 | -42.24% | 155781 | 28512.5 | 18.3% | 1.Inverter 36 offline on 01/01 due to insulation resistance fault and self resolve on 01/02 2. Low generation due to rain/snow. | 1.SR095132
Platt Hill | CT | 115129.745 | 228108.9 | -112979.155 | -49.53% | 231339.2 | -116209.455 | -50.23% | 1. The site tripped offline at 10:45AM on 01/03 and came back online at 07:00 AM on 01/06. The technician found that the surge protector breaker had tripped and reset it. 2. The site tripped offline at 05:45AM on 01/16 while the technician was onsite to remove the failed breaker. The site came back online at 08:30AM on 01/17 after the breaker was replaced. 3.Inverter 1 has started late for the production at 12:00 on 01/17 but two strings are kept offline for safety due to tree has felt on array | 1. SR095275 2. SR095529 3.SR095652
Powder Hill | CT | 157653 | 225761.3 | -68108.3 | -30.17% | 155676 | 1977 | 1.27% | 1. Inverter 7 started production late and later self-resolved at 09:15 AM on 01/13 due to a self-check startup failure. It failed to start again on 01/17 but was brought back online via a remote reset at 10:45 AM the same day. However, it tripped offline again at 11:15 AM on 01/27. The technician investigated the issue, and Inverter 7 was back online at 07:00 AM and 3 CT's were RMA'd on 01/28. 2. Inverter 8 dropped offline at 11:45 AM and was producing only 5 kW consistently. After a remote reset, the inverter came back online at 13:45 on 01/28. 3. Low generation due to rain/snow. | 1. SR095513 2. SR095081
Sand Road | CT | 151595 | 198096.8 | -46501.8 | -23.47% | 145302 | 6293 | 4.331% | 1. Site offline at 15:30 on 01/18. Technician found the Main AC Breaker tripped and the SEL-751 in the trip position with an "AC Loss" fault. Reset both the SEL and Main AC Breaker. The site is back online at 12:45 on 01/19. 2. Low generation due to rain/snow. | 1. SR095701
Suffield | CT | 177443 | 223979.4 | -46536.4 | -20.78% | 190993.6 | -13550.6 | -7.095% | 1. Low generation due to rain/snow.
Ashby-Duffy | MA | 153090 | 301950.1 | -148860.1 | -49.3% | 157476.5 | -4386.5 | -2.785% | 1. Inverter 2 remains offline for the whole month and will need to wait until the ground is unfrozen. 2. Inverter 55 tripped offline at 11:15 AM on 01/03 due to an electrical arc fault. After a reset, the inverter came back online at 10:30 AM on 01/06. 3. Inverter 54 tripped offline at 12:45 on 01/03 due to a high residual current. The technician found a field-made jumper connection with thermal damage. The MC M/F connectors were repaired and replaced. The inverter came back online at 10:30 on 01/06. 4.Inverter 39 string 5 blown a fuse and later technician replaced fuses on 01/15 5. Low generation due to rain/snow. | 1. SR093777 2. SR095277 3. SR095288 4.SR094302
Ashland | MA | 125168.5 | 243462.5 | -118294 | -48.59% | 133620.2 | -8451.7 | -6.325% | 1. Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 2. Inverter 30 tripped offline at 13:45 on 01/12 due to an insulation fault and later self-resolved, inverter back online at 14:15. 3.Inverter 66 tripped offline at 11:00 AM on 01/06 and self-resolved, inverter back online at 07:00 AM on 01/08. 4. Inverter 12 was offline intermittently whole month and being RMA'd. 5. Inverter 67 was being in RMA'd. 6. Inverter 57 was being in RMA'd. 7.Inverter 66 is bearly producing from 01/30 8. Low generation due to rain/snow. | 1. SR095816 2. SR095504 3. SR094685 4. SR093117 5. SR088450 6. SR091962 7.SR096271
Barrington | MA | 21905.5 | 31381.54 | -9476.04 | -30.2% | 35820 | -13914.5 | -38.85% | 1. Low generation due to weather/snow.
Bedford - 205 Burlington Rd | MA | 12393 | N/A |  |  | N/A
Billerica - 6 Cook Street | MA | 9769 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 10676 | N/A |  |  | N/A
Cheshire | MA | 20350.2064 | 43079.92 | -22729.7136 | -52.76% | 24192.56 | -3842.3536 | -15.88% | 1. Low generation due to rain/snow.
Lilly Lane | MA | 66477 | 93441.89 | -26964.89 | -28.86% | 112568.7 | -46091.7 | -40.95% | 1. Inverter 61 has been intermittently offline throughout the month and has been RMA'd. 2. The site tripped offline at 18:00 on 01/02. The technician found that the switchgear was open and the SEL-351A had tripped. He reset the SEL and closed the switchgear. The site came back online at 09:00 AM on 01/03. | 1. SR095846, SR095210 2. SR095259
Monument Valley | MA | 92298 | 36912.89 | 55385.11 | 150% | N/A |  |  | 1. Site production dropped at 15:15 on 01/28 as Sungrow technicians were onsite working on BESS. They continued work on 01/29, and production returned to normal at 15:30 on 01/29. 2. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1. SR092970 2. SR087370
Nationwide | MA | 149646 | 334678.8 | -185032.8 | -55.29% | 297479.6 | -147833.6 | -49.7% | 1. Inverter 16 tripped offline at 08:45AM on 01/19, inverter was self-resolved at 10:15AM on 01/21. 2. Low generation due to rain/snow. | 1. SR095712
Pulpit Hill | MA | 316117.75 | 470954.2 | -154836.45 | -32.88% | 355177.1 | -39059.35 | -11% | 1. Inverter 83 had a string 8 down since 11/27. It will be investigated during the next onsite visit. 2. Inverter 49 did not start production on 01/26. The technician investigated and found that the inverter was online but not communicating due to a Fault Protect 0130/090. Solectria will issue an RMA for the power head. The inverter has been tagged out and de-energized. 3. Inverter 42 did not start production on 01/29 reporting Bus Differential Fault. Technician investigated and found that the inverter was online but not communicating. Solectria processed an RMA. 4. Low generation due to rain/snow. | 1. SR093591 2. SR095984 3. SR096108
Sandwich | MA | 284645 | N/A |  |  | 295751 | -11106 | -3.755% | 1. PAD 4 is discharging at 15kW and CES performed calibration on 01/02. 2. The site was taken offline from 8:45 to 15:15 on 01/17 for SIM replacement. Afterward, the technician requested tech support to check production reporting issues on meters 3 and 4. AlsoEnergy confirmed PowerTrack settings were consistent across HEILA BESS Controllers 2, 3, and 4, indicating the issue is likely with the controllers. HEILA will now inspect remotely using the new SIM. | 1.SR095262 2.SR095545
Sturbridge Barn | MA | 75410.5 | 125791.1 | -50380.6 | -40.05% | 110058.4 | -34647.9 | -31.48% | 1. Site tripped offline and SEL Relay was opened on 01/02 at 18:00 later technician re-energized the relay at 08:15am on 01/03 2.Inverter 32 tripped offline at 13:30 on 01/25 due to "ARC Protection", later technician found and replaced rusty homerun MC connectors, and the inverter came back online at 10:30 on 01/27. 3. Low generation due to rain/snow. | 1.SR095261 2.SR095978
Sturbridge Garage | MA | 36683.75 | 59181.43 | -22497.68 | -38.01% | 55606.07 | -18922.32 | -34.03% | 1.Inverter 3 tripped offline at 12PM on 01/02 due to Bus(sum) over voltage fault and back online on 01/04. On 01/23 Technicians checked in and replaced RMA'd Inverter with new Inverter. Inverter was again offline from 01/24 due to stuck in standby mode and back online at 12PM on 01/27. 2.Site tripped offline at 17:48 and on battery mode, later auto-reclosed at 18:10 on 01/02. 3.Inverter 8 tripped offline at 10:30AM on 01/12 due to insulation resistance low fault and back online at 11:30AM on 01/13. 4. Low generation due to rain/snow. | 1.SR093378, SR096015 2.SR095260 3.SR095505
Halsey Valley | NY | 352603 | 438815.8 | -86212.8 | -19.65% | 384000 | -31397 | -8.176% | 1.Inverter 13 was offline from 12/20/24 due to insulation resistance low fault and after technician powered on, inverter back online at 9:30AM on 01/16/25. 2.Inverter 18, string 4 in CB18, was isolated due to poor voltage and a disconnected module caused by severe dirt and ice buildup in the MC4 connections. After inspection on 01/16, the technician replaced both MC4 connectors, reconnected the circuit, and powered on the inverter. It is now performing in line with its peers. 3. Low generation due to rain/snow. | 1.SR094997 2.SR094509
Hunt Creek | NY | 155889 | 294214.5 | -138325.5 | -47.02% | 228700 | -72811 | -31.84% | 1. Inverter 18 has multiple tripping events from 12/06/24 due to Floating capacitor voltage is high. 2.Site tripped offline at 07:00AM and after technician checked-in, site back online at 11:45 on 01/06. 3.Site tripped offline at 06:30AM and after technician closed the SEL Relay, site back online at 11:15 on 01/22. Inverters 2,3,4,5,6,8,10,14,15,16,17,19,22,25,27,28 and 29 are tripped offline at 09:15AM on 01/21 due to Grid Voltage unbalance and back online at 11:15AM on 01/22. 4.Inverters 5,23 and 27 tripped offline at 13:30 on 01/24 due to Grid voltage unbalance and back online on 01/25. 5. Low generation due to rain/snow. | 1.SR094254 2.SR093451 3.SR095801 4.SR095965
Smith Creek | NY | 264193 | 337115.3 | -72922.3 | -21.63% | 398598.4 | -134405.4 | -33.72% | 1.Site was taken offline from 10:45 to 16:45 on 01/06 due to technincian checked-in for hot spot remediation. 2. Inverters 1,3,6,12 and 27 tripped offline at 9:15AM on 01/21 due to Grid voltage unbalance and back online at 14:00 on 01/22. Site tripped offline at 06:30AM and after technician closed the SEL Relay, site back online at 14:00 on 01/22. | 1.SR095332 2.SR095805
Bradford - 256 Presidential Dr | MA | 306816.5 | 339000 | -32183.5 | -9.494% | 401656.5 | -94840 | -23.61% | 1.Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2. Low generation due to rain/snow. | 1.SR096051
Charlton – 111 Brookfield Road - Bus Lot | MA | 36616 | 27710.0996 | 8905.9004 | 32.14% | 56965.72 | -20349.72 | -35.72% | 1. Site stopped communicating at 1:25AM on 01/29 and on 03/31 technician powercycled the DAS comms were restored. 2. Low generation due to rain/snow. | 1. SR096103
Charlton – 154 Center Depot Road KMARD | MA | 31310 | 53271.4949 | -21961.4949 | -41.23% | 54358.81 | -23048.81 | -42.4% | 1. Low generation due to weather/snow.
Charlton – 142A Brookfield Rd (Mitchell) | MA | 35707.4359 | 52376.025 | -16668.5891 | -31.82% | 57257.31 | -21549.8741 | -37.64% | 1. Site lost communication on 01/10 and comms were back on 01/16 after technician powercycled DAS. 2. Low generation due to rain/snow. | 1. SR095421
Great Barrington – 3 Nolan Drive | MA | 55040 | 97230.9306 | -42190.9306 | -43.39% | 112112.88 | -57072.88 | -50.91% | 1. Low generation due to weather/snow.
Stockbridge – 92 State Line Road Truck Stop | MA | 86169 | 190974.8474 | -104805.8474 | -54.88% | 216276.62 | -130107.62 | -60.16% | 1. Low generation due to weather/snow.

## Feb
Lodestar |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 4097242.2184 | 5706989.1617 | -1609746.9433 | -28.21% | 5844278.04 | -1747035.8216 | -29.89%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 65600 | 127981.8 | -62381.8 | -48.74% | 118820.5 | -53220.5 | -44.79% | 1. Combiner Boxes 1.2 (DCP 1), 1.3 (DCP 7), 1.5 (DCP 14), 1.7 (DCP 10), 1.10 (DCP 4), 1.11 (DCP 11), and 1.15 (DCP 12) have been offline since 12/22. On 02/10, technician refitted them with a new contactor. Except for 1.2 (DCP 1), all combiner boxes came back online at 12:15 PM. 2. Low generation due to weather/snow. | 1.SR095215
Bunce | CT | 152247 | 205046.7 | -52799.7 | -25.75% | N/A |  |  | 1.Site was taken offline from 13:00 to 14:45 on 02/22 due to planned outage. 2. The site is experiencing multiple trips due to voltage fluctuations. Whenever the meter voltage drops below 610V, the site trips, and when the voltage returns to the nominal value, the site comes back online. This phenomenon has been occurring since Eversource performed maintenance on 02/22. Site production returned to normal on 02/27 after Eversource was dispatched on 02/26. | 1.SR097327 2.SR097832 | SR097832
Norcap North | CT | 196301.5 | 283245.5 | -86944 | -30.7% | 212347.1 | -16045.6 | -7.556% | 1.Inverter 25 experienced multiple offline incidents throughout the month due to a bus differential high fault and was subsequently RMA'd by Solectria. On 02/26, technicians replaced the RMA'd inverter with a new unit and inverter started producing in line with its peers. 2. Inverter 1 was offline on 02/16 and 02/17 due to a bus differential high fault and came back online on 02/18. It went offline again from 02/20 to 02/23 and on 02/27 and 02/28 due to the same fault. Solectria initiated the RMA process for the inverter on 02/21. 3. Low generation due to rain/snow. | 1.SR096190 2.SR097171, SR097549 & SR097792 | SR097171 | SR097549 | SR097792
Norcap South | CT | 217072.5 | 306757.9 | -89685.4 | -29.24% | 202120.5 | 14952 | 7.398% | 1. Inverter 36 started late for production on 02/01, 02/04, 02/07 and was offline on 02/13 & 02/27 due to Insulation Resistance Low fault. Self-resolved on 02/28. 2. Low generation due to rain/snow. | 1.SR096465
Platt Hill | CT | 142609.255 | 252288 | -109678.745 | -43.47% | 273596.9 | -130987.645 | -47.88% | 1.Site was tripped offline at 13:30 on 02/04 due to main breaker trip and back online at 10:30 on 02/05 after tehnician closed the breaker. Again site tripped offline at 20:00 on 02/16 and after technician reset main breaker site back online at 11:30 on 02/18. 2. Low generation due to rain/snow. | 1.SR096295
Powder Hill | CT | 173406 | 236232.6 | -62826.6 | -26.6% | 178140 | -4734 | -2.657% | 1.Site was tripped offline on battery mode from 12:45 to 13:30 on 02/07. 2.Three CT's of inverter 7 were RMA'd from 01/28. Received parts and need to dispatch. | 1.SR096471 2.SR095513 | SR095513
Sand Road | CT | 157864 | 194906.2 | -37042.2 | -19.01% | 179737 | -21873 | -12.17% | 1.Site was taken offline from 10:45 to 11:45 on 02/21 due to technicians checked in to collect DGA samples. 2.Site stopped communicating at 12PM on 02/22 and back online at 08:15 on 02/23 after technician reset main breaker and SEL relay. 3.Inverter 9 started late for production at 13:00 on 02/27 due to insulation Fault. | 1.SR097562 2.SR097648 3.SR097870 | SR097648 | SR097870
Suffield | CT | 160474 | 229753.5 | -69279.5 | -30.15% | 221930.9 | -61456.9 | -27.69% | 1.On 02/26, the technician replaced CB 14's String 9 (faulty) and String 13 (open circuit). 2. Low generation due to rain/snow | 1.SR089923, SR090122 | SR090122
Ashby-Duffy | MA | 85456 | 296805.6 | -211349.6 | -71.21% | 209076.1 | -123620.1 | -59.13% | 1.Inverter 2 was offline since 12/19 and will remains offline until the ground is unfrozen. 2.Inverter 39 string 5 blew a fuse and requires underground wiring replacement. Work will be scheduled once the ground thaws. 3. Low generation due to rain/snow. | 1. SR093777,SR097797 2.SR094302, SR097796 | SR097797 | SR094302 | SR097796
Ashland | MA | 115560 | 235192.7 | -119632.7 | -50.87% | 225868 | -110308 | -48.84% | 1.Inverter 49 was being RMA'D since 10/16/23. 2.Inverter 67 was being RMA'd. 3.Inverter 57 was being RMA'd. 4.Inverter 12 was offline intermittently whole month and being RMA'd. 5.Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 6.Inverter 66 is bearly producing due to protect 0260 fault from 01/30 and back to normal after technician replaced MC4 connectors that were causing arc fault on 02/04. 7.Inverter 21 was offline on 02/06 due to ARC Protection fault and back online at 11:45 on 02/07 after technician replaced blown DC fuse and fuse holders. 8.Inverter 24 has multiple trip events through out the month due to Insulation Resistance Low fault. 9. Low generation due to rain/snow. | 1.SR088449 2.SR088450 3.SR091962 4.SR093117, SR097799 5.SR095816 6.SR096271 7.SR096370 8.SR097060 | SR088450 | SR091962 | SR093117 | SR097799 | SR095816 | SR096271 | SR096370 | SR097060
Barrington | MA | 22100 | 27320.93 | -5220.93 | -19.11% | 54460 | -32360 | -59.42% | 1. Low generation due to rain/snow.
Bedford - 205 Burlington Rd | MA | 6760 | N/A |  |  | N/A
Billerica - 6 Cook Street | MA | 5612 | N/A |  |  | N/A
Billerica - 780 Boston Road | MA | 6214 | N/A |  |  | N/A |  |  | 1.Inverter 4 was offline on 02/27 due to Insulation resistance too low fault and resumed production at 13:40 on 02/28. | 1.SR097899
Cheshire | MA | 16209.0436 | 46433.28 | -30224.2364 | -65.09% | 34106.99 | -17897.9464 | -52.48% | 1. Low generation due to rain/snow.
Lilly Lane | MA | 70582.5 | 102338.9 | -31756.4 | -31.03% | 133421.2 | -62838.7 | -47.1% | 1.Inverter 61 was being RMA'd from 01/22. 2.Inverter 67 was offline from 11:15 to 15:30 on 02/17 due to a grid over-frequency fault. On 02/26, it went offline again due to an insulation resistance low fault. The technician repaired broken MC4 connectors and cleared an arc fault, restoring the inverter online at 13:45 on 02/27. 3.On 02/24, Inverter 69 was offline due to an insulation resistance low fault. The technician repaired the jumper cable and ensured sufficient slack, restoring the inverter online at 14:30 on 02/24. 4.Inverter 50 was offline on 02/25 due to Insulation resistance low fault and back online at 13:15 on 02/26 after technician cleared the arc fault and repaired the bad MC4 connections. 5. Low generation due to rain/snow. | 1.SR095846, SR097795 2.SR097191 3.SR097690 4.SR097747 | SR097795 | SR097191 | SR097690 | SR097747
Monument Valley | MA | 117707.1058 | 46997.43 | 70709.6758 | 150.5% | N/A |  |  | 1.Site was taken offline from 8:00 to 9:15 on 02/21. Technicians was onsite to collect DGA samples. 2. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1.SR097561 2. SR087370 | SR087370
Nationwide | MA | 52369 | 335928.3 | -283559.3 | -84.41% | 339349.6 | -286980.6 | -84.57% | 1. Inverter 13 was offline on 02/27 and back online on 02/28. 2. Low generation due to rain/snow. | 1.SR097881
Pulpit Hill | MA | 334214.25 | 482625.5 | -148411.25 | -30.75% | 489731.3 | -155517.05 | -31.76% | 1.Inverter 83 had a string 8 down since 11/27. It will be investigated during the next onsite visit. 2.Inverter 49 did not start production on 01/26. The technician investigated and found that the inverter was online but not communicating due to a Fault Protect 0130/090. Solectria will issue an RMA for the power head. The inverter has been tagged out and de-energized. 3. Inverter 42 did not start production on 01/29 reporting Bus Differential Fault. Technician investigated and found that the inverter was online but not communicating. Solectria processed an RMA. 4. Low generation due to rain/snow. | 1.SR093591, SR097798 2.SR095984 3.SR096108, SR097793 | SR097798 | SR095984 | SR096108 | SR097793
Sandwich | MA | 315624 | N/A |  |  | 367963 | -52339 | -14.22% | 1.Inverters on Pad 4 are all showing some ground/communication faults within the XGI portal from 02/11 and self resolved on 02/24. 2.On 2/20, Pad 1&4 are showing active fault. Later pad 1 got self- resolved and Pad 4 was reset by CES. 3.On 02/20, the technician checked in to take DC measurements on Pad 4 but had to check out due to inclement weather. On 02/24, the technician returned to troubleshoot incorrect meter values for Pad 4 caused by damaged conductor insulation and a loose terminal jumper near the Verivolt IsoBlock. The technician repaired the damage, restored the connection, and confirmed correct voltage and amperage readings on the Pad 4 meter. The technician also discovered that Pad 3's Power Limiting factor was set to 81.4% instead of 100%. With CES' approval, the setting was adjusted to 100%, increasing inverter output to 166kW. The technician then power cycled the Pad 3 Heila Controller and worked with CES to reset site mode settings, restoring automatic system dispatch. The technician monitored the site for 30 minutes to confirm normal operation. | 1.SR096680 2.SR097547 3.SR095262 | SR097547 | SR095262
Sturbridge Barn | MA | 77009 | 121747.9 | -44738.9 | -36.75% | 133486.9 | -56477.9 | -42.31% | 1.Inverter 32 was offline on 02/14 due to an ARC protection fault and came back online at 13:15 on 02/19 after a technician swapped the ARC board between Inverters 31 and 32 to check if the fault followed the board. Both inverters are online and producing. 2.Site tripped offline and was on battery mode at 11:00 on 02/17 and back online at 10:30 on 02/18 after technician closed the reclosure. 3. Low generation due to rain/snow. | 1.SR097066 2.SR097198 | SR097198
Sturbridge Garage | MA | 36142.5 | 58118.59 | -21976.09 | -37.81% | 65907.13 | -29764.63 | -45.16% | 1. Low generation due to weather/snow.
Halsey Valley | NY | 433614 | 486830.4 | -53216.4 | -10.93% | 528000 | -94386 | -17.88% | 1. Low generation due to weather/snow.
Hunt Creek | NY | 238580 | 348340.5 | -109760.5 | -31.51% | 340300 | -101720 | -29.89% | 1. Inverter 27 was tripped offline from 9AM to 10:45AM on 02/17 due to Grid voltage unbalance fault. 2.All inverters tripped offline at 14:15 on 02/15 due to Grid voltage unbalance fault and back online on 02/16. Again all inverters tripped offline between 9:15 to 13:00 on 02/23 due to Grid voltage unbalance fault. 3. Inverter 18 was ofline since 12/08/24 due to floating capacitor high voltage. Will investigate next time onsite. | 1.SR097182 2.SR097150 3. SR094254 | SR097150 | SR094254
Smith Creek | NY | 329908 | 395368.9 | -65460.9 | -16.56% | 472752.2 | -142844.2 | -30.22% | 1.All inverters tripped offline at 14:15 on 02/15 due to Grid voltage unbalance fault and back online on 02/16. Again all inverters tripped offline between 9:15 to 13:00 on 02/23 due to Grid voltage unbalance fault. | 1.SR097151
Bradford - 256 Presidential Dr | MA | 341831 | 434992 | -93161 | -21.42% | 529201.8 | -187370.8 | -35.41% | 1.Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2.Inverter 84 was not communicating from 02/02, after tehnician powercycled inverter regained communication on 02/24 at 11:00AM. | 1.SR096051,SR097794 2.SR097657 | SR097794 | SR097657
Charlton – 111 Brookfield Road - Bus Lot | MA | 33288 | 40369.2841 | -7081.2841 | -17.54% | 61889.87 | -28601.87 | -46.21% | 1. Site stopped communicating on 02/10 and power factors able to troubleshoot the issue and comms were restored on 02/.12. 2. Site tripped offline at 11:20AM on 02/17 and technician re-energized the site and it is back online on 02/18. | 1. SR096287 2. SR097195 | SR097195
Charlton – 154 Center Depot Road KMARD | MA | 20320 | 53693.111 | -33373.111 | -62.16% | 59765.73 | -39445.73 | -66% | 1. Inverter 13 was not communicating from 07/30/24, based on meter inverter was offline. The inverter was RMA'd by QE solar on 02/26. 2. Site tripped offline at 11:00AM ON 02/17. On 02/18 technician closed the recloser and site was back online at 8:50AM. 3. Site stopped communicating at 9:30PM on 02/25 and comms were restored on 02/26 after DAS powercycled. 4. Low generation due to weather/snow. | 1. SR096880 2. SR097194 3. SR097744 | SR097194 | SR097744
Charlton – 142A Brookfield Rd (Mitchell) | MA | 33022.5641 | 58822.546 | -25799.9819 | -43.86% | 62829.33 | -29806.7659 | -47.44% | 1. Site stopped communicating on 02/01 and comms were restored on 02/04 after DAS powercycled. 2. Site stopped communicating at 6:30PM on 02/25 and comms were restored on 02/26 after DAS powercycled. 3. Low generation due to weather/snow. | 1. SR096242 2. SR097809 | SR097809
Great Barrington – 3 Nolan Drive | MA | 50410 | 106085.9679 | -55675.9679 | -52.48% | 123737.26 | -73327.26 | -59.26% | 1. Site stopped commnicating at 11:25AM on 02/14. On 02/18 technician found recloser open position and closed back. The site back online on the same day. 2. Site stopped communicating at 1:20PM on 02/23. Valuses are struck for inverters 1 to 7. Site comms restored on 02/25 but inverter 5 remains offline. On 02/26 technician investigated the issue and inverter was being RMA'd. 3. Low generation due to weather/snow. | 1. SR097148 2. SR097662 | SR097662
Stockbridge – 92 State Line Road Truck Stop | MA | 89135 | 192765.1228 | -103630.1228 | -53.76% | 225738.73 | -136603.73 | -60.51% | 1. Inverters 1 to 28 stopped communication at 07:00AM on 02/03, production can be verified at meter level. Communications were self resolved on 02/07 2. On 02/16, Phase A voltage dropped to 0V while current held steady at ~40A, indicating the meter wasn't capturing full inverter output. On 02/18, the technician found the recloser tripped and restored it, bringing Phase A voltage and current back to normal by 8:10 AM. 3. Inverter 7 tripped offline at 3:35PM on 02/14 and inverter 5 tripped offline at 1:55PM on 02/15. On 02/18 technician cleared faults for both inverters, inverter 7 back online at 9:45AM but inverter 5 remains offline. On 02/21 techncian reset the inverter 5 and it is back online at 2:10PM on the sameday. 4. Inverter 5 tripped offline at 4:40PM on 02/21. On 02/24 technician found inverter reporting arc fault and he isolated the string 4 and inverter back online at 8:50AM on the same day. 5. Inverter 7 tripped offline at 9:40AM on 02/25. On 02/26 technician troubleshooted and cleared the fault, inverter back online at 3:40PM on the sameday. 6. Inverter 44 tripped offline at 14:40 due to "PF 100 production down" on 02/26. On 02/28 technician reset the inverter and it is back online at 2:00PM. 7. Low generation due to weather/snow. | 1. SR096270 2. SR097154 3. SR097154, SR097155, SR097338 4. SR097338, SR097654 5. SR097807 6. SR097851 | SR097154 | SR097154 | SR097155 | SR097338 | SR097338 | SR097654 | SR097807 | SR097851

## Mar
Lodestar |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 8516922.4648 | 7921237.0293 | 595685.4354 | 7.52% | 7889841.93 | 627080.5348 | 7.948%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 160256 | 162863 | -2607 | -1.601% | 164231 | -3975 | -2.42% | 1. Combiner box 1.2(DCP-1) is offline since 12/22/24. On 03/13 technician troubleshooted by plugging CT measurement wire and combiner box resumed communicating at 11:00AM. | 1. SR098455, SR095215 | SR095215
Bunce | CT | 301622.5 | 282807.6 | 18814.9 | 6.653% | NA
Norcap North | CT | 306603.5 | 329886.4 | -23282.9 | -7.058% | 305427 | 1176.5 | 0.3852% | 1. Inverter 1 was experienced multiple tripping events in previous month due to bus differential high fault and solectria initiated an RMA. On 03/06 technician replaced inverter with a new one and it is started producing from 9:45AM on the same day. 2. Site tripped offline at 14:15 on 03/11 and back online after technician re-energizing at 17:15 on the same day. 3. The site had a brief outage between 14:40 to 15:03 on 03/22. | 1. SR097792 2. SR098395 3. SR098889 | SR098395 | SR098889
Norcap South | CT | 320974.5 | 349780.3 | -28805.8 | -8.235% | 298676.2 | 22298.3 | 7.466% | 1.Inverter 36 experienced late start and offline issues throughout the month. The inverter typically self-resolves on alternate days. On 03/21, a technician performed troubleshooting and brought the inverter back online. 2. The site had a brief outage between 14:40 to 15:03 on 03/22. | 1. SR096465 2. SR098890 | SR098890
Platt Hill | CT | 300382 | 344310.9 | -43928.9 | -12.76% | 352217.3 | -51835.3 | -14.72% | 1. Site tripped offline at 23:45 on 03/06. On 03/08 after re-energize the site was back online at 10:30AM. 2. Site tripped offline at 12:30PM on 03/11. On 03/12 technician reset the main breaker and site back online at 9:00AM. 3. Site tripped offline at 9:30AM on 03/21 and later technician re-energized the site at 14:00 on the same day. 4. Site tripped offline at 6:15AM on 03/24. On 03/25 technician re-energized and it is back online at 10:15AM. 5. Inverter 5 started late for production at 12:30PM due to insulation fault on 03/31. | 1. SR098238 2. SR098398 3. SR098862 4. SR098926 5. SR099192 | SR098398 | SR098862 | SR098926 | SR099192
Powder Hill | CT | 305500 | 302824.2 | 2675.8 | 0.8836% | 233148 | 72352 | 31.03% | 1. Three CTs for Inverter 7 were RMA'd on 01/28. On 03/12, the site was offline from 11:00 AM to 12:30 PM as a technician was onsite replacing the three CTs for Inverter 7. | 1. SR095513
Sand Road | CT | 319904 | 300950.2 | 18953.8 | 6.298% | 277950 | 41954 | 15.09%
Suffield | CT | 308891 | 293653.5 | 15237.5 | 5.189% | 315921.2 | -7030.2 | -2.225% | 1. Site stopped communicating at 18:30 on 03/28. On 03/29 technician found recloser in open state and phase A&B are faulted. Technician cleared the fault and closed the recloser, site back online at 13:15 on same day. | 1. SR099128
Ashby-Duffy | MA | 293392 | 387655.3 | -94263.3 | -24.32% | 281840.8 | 11551.2 | 4.098% | 1. Inverter 2 was offline since 12/19 and will remains offline until the ground is unfrozen. 2. Inverter 24 started late for the production at 10:00AM on 03/06 due to insulation fault. 3. Inverter 38 stopped communicating at 1:30AM from 03/11. Will investigate while next time onsite. 4. Inverters 43, 47, and 59 were derated by 4–5 kW each starting at 10:30 AM on 03/12 due to excessive temperature. On 03/19, technician attempted to troubleshoot the issue, but it was unsuccessful, and SMA RMA’d the fans for these inverters. On 03/28, the technician replaced the fans, but the issue persisted. Further testing with SMA indicated a likely power supply failure in these inverters, and the powerheads have been RMA’d. | 1. SR097797 2. SR098200 3. SR098383 4. SR098407 | SR098200 | SR098383 | SR098407
Ashland | MA | 290755.5 | 311890.3 | -21134.8 | -6.776% | 320735.9 | -29980.4 | -9.347% | 1.Inverter 49 was being RMA'D since 10/16/23. 2.Inverter 67 was being RMA'd. 3.Inverter 57 was being RMA'd. 4.Inverter 12 was being RMA'd. 5.Inverter 16 was offline since 11/13 due to Arc Protection and being RMA'd. 6. Inverter 24 experiencing tripping events since 02/14. On 03/04 technician troubleshooted the issue with solectria and issue has been resolved from 03/05. 7. Site was offline from 7:30AM to 10:45AM on 03/18 due to technician was onsite to collect transformer DGA samples. 8. Inverters 40 to 46 tripped offline at 1:45PM due to grid voltage out of range. On 03/12 technician swapped the leads with the breaaker and inverters back online at 10:4AM on the same day. 9. Inverter 37 was started late for the production at 10:45AM on 03/18 due to insulation fault. 10. Inverter 65 started late for the production at 15:00 on 03/20 due to Insuation resistance low. | 1. SR088450 2. SR088450 3.SR091962 4.SR093117, SR097799 5. SR095816 6. SR097060 7. SR097563 8. SR098396 9. SR098679 10. SR098821 | SR088450 | SR091962 | SR093117 | SR097799 | SR095816 | SR097060 | SR097563 | SR098396 | SR098679 | SR098821
Barrington | MA | 68255 | 16516.58 | 51738.42 | 313.3% | 68910 | -655 | -0.9505% | 1. During morning hours weather station reporting low irradiance values. Working with Also energy and they are investigating. | 1. SR099616
Bedford - 205 Burlington Rd | MA | 35447 | NA |  |  | NA
Billerica - 6 Cook Street | MA | 31709 | NA |  |  | NA
Billerica - 780 Boston Road | MA | 36026 | NA |  |  | NA
Cheshire | MA | 69411.7888 | 71712.76 | -2300.9712 | -3.209% | 47518.1 | 21893.6888 | 46.07%
Lilly Lane | MA | 150553 | 142040.5 | 8512.5 | 5.993% | 159655.1 | -9102.1 | -5.701% | 1.Inverter 61 was being RMA'd from 01/22. | 1. SR097795
Monument Valley | MA | 294118.6792 | 66602.86 | 227515.8192 | 341.6% | NA |  |  | 1. Site stopped communicating at 3:00AM on 03/07. Technician found recloser open and after a reset site was back online at 13:45 on the same day. 2. Expected generation values are lower than actual values. AlsoEnergy stated that expected values are calculated based on inverter data and weather conditions and recommended an onsite visit. However, due to communication issues with the inverters, the expected values remain low. | 1. SR098250 2. SR087370 | SR087370
Nationwide | MA | 525648 | 470640.1 | 55007.9 | 11.69% | 455456 | 70192 | 15.41% | 1.Inverter 13 experienced late start issues intermittently throughout the month. | 1. SR097881
Pulpit Hill | MA | 649245.25 | 627559.4 | 21685.85 | 3.456% | 660610.7 | -11365.45 | -1.72% | 1. Inverter 49 did not start production on 01/26. The powerhead was being RMA'd since 01/29. On 03/04 technician replaced inverter 49 and it was back online at 14:45. 2. Inverter 42 was RMA'd since 02/26. On 03/04 technician replaced inverter and it is back online at 02:00PM. 3. The site was offline from 11:00AM to 13:45 due to technician was onsite for inverters 42 and 49 replacement on 03/04. 4. Inverter 83 had a string 8 down since 11/27. It will be investigated during the next onsite visit. | 1. SR095984 2. SR097793 3. SR097793, SR095984 4. SR093591, SR097798 | SR097793 | SR097793 | SR095984 | SR093591 | SR097798
Sandwich | MA | 353596 | NA |  |  | 495038 | -141442 | -28.57% | 1. Site tripped offline at 14:00 on 03/07 and started for production on 03/08. As per Erik site was back online by reset from sandwich. 2. PAD 4 tripped offline at 17:30 on 03/11 and remained offline throughout the month. Interface board and DSP board need to be replaced. | 1. SR098286 2. SR098405 | SR098405
Sturbridge Barn | MA | 154300 | 157826.2 | -3526.2 | -2.234% | 172343 | -18043 | -10.47% | 1. Inverter 25 tripped offline at 14:45 on 03/02. On 03/03, a technician worked with Solectria support and removed the parallel bus bar to put the inverter in independent mode. The inverter came back online at 14:30 on the same day. 2. Site tripped offline at 1:00AM and later technician re-energized the site and it was back online at 8:00AM. 3. Inverter 32 tripped offline at 13:00 on 03/06 and back online at 6:30AM on 03/07 after a reset. | 1. SR097966 2. SR098186 3. SR098223 | SR098186 | SR098223
Sturbridge Garage | MA | 77575.25 | 75875.88 | 1699.37 | 2.24% | 78866.2 | -1290.95 | -1.637%
Halsey Valley | NY | 746709 | 764179.6 | -17470.6 | -2.286% | 697000 | 49709 | 7.132% | 1. Site tripped offline at 9:00AM and back online at 2:00PM due to utility outage on 03/10. | 1. SR098333
Hunt Creek | NY | 543121 | 574757.3 | -31636.3 | -5.504% | 498900 | 44221 | 8.864% | 1. Inverter 18 was ofline since 12/08/24 due to floating capacitor high voltage. Will investigate next time onsite. 2. Inverters 5,3 and 27 tripped offline at 15:20 due to Grid voltage unbalance. Inverters self resolved at 16:30 on 03/14. 3. Multiple inverters tripped offline due to Grid voltage unbalance at 13:30 on 03/08. Inveretrs self resolved at 16:00 on the sameday. 4. Inverter 27 tripped offline at 10:45AM and self-resolved back online at 16:00 on 03/09. 5. Multiple inverters tripped offline at 8:15 AM and self resolved at 11:00AM on 03/26. | 1. SR094254 2. SR095965 3. SR098301 4. SR098316 5. SR098993 | SR095965 | SR098301 | SR098316 | SR098993
Smith Creek | NY | 595618 | 619479.8 | -23861.8 | -3.852% | 602155.1 | -6537.1 | -1.086% | 1. Multiple inverters tripped offline due to Grid voltage unbalance at 13:30 on 03/08. Inveretrs self resolved at 16:00 on the sameday. | 1. SR098300
Bradford - 256 Presidential Dr | MA | 645415 | 608236.9071 | 37178.0929 | 6.112% | 670083.4 | -24668.4 | -3.681% | 1. Inverter 128 was not communicating since 12/07/24. Communications card has been RMA'd and will be replaced during a combined dispatch. 2. Site had brief outage in between 12:20PM to 12:25PM. But inverters 1 to 4, 42 and 104 was not came back online. Inverters self resolved and started for production on 03/08. 3. Inverters 1 to 55 stopped communicating at 12:45 on 03/14, production not confirmed. On 03/18 technician powercyled DAS and comms were restored. | 1. SR096051,SR097794, SR099300 2. SR098265 3. SR098601 | SR097794 | SR099300 | SR098265 | SR098601
Charlton – 111 Brookfield Road - Bus Lot | MA | 75634 | 60424.0006 | 15209.9994 | 25.17% | 80041.66 | -4407.66 | -5.507% | 1. Site was offline on 03/06 and later technician found SEL in open position and closed it. The site was back online at 1:35PM on the sameday. | 1. SR098211
Charlton – 154 Center Depot Road KMARD | MA | 54420 | 69917.3952 | -15497.3952 | -22.17% | 78110.62 | -23690.62 | -30.33% | 1. Inverter 13 was not communicating from 07/30/24, based on meter inverter was offline. The inverter was RMA'd by QE solar on 02/26. 2. Site was offline on 03/06 and later technician found SEL in open position and closed it. The site was back online at 12:25PM on the sameday. 3. Site lost communication on 03/18 and technician teoubleshooted the issue but comms issue persit. On 03/19 the site comms were back at 9:15AM. | 1. SR096880 2. SR098203 3. SR098685 | SR098203 | SR098685
Charlton – 142A Brookfield Rd (Mitchell) | MA | 70420 | 76380.4585 | -5960.4585 | -7.804% | 80313.94 | -9893.94 | -12.32% | 1. Inverter 1 is not communicating since 03/01. On 03/06 technician investigated but issue persist. Solectria has recommended replacing the powerhead to regain communication. | 1. SR098182
Great Barrington – 3 Nolan Drive | MA | 145285.4967 | 155216.5388 | -9931.0421 | -6.398% | 161684.64 | -16399.1433 | -10.14% | 1. Inverter 5 was being RMA'd since 02/26. On 03/26 technician replaced inverter 5 and it is back online and producing. 2. Inverter 14 was underproducing by 5kW compared to its peers. Will investigate next time onsite. 3. Inverter 24 tripped offline at 7:30AM on 03/13. On 03/14 technician investigated and found inverter was faulted with protect 90 and it was being RMA'd by solectria. 4. Inverters and meter stopped communicating from 5:00PM on 03/14. On 03/16 technician found site was online but no communication. On 03/26 technician worked with powerfactors and communications were regained. | 1. SR097843 2. SR098468 3. SR098503 4. SR098604 | SR098468 | SR098503 | SR098604
Stockbridge – 92 State Line Road Truck Stop | MA | 286134 | 297249.0491 | -11115.0491 | -3.739% | 333008.07 | -46874.07 | -14.08% | 1. Inverters 25 and 38 tripped offline at 8:05 reporting "PF100-production down" on 03/06 and self resolved and started for production on 03/07. 2. Inverter 44 didn't started for production on 03/12. On 03/14 technician re-energized and inverter was back online on the sameday. 3. Site stopped communicating at 6:30PM on 03/16. On 03/18 tech powercycled DAS and communications were restored. | 1. SR098230 2. SR098492 3. SR099148 | SR098492 | SR099148

## Apr
Lodestar |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## May
Lodestar |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Jun
Lodestar |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Jul
Lodestar |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Aug
Lodestar |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 10151177.5 | 7927515 | 2223662.5 | 28.05% | 9645209.7 | 505967.8 | 5.246% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT | 172046 | 188098 | -16052 | -8.534% | 184916.4 | -12870.4 | -6.96%
Bunce | CT | 356160 | 214884 | 141276 | 65.75% | NA
Norcap North | CT | 353706 | 350440 | 3266 | 0.932% | 358531.5 | -4825.5 | -1.346%
Norcap South | CT | 378641 | 367429.8 | 11211.2 | 3.051% | 351983 | 26658 | 7.574%
Platt Hill | CT | 388207 | 409220 | -21013 | -5.135% | 411409.7 | -23202.7 | -5.64%
Powder Hill | CT | 360699 | 362106 | -1407 | -0.3886% | 283282 | 77417 | 27.33%
Sand Road | CT | 386609 | 343428.9 | 43180.1 | 12.57% | 327346.2 | 59262.8 | 18.1%
Suffield | CT | 365172 | 357945 | 7227 | 2.019% | 361334.4 | 3837.6 | 1.062%
Ashby-Duffy | MA | 344927 | 358435 | -13508 | -3.769% | 350894.1 | -5967.1 | -1.701%
Ashland | MA | 361151 | 374718 | -13567 | -3.621% | 381791.5 | -20640.5 | -5.406%
Barrington | MA | 76945 | 67187 | 9758 | 14.52% | 86469.4 | -9524.4 | -11.01%
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA | 82137 | 83247.6 | -1110.6 | -1.334% | 64884 | 17253 | 26.59%
Lilly Lane | MA | 175990 | 173631 | 2359 | 1.359% | 177958 | -1968 | -1.106%
Monument Valley | MA | 380364 | 282628.5 | 97735.5 | 34.58% | 0 | 380364
Nationwide | MA | 550601 | 536230 | 14371 | 2.68% | 536327 | 14274 | 2.661%
Pulpit Hill | MA | 810809 | 774638.7 | 36170.3 | 4.669% | 777126 | 33683 | 4.334%
Sandwich | MA | 542197 | 0 | 542197 |  | 584062 | -41865 | -7.168%
Sturbridge Barn | MA | 176159 | 183008 | -6849 | -3.742% | 190566.5 | -14407.5 | -7.56%
Sturbridge Garage | MA | 85972.5 | 86378 | -405.5 | -0.4694% | 87896 | -1923.5 | -2.188%
Halsey Valley | NY | 973648 | 965597 | 8051 | 0.8338% | 1001133 | -27485 | -2.745%
Hunt Creek | NY | 652076 | 694573.5 | -42497.5 | -6.119% | 713489 | -61413 | -8.607%
Smith Creek | NY | 727810 | 753691 | -25881 | -3.434% | 740977 | -13167 | -1.777%
Bradford - 256 Presidential Dr | MA | 810488 | 0 | 810488 |  | 810307 | 181 | 0.02234%
Charlton – 111 Brookfield Road - Bus Lot | MA | 82680 | 0 | 82680 |  | 94856 | -12176 | -12.84%
Charlton – 154 Center Depot Road KMARD | MA | 77250 | 0 | 77250 |  | 91832 | -14582 | -15.88%
Charlton – 142A Brookfield Rd (Mitchell) | MA | 79236 | 0 | 79236 |  | 93318 | -14082 | -15.09%
Great Barrington – 3 Nolan Drive | MA | 62374 | 0 | 62374 |  | 189713 | -127339 | -67.12%
Stockbridge – 92 State Line Road Truck Stop | MA | 337123 | 0 | 337123 |  | 392807 | -55684 | -14.18%

## Sep
Lodestar |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Oct
Lodestar |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Nov
Lodestar |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Dec
Lodestar |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Barkhamsted | CT
Bunce | CT
Norcap North | CT
Norcap South | CT
Platt Hill | CT
Powder Hill | CT
Sand Road | CT
Suffield | CT
Ashby-Duffy | MA
Ashland | MA
Barrington | MA
Bedford - 205 Burlington Rd | MA
Billerica - 6 Cook Street | MA
Billerica - 780 Boston Road | MA
Cheshire | MA
Lilly Lane | MA
Monument Valley | MA
Nationwide | MA
Pulpit Hill | MA
Sandwich | MA
Sturbridge Barn | MA
Sturbridge Garage | MA
Halsey Valley | NY
Hunt Creek | NY
Smith Creek | NY
Bradford - 256 Presidential Dr | MA
Charlton – 111 Brookfield Road - Bus Lot | MA
Charlton – 154 Center Depot Road KMARD | MA
Charlton – 142A Brookfield Rd (Mitchell) | MA
Great Barrington – 3 Nolan Drive | MA
Stockbridge – 92 State Line Road Truck Stop | MA

## Sites
Portfolio: | Lodestar
Site DAS Name | Site | State | Update | DAS
Barkhamsted Solar | Barkhamsted | CT | AEF | PowerTrack
Bunce Solar | Bunce | CT | AEF | PowerTrack
Norcap North | Norcap North | CT | AEF | PowerTrack
Norcap South | Norcap South | CT | AEF | PowerTrack
Platt Hill | Platt Hill | CT | AEF | PowerTrack
Powder Hill | Powder Hill | CT | AEF | PowerTrack
Sand Road Solar | Sand Road | CT | AEF | PowerTrack
Suffield Solar | Suffield | CT | AEF | PowerTrack
Ashby-Duffy | Ashby-Duffy | MA | AEF | PowerTrack
Ashland Solar | Ashland | MA | AEF | PowerTrack
Barrington Fairgrounds | Barrington | MA | AEF | PowerTrack
MA: Bedford - 205 Burlington Rd | Bedford - 205 Burlington Rd | MA |  | GPM
MA: Billerica: 6 Cook Street | Billerica - 6 Cook Street | MA |  | GPM
MA: Billerica - 780 Boston Road | Billerica - 780 Boston Road | MA |  | GPM
Cheshire Solar | Cheshire | MA | AEF | PowerTrack
Lilly Lane (N-4) | Lilly Lane | MA | AEF | PowerTrack
Monument Valley | Monument Valley | MA | AEF | PowerTrack
Nationwide | Nationwide | MA | AEF | PowerTrack
Pulpit Hill | Pulpit Hill | MA | AEF | PowerTrack
MA: Sandwich - 9 Victory Drive Solar | Sandwich | MA |  | PowerTrack
Sturbridge Barn (N-3) | Sturbridge Barn | MA | AEF | PowerTrack
Sturbridge Garage (R-2) | Sturbridge Garage | MA | AEF | PowerTrack
Halsey Valley | Halsey Valley | NY | AEF | PowerTrack
Hunt Creek Solar | Hunt Creek | NY | AEF | PowerTrack
Smith Creek Solar | Smith Creek | NY | AEF | PowerTrack
006 - Bradford O&M | Bradford - 256 Presidential Dr | MA |  | PF Drive
007 - Bus Lot O&M | Charlton – 111 Brookfield Road - Bus Lot | MA |  | PF Drive
010 - Kmard O&M | Charlton – 154 Center Depot Road KMARD | MA |  | PF Drive
011 - Mitchell O&M | Charlton – 142A Brookfield Rd (Mitchell) | MA |  | PF Drive
012 - Nolan O&M | Great Barrington – 3 Nolan Drive | MA |  | PF Drive
014 - Truck Stop O&M | Stockbridge – 92 State Line Road Truck Stop | MA |  | PF Drive