## Year to Date
Marana USD |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 1212801 | 0 | 1212801 | 0% | 0 | 1212801 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Marana - Degrazia ES | AZ | 71978 | 0 | 71978 | 0% | 0 | 0 | 0%
AZ: Marana - Gladden Farms Ph 2 | AZ | 70035 | 0 | 70035 | 0% | 0 | 0 | 0%
AZ: Marana - Marana High School | AZ | 292367 | 0 | 292367 | 0% | 0 | 0 | 0%
AZ: Marana - Mountain View HS Exp. | AZ | 380175 | 0 | 380175 | 0% | 0 | 0 | 0%
AZ: Marana - Rattlesnake Ridge ES | AZ | 54345 | 0 | 54345 | 0% | 0 | 0 | 0%
AZ: Marana - Roadrunner ES | AZ | 84391 | 0 | 84391 | 0% | 0 | 0 | 0%
AZ: Marana - Thornydale Elementary | AZ | 45315 | 0 | 45315 | 0% | 0 | 0 | 0%
AZ: Marana - Tortolita MS | AZ | 118669 | 0 | 118669 | 0% | 0 | 0 | 0%
AZ: Marana - Picture Rocks Intermediat | AZ | 95526 | 0 | 95526 | 0% | 0 | 0 | 0%

## 1st Qtr
Marana USD |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1212801 | 0 | 1212801 | 0% | 0 | 1212801 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Marana - Degrazia ES | AZ | 71978 | 0 | 71978 | 0% | 0 | 0 | 0%
AZ: Marana - Gladden Farms Ph 2 | AZ | 70035 | 0 | 70035 | 0% | 0 | 0 | 0%
AZ: Marana - Marana High School | AZ | 292367 | 0 | 292367 | 0% | 0 | 0 | 0%
AZ: Marana - Mountain View HS Exp. | AZ | 380175 | 0 | 380175 | 0% | 0 | 0 | 0%
AZ: Marana - Rattlesnake Ridge ES | AZ | 54345 | 0 | 54345 | 0% | 0 | 0 | 0%
AZ: Marana - Roadrunner ES | AZ | 84391 | 0 | 84391 | 0% | 0 | 0 | 0%
AZ: Marana - Thornydale Elementary | AZ | 45315 | 0 | 45315 | 0% | 0 | 0 | 0%
AZ: Marana - Tortolita MS | AZ | 118669 | 0 | 118669 | 0% | 0 | 0 | 0%
AZ: Marana - Picture Rocks Intermediat | AZ | 95526 | 0 | 95526 | 0% | 0 | 0 | 0%

## 2nd Qtr
Marana USD |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Marana - Degrazia ES | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Gladden Farms Ph 2 | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Marana High School | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Mountain View HS Exp. | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Rattlesnake Ridge ES | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Roadrunner ES | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Thornydale Elementary | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Tortolita MS | AZ | 0 | 0 | 0 |  |  | 0
AZ: Marana - Picture Rocks Intermediat | AZ | 0 | 0 | 0 |  |  | 0

## 3rd Qtr
Marana USD |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Marana - Degrazia ES | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Gladden Farms Ph 2 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Marana High School | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Mountain View HS Exp. | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Rattlesnake Ridge ES | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Roadrunner ES | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Thornydale Elementary | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Tortolita MS | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Picture Rocks Intermediat | AZ | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Marana USD |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
AZ: Marana - Degrazia ES | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Gladden Farms Ph 2 | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Marana High School | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Mountain View HS Exp. | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Rattlesnake Ridge ES | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Roadrunner ES | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Thornydale Elementary | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Tortolita MS | AZ | 0 | 0 | 0 |  | 0 | 0
AZ: Marana - Picture Rocks Intermediat | AZ | 0 | 0 | 0 |  | 0 | 0

## Jan
Marana USD |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 339174 | 0 | 339174 | 0% | 0 | 339174 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ | 18297 | N/A |  |  | N/A |  | 0% | 1.Inverter A2 was down by two strings, and inverter C2 was down by one string due to blown fuses, according to the drawing, resulting in approximately an 8 kW loss. Upon the technician's visit on 01/16, all blown fuses were replaced, and the inverters were re-energized. 2.Inverter B1 was operating with one string down, and inverter B2 was operating with two strings down due to blown fuses. Upon the technician's visit on 01/23, the blown fuses were replaced, and the strings were restored. | 1.SR095544, SR095711 2.SR095711 | SR095711 | SR095711
AZ: Marana - Gladden Farms Ph 2 | AZ | 19073 | N/A |  |  | N/A |  | 0%
AZ: Marana - Marana High School | AZ | 79212 | N/A |  |  | N/A |  | 0% | 1.Inverter C3 is being RMA'D from 12/19/2024. 2.Inverter D1 kept offline from 09/13 and back online at 04:00PM on 01/31. 3.Inverter A4 is offline on 01/27 and being RMA'D 4.Inverters A2, G3, and F3 were operating with one string down, while inverters A6, B1, and C2 were operating with two strings down. Inverter G1 had three strings down, and inverter G2 had four strings down due to blown fuses. Upon the technician's visit on 01/22, all blown fuses were replaced, and the inverters were restored to operation. 5. Shark meter has to be replaced. | 1.SR094543 2.SR093461 3.SR095890 4.SR095709 5.SR096093, SR094821 | SR093461 | SR095890 | SR095709 | SR096093 | SR094821
AZ: Marana - Mountain View HS Exp. | AZ | 111815 | N/A |  |  | N/A |  | 0% | 1. Inverter A1 underperforming by 4 kW from 09/17/24. | 1. SR095235
AZ: Marana - Rattlesnake Ridge ES | AZ | 13384 | N/A |  |  | N/A |  | 0% | 1.Inverter A3 has been offline since 1:30 PM on 12/22/2024. On 01/07, the technician stated that four strings were faulty and causing isolation errors. He brought it back online by connecting only two functional strings. | 1.SR095024, SR095415 | SR095415
AZ: Marana - Roadrunner ES | AZ | 24328 | N/A |  |  | N/A |  | 0% | 1.Inverter A2 is underperforming by approximately 5 kW compared to its peers, possibly due to a string down. | 1.SR095825
AZ: Marana - Thornydale Elementary | AZ | 11826 | N/A |  |  | N/A |  | 0%
AZ: Marana - Tortolita MS | AZ | 33639 | N/A |  |  | N/A |  | 0% | 1.Inverter A2 was underperforming by approximately 4 kW compared to its peers, possibly due to a string down. After a technician's visit on 01/23, he stated that three strings were not functioning. Upon replacing the blown fuses, Inverter A2 began producing as expected. 2.Inverter C1 was found with two strings down. After a technician's visit on 01/23, the blown fuses of both strings were replaced, and the inverter returned to normal production. | 1.SR095826 2.SR095710 | SR095710
AZ: Marana - Picture Rocks Intermediat | AZ | 27600 | N/A |  |  | N/A |  | 0%

## Feb
Marana USD |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 390615 | 0 | 390615 | 0% | 0 | 390615 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ | 23021 | N/A |  |  | N/A |  |  | 1.Inverter A1 tripped offline at 11:45AM on 02/14 and back online on 02/15 and Inverter A2 was underperforming by 9 kW. Upon the technician's arrival to the site on 02/20, he stated that two strings were abnormal and found that the fuses were blown. After replacing the fuses, the strings were restored, and issue still exists. | 1.SR097112
AZ: Marana - Gladden Farms Ph 2 | AZ | 22104 | N/A |  |  | N/A
AZ: Marana - Marana High School | AZ | 96517 | N/A |  |  | N/A |  |  | 1.Inverter C3 has been RMA'd since 12/19/2024. Upon the technician's arrival to the site on 02/05 to troubleshoot the inverter, after some modifications to the settings, the inverter was back online at 02:00 PM on 02/05. 2.Inverter A4 was offline on 01/27 and is being RMA'd. Upon the technician's arrival to the site on 02/05 to troubleshoot the inverter, after swapping out the integrated disconnect switch and making some modifications to the settings, the inverter was back online at 02:00 PM on 02/05.. 3.Inverters B3, D1, and F3 are underperforming by approximately 5 kW, inverter G1 is underperforming by 15 kW, inverter F2 is underperforming by 8 kW, and inverter A6 is underperforming by 4 kW. Upon the technician's arrival on 02/05, it was found that inverter G1 had a damaged wire and MC4 connectors between modules 12-16 of 20. After replacing the MC4 connectors, the inverter resumed producing at 100%. For inverter F2, two fuses were replaced. Inverters A6, B3, D1, and F3 are experiencing issues related to age degradation and efficiency loss. | 1.SR094543, SR095890 2.SR095890 3.SR096302 | SR095890 | SR095890 | SR096302
AZ: Marana - Mountain View HS Exp. | AZ | 122547 | N/A |  |  | N/A |  |  | 1. Inverter A1 underperforming by 4 kW from 09/17/24. | 1. SR095235
AZ: Marana - Rattlesnake Ridge ES | AZ | 16287 | N/A |  |  | N/A |  |  | 1.Inverter A3 has been offline since 1:30 PM on 12/22/2024. On 01/07, the technician stated that four strings were faulty and causing isolation errors. He brought it back online by connecting only two functional strings. | 1.SR095024, SR095415 | SR095415
AZ: Marana - Roadrunner ES | AZ | 26794 | N/A |  |  | N/A |  |  | 1.Inverter A2 is underperforming by approximately 5 kW compared to its peers, possibly due to a string being down, and inverter A3 is underperforming by 3 kW. Upon the technician's visit on 02/13, he found that strings 1 and 3 of inverter A3 were down due to blown fuses. After replacing the fuses, the inverter back to normal, and no abnormalities were found in inverter A2. | 1.SR095825
AZ: Marana - Thornydale Elementary | AZ | 14208 | N/A |  |  | N/A
AZ: Marana - Tortolita MS | AZ | 38763 | N/A |  |  | N/A |  |  | 1. The meter is not capturing the total power of all inverters.Upon the technician's arrival on 02/10, he noted that Phase C was in an off state, which might be affecting the Shark meter and recommended replacing the CTs. 2. Inverter C1 dropped a string at 1:15 pm on 02/21. | 1.SR096293 2.SR097628 | SR097628
AZ: Marana - Picture Rocks Intermediat | AZ | 30374 | N/A |  |  | N/A

## Mar
Marana USD |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 483012 | 0 | 483012 | 0% | 0 | 483012 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ | 30660 | N/A |  |  | N/A |  |  | 1. Inverter A2 was underperforming by 9 kW. Upon the technician's arrival at the site on 02/20, he noted that two strings were abnormal and found that the fuses were blown. After replacing the fuses, the strings were restored, but the inverter was still underperforming. The technician returned to the site on 03/12 and performed a further replacement of 15-amp string fuses. Following this, the inverter returned to normal performance on 03/12. 2. Inverter C1 was underperforming by 5–6 kW. Upon the technician's arrival to the site on 03/12, he found that the fuses were blown. After replacing the fuses, the inverter is now performing as expected. | 1. SR097986, SR097112 2. SR097986 | SR097112 | SR097986
AZ: Marana - Gladden Farms Ph 2 | AZ | 28858 | N/A |  |  | N/A
AZ: Marana - Marana High School | AZ | 116638 | N/A |  |  | N/A |  |  | 1.Shark meter is not capturing all inverters production from 12/17 and needs to be replaced. | 1.SR094821, SR096093 | SR096093
AZ: Marana - Mountain View HS Exp. | AZ | 145813 | N/A |  |  | N/A |  |  | 1.Inverter A4 lost a string from 03/19/25. | 1.SR098807
AZ: Marana - Rattlesnake Ridge ES | AZ | 24674 | N/A |  |  | N/A |  |  | 1.Inverter A3 was offline from 11:30 AM to 01:00 PM on 03/06 for a technician visit. On 03/06 ,a ground fault was identified on String 33, three isolated strings were rectified, and further dissection of String 33 is needed to locate the insulation issue.Again on 03/14, a technician visited the site and mentioned a replacement module needs to be installed. 2.Inverter A2 dropped a string on 03/02/25. On 03/06, a technician visited the site, found a blown 15A string fuse, and replaced it. Since then, the inverter has been producing as expected. | 1.SR095415,SR98669 2. SR095415,SR097987 | SR98669 | SR095415 | SR097987
AZ: Marana - Roadrunner ES | AZ | 33269 | N/A |  |  | N/A
AZ: Marana - Thornydale Elementary | AZ | 19281 | N/A |  |  | N/A
AZ: Marana - Tortolita MS | AZ | 46267 | N/A |  |  | N/A |  |  | 1.The meter is not capturing the total power of all inverters. On 02/10, the technician found Phase C off, possibly affecting the Shark meter, and recommended replacing the CTs and installing a new surge protection device 2.Inverter C1 dropped one string at 1:15 PM on 02/21, a second on 03/25/25, and a third on 03/28/25, resulting in three strings offline. This has led to an estimated power loss of 12 kW, representing approximately 5% of the system’s total capacity | 1.SR096293 2.SR097628 | SR097628
AZ: Marana - Picture Rocks Intermediat | AZ | 37552 | N/A |  |  | N/A

## Apr
Marana USD |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## May
Marana USD |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Jun
Marana USD |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Jul
Marana USD |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Aug
Marana USD |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Sep
Marana USD |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Oct
Marana USD |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Nov
Marana USD |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Dec
Marana USD |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ

## Sites
Portfolio: | Marana USD
Site DAS Name | State | Update | DAS
AZ: Marana - Degrazia ES | AZ
AZ: Marana - Gladden Farms Ph 2 | AZ
AZ: Marana - Marana High School | AZ
AZ: Marana - Mountain View HS Exp. | AZ
AZ: Marana - Rattlesnake Ridge ES | AZ
AZ: Marana - Roadrunner ES | AZ
AZ: Marana - Thornydale Elementary | AZ
AZ: Marana - Tortolita MS | AZ
AZ: Marana - Picture Rocks Intermediat | AZ