## Year to Date
JLL |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 321048.413 | 0 | 321048.413 | 0% | 0 | 321048.413 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bullhead | AZ | 515.8 | 0 | 515.8 |  | 0 | 0
Peoria | AZ | 134.3 | 0 | 134.3 |  | 0 | 0
Tucson | AZ | 4801.189 | 0 | 4801.189 |  | 0 | 0
Hialeah | FL | -4653.21 | 0 | -4653.21 |  | 0 | 0
Jacksonville | FL | 518.564 | 0 | 518.564 |  | 0 | 0
Miami Gardens | FL | 543.6 | 0 | 543.6 |  | 0 | 0
Fort Myers | FL | 27115.1 | 0 | 27115.1 |  | 0 | 0
Orlando | FL | 21120.15 | 0 | 21120.15 |  | 0 | 0
Port St. Lucie | FL | 45063.2 | 0 | 45063.2 |  | 0 | 0
Tampa | FL | 7329.2 | 0 | 7329.2 |  | 0 | 0
Roswell | GA | 26314.9 | 0 | 26314.9 |  | 0 | 0
Charlotte | NC | 10740.9 | 0 | 10740.9 |  | 0 | 0
Raleigh | NC | 14237.9 | 0 | 14237.9 |  | 0 | 0
Cordova | TN | 13139.5 | 0 | 13139.5 |  | 0 | 0
Austin | TX | 6832 | 0 | 6832 |  | 0 | 0
Frisco | TX | 11784.7 | 0 | 11784.7 |  | 0 | 0
Copperfield | TX | 6872.1 | 0 | 6872.1 |  | 0 | 0
Charlotte - B of A - 1 BAC | NC | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - 401 N Tryon | NC | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg A | AZ | 10791.25 | 0 | 10791.25 |  | 0 | 0
Chandler - B of A Campus Bldg B | AZ | 19506.5 | 0 | 19506.5 |  | 0 | 0
Chandler - B of A Campus Bldg C | AZ | 10495.3 | 0 | 10495.3 |  | 0 | 0
Chandler - B of A Campus Bldg D | AZ | 5978.87 | 0 | 5978.87 |  | 0 | 0
Tampa - BoA Ekman | FL | 81866.6 | 0 | 81866.6 |  | 0 | 0
Charlotte - B of A - Sherrill | NC | 0 | 0 | 0 |  | 0 | 0

## 1st Qtr
JLL |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 227964.073 | 0 | 227964.073 | 0% | 0 | 227964.073 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bullhead | AZ | 223.9 | 0 | 223.9 |  | 0 | 0
Peoria | AZ | 134.3 | 0 | 134.3 |  | 0 | 0
Tucson | AZ | 4801.189 | 0 | 4801.189 |  | 0 | 0
Hialeah | FL | -727.7 | 0 | -727.7 |  | 0 | 0
Jacksonville | FL | 277.064 | 0 | 277.064 |  | 0 | 0
Miami Gardens | FL | 294.5 | 0 | 294.5 |  | 0 | 0
Fort Myers | FL | 12350.9 | 0 | 12350.9 |  | 0 | 0
Orlando | FL | 9370.1 | 0 | 9370.1 |  | 0 | 0
Port St. Lucie | FL | 24214.5 | 0 | 24214.5 |  | 0 | 0
Tampa | FL | 3163.1 | 0 | 3163.1 |  | 0 | 0
Roswell | GA | 13469 | 0 | 13469 |  | 0 | 0
Charlotte | NC | 5942.8 | 0 | 5942.8 |  | 0 | 0
Raleigh | NC | 7561.2 | 0 | 7561.2 |  | 0 | 0
Cordova | TN | 5806.3 | 0 | 5806.3 |  | 0 | 0
Austin | TX | 2467.9 | 0 | 2467.9 |  | 0 | 0
Frisco | TX | 6282.5 | 0 | 6282.5 |  | 0 | 0
Copperfield | TX | 3694 | 0 | 3694 |  | 0 | 0
Charlotte - B of A - 1 BAC | NC | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - 401 N Tryon | NC | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg A | AZ | 10791.25 | 0 | 10791.25 |  | 0 | 0
Chandler - B of A Campus Bldg B | AZ | 19506.5 | 0 | 19506.5 |  | 0 | 0
Chandler - B of A Campus Bldg C | AZ | 10495.3 | 0 | 10495.3 |  | 0 | 0
Chandler - B of A Campus Bldg D | AZ | 5978.87 | 0 | 5978.87 |  | 0 | 0
Tampa - BoA Ekman | FL | 81866.6 | 0 | 81866.6 |  | 0 | 0
Charlotte - B of A - Sherrill | NC | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
JLL |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 93084.34 | 0 | 93084.34 | 0% | 0 | 93084.34 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bullhead | AZ | 291.9 | 0 | 291.9 |  | 0 | 0
Peoria | AZ | 0 | 0 | 0 |  | 0 | 0
Tucson | AZ | 0 | 0 | 0 |  | 0 | 0
Hialeah | FL | -3925.51 | 0 | -3925.51 |  | 0 | 0
Jacksonville | FL | 241.5 | 0 | 241.5 |  | 0 | 0
Miami Gardens | FL | 249.1 | 0 | 249.1 |  | 0 | 0
Fort Myers | FL | 14764.2 | 0 | 14764.2 |  | 0 | 0
Orlando | FL | 11750.05 | 0 | 11750.05 |  | 0 | 0
Port St. Lucie | FL | 20848.7 | 0 | 20848.7 |  | 0 | 0
Tampa | FL | 4166.1 | 0 | 4166.1 |  | 0 | 0
Roswell | GA | 12845.9 | 0 | 12845.9 |  | 0 | 0
Charlotte | NC | 4798.1 | 0 | 4798.1 |  | 0 | 0
Raleigh | NC | 6676.7 | 0 | 6676.7 |  | 0 | 0
Cordova | TN | 7333.2 | 0 | 7333.2 |  | 0 | 0
Austin | TX | 4364.1 | 0 | 4364.1 |  | 0 | 0
Frisco | TX | 5502.2 | 0 | 5502.2 |  | 0 | 0
Copperfield | TX | 3178.1 | 0 | 3178.1 |  | 0 | 0
Charlotte - B of A - 1 BAC | NC | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - 401 N Tryon | NC | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg A | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg B | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg C | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg D | AZ | 0 | 0 | 0 |  | 0 | 0
Tampa - BoA Ekman | FL | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - Sherrill | NC | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
JLL |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bullhead | AZ | 0 | 0 | 0 |  | 0 | 0
Peoria | AZ | 0 | 0 | 0 |  | 0 | 0
Tucson | AZ | 0 | 0 | 0 |  | 0 | 0
Hialeah | FL | 0 | 0 | 0 |  | 0 | 0
Jacksonville | FL | 0 | 0 | 0 |  | 0 | 0
Miami Gardens | FL | 0 | 0 | 0 |  | 0 | 0
Fort Myers | FL | 0 | 0 | 0 |  | 0 | 0
Orlando | FL | 0 | 0 | 0 |  | 0 | 0
Port St. Lucie | FL | 0 | 0 | 0 |  | 0 | 0
Tampa | FL | 0 | 0 | 0 |  | 0 | 0
Roswell | GA | 0 | 0 | 0 |  | 0 | 0
Charlotte | NC | 0 | 0 | 0 |  | 0 | 0
Raleigh | NC | 0 | 0 | 0 |  | 0 | 0
Cordova | TN | 0 | 0 | 0 |  | 0 | 0
Austin | TX | 0 | 0 | 0 |  | 0 | 0
Frisco | TX | 0 | 0 | 0 |  | 0 | 0
Copperfield | TX | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - 1 BAC | NC | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - 401 N Tryon | NC | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg A | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg B | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg C | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg D | AZ | 0 | 0 | 0 |  | 0 | 0
Tampa - BoA Ekman | FL | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - Sherrill | NC | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
JLL |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Bullhead | AZ | 0 | 0 | 0 |  | 0 | 0
Peoria | AZ | 0 | 0 | 0 |  | 0 | 0
Tucson | AZ | 0 | 0 | 0 |  | 0 | 0
Hialeah | FL | 0 | 0 | 0 |  | 0 | 0
Jacksonville | FL | 0 | 0 | 0 |  | 0 | 0
Miami Gardens | FL | 0 | 0 | 0 |  | 0 | 0
Fort Myers | FL | 0 | 0 | 0 |  | 0 | 0
Orlando | FL | 0 | 0 | 0 |  | 0 | 0
Port St. Lucie | FL | 0 | 0 | 0 |  | 0 | 0
Tampa | FL | 0 | 0 | 0 |  | 0 | 0
Roswell | GA | 0 | 0 | 0 |  | 0 | 0
Charlotte | NC | 0 | 0 | 0 |  | 0 | 0
Raleigh | NC | 0 | 0 | 0 |  | 0 | 0
Cordova | TN | 0 | 0 | 0 |  | 0 | 0
Austin | TX | 0 | 0 | 0 |  | 0 | 0
Frisco | TX | 0 | 0 | 0 |  | 0 | 0
Copperfield | TX | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - 1 BAC | NC | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - 401 N Tryon | NC | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg A | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg B | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg C | AZ | 0 | 0 | 0 |  | 0 | 0
Chandler - B of A Campus Bldg D | AZ | 0 | 0 | 0 |  | 0 | 0
Tampa - BoA Ekman | FL | 0 | 0 | 0 |  | 0 | 0
Charlotte - B of A - Sherrill | NC | 0 | 0 | 0 |  | 0 | 0

## Jan
JLL |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 140840.521 | 0 | 140840.521 | 0% | 0 | 140840.521 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ | 51 | N/A |  |  | N/A
Peoria | AZ | 72 | N/A |  |  | N/A
Tucson | AZ | 1393 | N/A |  |  | N/A
Hialeah | FL | -172 | N/A |  |  | N/A |  |  | 1. Site is reporting its production at the meter as a negative value, but inverter production is positive from 09/11, due to a faulty CT and its leads needed to be reversed to read positive production. | 1. SR090283
Jacksonville | FL | 87 | N/A |  |  | N/A
Miami Gardens | FL | 83 | N/A |  |  | N/A
Fort Myers | FL | 441 | N/A |  |  | N/A
Orlando | FL | 343 | N/A |  |  | N/A
Port St. Lucie | FL | 6338 | N/A |  |  | N/A |  |  | 1. 2 microinverters are not reporting and 1 microinverter is not producing since 01/22/25. Parts are needed to bring them back online. | 1. SR095856
Tampa | FL | 1142 | N/A |  |  | N/A
Roswell | GA | 3328 | N/A |  |  | N/A |  |  | 1. 25 microinverters have been offline since 06/25. The Southwest microinverters are receiving AC voltage but not DC voltage, while the Northeast microinverters are not reporting, likely due to a breaker trip. | 1. SR087006
Charlotte | NC | 1742 | N/A |  |  | N/A
Raleigh | NC | 2308 | N/A |  |  | N/A
Cordova | TN | 2194 | N/A |  |  | N/A
Austin | TX | - | N/A |  |  | N/A |  |  | 1. Site was taken offline since 12/09/24 for equipment reinstallation as per customer's request and remained offline through the month. | 1. SR087694
Frisco | TX | 1588 | N/A |  |  | N/A |  |  | 1. 9 microinverters are not reporting from 11:35AM on 01/05 and remained throughtout the month. | 1. SR095523
Copperfield | TX | 971 | N/A |  |  | N/A |  |  | 1. 17 microinverters are not producing since 12/09/24 and also faulty CT at the meter due to a site configuration/mapping is wrong causing strings to be down, On 01/03/25, the technicien mentioned that the wires onsite were very brittle and replaced a few connectors and brought back online, The remaining work will be completed during PM 2025, as per the customer's request | 1. SR094284
Charlotte - B of A - 1 BAC | NC | - | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1. SR086583
Charlotte - B of A - 401 N Tryon | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1. SR086584
Chandler - B of A Campus Bldg A | AZ | 10791.25 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456
Chandler - B of A Campus Bldg B | AZ | 19506.5 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456
Chandler - B of A Campus Bldg C | AZ | 10495.3 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456
Chandler - B of A Campus Bldg D | AZ | 5978.87 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456
Tampa - BoA Ekman | FL | 72159.601 | N/A |  |  | N/A |  |  | 1. Inverter 4-1 back online at 13:30 on 01/10/25 after the technician performed reset inhibition. 2. Inverter 5-1 regained its communication on 01/09/25 after the technician replaced the communication board. 3. Inverter 5-2 was back online on 12/10/24, and Inverter 1-1 resumed communication. On 01/09/25, the technician found that Inverter 3 had a faulty communication board, which has been RMA'd. Additionally, Inverter 4-1 has been offline since 10/22/24. Following SMA instructions, the technician performed an operational reset inhibition and brought it back online the same day. | 1. SR095532, SR092433 2. SR091053 3. SR092433, SR095532
Charlotte - B of A - Sherrill | NC | [7 empty] | 1. Site is not found in Also Energy. The system is shut down (locked out) currently pending RSD Remediation | 1. SR086585

## Feb
JLL |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 38679.499 | 0 | 38679.499 | 0% | 0 | 38679.499 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ | 68.1 | N/A |  |  | N/A
Peoria | AZ | 62.3 | N/A |  |  | N/A |  |  | 1. Site was offline since 02/22/25 and remained offline throughout the month. | 1. SR097705
Tucson | AZ | 1684.7 | N/A |  |  | N/A
Hialeah | FL | -229.7 | N/A |  |  | N/A |  |  | 1. Site is reporting its production at the meter as a negative value, but inverter production is positive from 09/11, due to a faulty CT and its leads needed to be reversed to read positive production. | 1. SR090283
Jacksonville | FL | 83.3 | N/A |  |  | N/A
Miami Gardens | FL | 93.3 | N/A |  |  | N/A
Fort Myers | FL | 5014 | N/A |  |  | N/A
Orlando | FL | 3647.9 | N/A |  |  | N/A
Port St. Lucie | FL | 7313 | N/A |  |  | N/A |  |  | 1. 2 microinverters are not reporting and 1 microinverter is not producing since 01/22/25. Parts are needed to bring them back online. | 1. SR095856
Tampa | FL | 126.9 | N/A |  |  | N/A
Roswell | GA | 4102 | N/A |  |  | N/A |  |  | 1. 25 microinverters have been offline since 06/25. The Southwest microinverters are receiving AC voltage but not DC voltage, while the Northeast microinverters are not reporting, likely due to a breaker trip. | 1. SR087006
Charlotte | NC | 1718.1 | N/A |  |  | N/A
Raleigh | NC | 2029.8 | N/A |  |  | N/A |  |  | 1. Microinverters didn't report on 02/19 & 02/20, with minimal production due to a weather event. | 1. SR097570
Cordova | TN | 215.9 | N/A |  |  | N/A |  |  | 1. Two microinverters stopped reporting on 02/20 and self-resolved on 02/25. | 1. SR097571
Austin | TX | 147 | N/A |  |  | N/A |  |  | 1. Site was online for testing on 02/14, then offline from 02/15/25 for remaining equipment reinstallation per the customer's request. It came back online at 11:45 AM on 02/26/25 after passing the final inspection. | 1. SR087694
Frisco | TX | 1819 | N/A |  |  | N/A |  |  | 1. 9 microinverters were brought online at 10:35 AM on 02/07/2025 after the technician plugged in the 4-string connector during the PM event and reenergized the inverters. | 1. SR095523, PM9700 & SR097030 | SR097030
Copperfield | TX | 1076.9 | N/A |  |  | N/A |  |  | 1. 17 microinverters have not been producing since 12/09/24 due to a faulty CT at the meter caused by incorrect site configuration, resulting in downed strings. On 01/03/25, the technician replaced a few brittle connectors. During the PM event on 02/21/25, the technician corrected the C-phase CT wiring, but the meter is showing negative values and requires further troubleshooting. | 1.SR094284, PM9699 & SR097692 | SR097692
Charlotte - B of A - 1 BAC | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1. SR086583
Charlotte - B of A - 401 N Tryon | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1. SR086583
Chandler - B of A Campus Bldg A | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg B | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg C | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg D | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Tampa - BoA Ekman | FL | 9706.999 | N/A |  |  | N/A |  |  | 1. Inverter 4-1 back online at 13:30 on 01/10/25 after the technician performed reset inhibition. 2. Site was offline from at 09:30 on 02/05/25 due to an main breaker trip and remaind offline throughout the month. | 1. SR095532, SR092433 2. SR096384 | SR092433 | SR096384
Charlotte - B of A - Sherrill | NC | [7 empty] | 1. Site is not found in Also Energy. The system is shut down (locked out) currently pending RSD Remediation | 1. SR086585

## Mar
JLL |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 48444.053 | 0 | 48444.053 | 0% | 0 | 48444.053 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ | 104.8 | N/A |  |  | N/A
Peoria | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was offline since 02/22/25 and remained offline throughout the month. | 1. SR097705
Tucson | AZ | 1723.489 | N/A |  |  | N/A |  |  | 1. Site gateway not reporting since 03:30 on 03/25/25 and remained down throughout the month | 1. SR099003
Hialeah | FL | -326 | N/A |  |  | N/A |  |  | 1. Site is reporting its production at the meter as a negative value, but inverter production is positive from 09/11, due to a faulty CT and its leads needed to be reversed to read positive production. | 1. SR090283
Jacksonville | FL | 106.764 | N/A |  |  | N/A
Miami Gardens | FL | 118.2 | N/A |  |  | N/A
Fort Myers | FL | 6895.9 | N/A |  |  | N/A
Orlando | FL | 5379.2 | N/A |  |  | N/A
Port St. Lucie | FL | 10563.5 | N/A |  |  | N/A |  |  | 1. 2 microinverters are not reporting and 1 microinverter is not producing since 01/22/25. Parts are needed to bring them back online and on 03/20/25 holded WO. 2. One of the gateways (Gateway 122033008814) has not communicated since 03/31 at 21:06 EDT and later self resolved | 1. SR095856 2. SR099294(but looks good in enphase on those days verify once) | SR099294
Tampa | FL | 1894.2 | N/A |  |  | N/A |  |  | 1. 8 microinverters are reporting AC Voltage Low On 03/31/25 and later self resolved the same day. | 1. SR099197
Roswell | GA | 6039 | N/A |  |  | N/A |  |  | 1. 25 microinverters have been offline since 06/25. The Southwest microinverters are receiving AC voltage but not DC voltage, while the Northeast microinverters are not reporting, likely due to a breaker trip. | 1. SR087006
Charlotte | NC | 2482.7 | N/A |  |  | N/A
Raleigh | NC | 3223.4 | N/A |  |  | N/A |  |  | 1. All micros are communicating and producing from 03/27/25. 2. One microinverter (device ID 482126008076) has failed to report since 03/31/25. | 1. SR097570 2. SR099372 | SR099372
Cordova | TN | 3396.4 | N/A |  |  | N/A
Austin | TX | 2320.9 | N/A |  |  | N/A
Frisco | TX | 2875.5 | N/A |  |  | N/A
Copperfield | TX | 1646.1 | N/A |  |  | N/A |  |  | 1. 17 microinverters have not been producing since 12/09/24 due to a faulty CT at the meter caused by incorrect site configuration, resulting in downed strings. On 01/03/25, the technician replaced a few brittle connectors. During the PM event on 02/21/25, the technician corrected the C-phase CT wiring, but the meter is showing negative values and requires further troubleshooting. | 1.SR094284, PM9699 & SR097692 | SR097692
Charlotte - B of A - 1 BAC | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1. SR086583
Charlotte - B of A - 401 N Tryon | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1. SR086583
Chandler - B of A Campus Bldg A | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg B | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg C | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg D | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1. SR095935, SR095456 | SR095456
Tampa - BoA Ekman | FL | 0 | N/A |  |  | N/A |  |  | 1. Site was offline from at 09:30 on 02/05/25 due to an main breaker trip and remaind offline throughout the month. | 1. SR096384
Charlotte - B of A - Sherrill | NC | [7 empty] | 1. Site is not found in Also Energy. The system is shut down (locked out) currently pending RSD Remediation | 1. SR086585

## Apr
JLL |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 49082.34 | 0 | 49082.34 | 0% | 0 | 49082.34 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ | 137.8 | N/A |  |  | N/A
Peoria | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was offline since 02/22/25 and remained offline throughout the month. | 1. SR097705
Tucson | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site gateway not reporting since 03:30 on 03/25/25 and remained down throughout the month | 1. SR099003
Hialeah | FL | -353.61 | N/A |  |  | N/A |  |  | 1. Site is reporting its production at the meter as a negative value, but inverter production is positive from 09/11, due to a faulty CT and its leads needed to be reversed to read positive production. | 1. SR090283
Jacksonville | FL | 121.8 | N/A |  |  | N/A
Miami Gardens | FL | 123.1 | N/A |  |  | N/A
Fort Myers | FL | 7463.7 | N/A |  |  | N/A |  |  | 1. 104 microinverters are offline on 04/24 due to 'AC Voltage Low/Out of Range'. By 04/25, 2 microinverters were still reporting 'No Power,' while the rest had self-resolved. As of 04/30, 2 microinverters have been RMA'd. | 1. SR100345
Orlando | FL | 5943.75 | N/A |  |  | N/A
Port St. Lucie | FL | 11075.4 | N/A |  |  | N/A |  |  | 1. One of the gateways (Gateway 122033008814) has not communicated since 03/31 at 21:06 EDT and later self resolved 1. 26 microinverters are not reporting and 1 microinverter is not producing since 04/17. | 1. SR099294 2. SR095856 | SR095856
Tampa | FL | 2119.6 | N/A |  |  | N/A
Roswell | GA | 6565.7 | N/A |  |  | N/A |  |  | 1. 25 microinverters have been offline since 06/26/24. The southwest microinverters are receiving AC voltage but not DC voltage, while the northeast microinverters are not reporting, likely due to a breaker trip. By 04/17, 17 microinverters remained offline while the rest had self-resolved. As of 04/29, 25 microinverters are offline. | 1. SR087006
Charlotte | NC | 2476.1 | N/A |  |  | N/A
Raleigh | NC | 3441.2 | N/A |  |  | N/A |  |  | 1. One microinverter (Device ID: 482126008076) has failed to report since 03/31/25. On 04/15, the microinverter was under RMA'd. | 1. SR099372
Cordova | TN | 3846.5 | N/A |  |  | N/A
Austin | TX | 2067.9 | N/A |  |  | N/A
Frisco | TX | 2532.4 | N/A |  |  | N/A
Copperfield | TX | 1521 | N/A |  |  | N/A |  |  | 1. 17 microinverters have not been producing since 12/09/24 due to a faulty CT at the meter caused by incorrect site configuration, resulting in downed strings. On 01/03/25, the technician replaced a few brittle connectors. During the PM event on 02/21/25, the technician corrected the C-phase CT wiring, but the meter is showing negative values and requires further troubleshooting. | 1.SR094284, PM9699 & SR097692, SR101677 | SR097692 | SR101677
Charlotte - B of A - 1 BAC | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1.SR086583
Charlotte - B of A - 401 N Tryon | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1.SR086584
Chandler - B of A Campus Bldg A | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg B | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg C | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg D | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Tampa - BoA Ekman | FL | 0 | N/A |  |  | N/A |  |  | 1. Site was offline from at 09:30 on 02/05/25 due to an main breaker trip and remaind offline throughout the month. | 1. SR096384
Charlotte - B of A - Sherrill | NC |  | N/A |  |  | N/A |  |  | 1. Site is not found in Also Energy. The system is shut down (locked out) currently pending RSD Remediation | 1. SR086585

## May
JLL |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 44002 | 0 | 44002 | 0% | 0 | 44002 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ | 154.1 | N/A |  |  | N/A
Peoria | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site was offline since 02/22/25 and due to Pending Corrigo WO was denied by customer. | 1. SR097705
Tucson | AZ | 0 | N/A |  |  | N/A |  |  | 1. Site gateway not reporting since 03:30 on 03/25/25. | 1. SR099003
Hialeah | FL | -3571.9 | N/A |  |  | N/A |  |  | 1. Site is reporting its production at the meter as a negative value, but inverter production is positive from 09/11, due to a faulty CT and its leads needed to be reversed to read positive production. | 1. SR090283
Jacksonville | FL | 119.7 | N/A |  |  | N/A
Miami Gardens | FL | 126 | N/A |  |  | N/A
Fort Myers | FL | 7300.5 | N/A |  |  | N/A |  |  | 1. 104 microinverters are offline on 04/24 due to 'AC Voltage Low/Out of Range'. By 04/25, 2 microinverters were still reporting 'No Power,' while the rest had self-resolved. As of 04/30, 2 microinverters have been RMA'd. | 1. SR100345
Orlando | FL | 5806.3 | N/A |  |  | N/A
Port St. Lucie | FL | 9773.3 | N/A |  |  | N/A |  |  | 1. 26 microinverters are not reporting and 1 microinverter is not producing since 04/17. 2. Both gateways (Gateway 122033008814, 122033006173) has not communicated since 05/08 at 11:58 EDT and later self resolved on 05/14. | 1. SR095856 2. SR101165 | SR101165
Tampa | FL | 2046.5 | N/A |  |  | N/A
Roswell | GA | 6280.2 | N/A |  |  | N/A |  |  | 1. 25 microinverters have not been reporting and are possibly offline since 04/29. | 1. SR087006
Charlotte | NC | 2322 | N/A |  |  | N/A
Raleigh | NC | 3235.5 | N/A |  |  | N/A |  |  | 1. One microinverter (Device ID: 482126008076) has failed to report since 03/31/25. On 04/15, the microinverter was under RMA'd. | 1. SR099372
Cordova | TN | 3486.7 | N/A |  |  | N/A
Austin | TX | 2296.2 | N/A |  |  | N/A
Frisco | TX | 2969.8 | N/A |  |  | N/A
Copperfield | TX | 1657.1 | N/A |  |  | N/A |  |  | 1. 17 microinverters have not been producing since 12/09/24 due to a faulty CT at the meter caused by incorrect site configuration, resulting in downed strings. On 01/03/25, the technician replaced a few brittle connectors. During the PM event on 02/21/25, the technician corrected the C-phase CT wiring, but the meter is showing negative values and requires further troubleshooting. | 1.1.SR094284, PM9699 & SR097692, SR101677 | SR097692 | SR101677
Charlotte - B of A - 1 BAC | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1.SR086583
Charlotte - B of A - 401 N Tryon | NC | 0 | N/A |  |  | N/A |  |  | 1. No site comms to DAS since 4/26/23. The system is shut down (locked out) currently pending RSD Remediation. | 1.SR086584
Chandler - B of A Campus Bldg A | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg B | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg C | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Chandler - B of A Campus Bldg D | AZ | 0 | N/A |  |  | N/A |  |  | 1.Site was de-energized on 01/09/2025 at 18:00 due to a serious electrical grounding hazard and remained offline throughout the month. | 1.SR095935, SR095456 | SR095456
Tampa - BoA Ekman | FL | 0 | N/A |  |  | N/A |  |  | 1. Site was offline from at 09:30 on 02/05/25 due to an main breaker trip and remaind offline throughout the month. | 1. SR096384
Charlotte - B of A - Sherrill | NC | 0 | N/A |  |  | N/A |  |  | 1. Site is not found in Also Energy. The system is shut down (locked out) currently pending RSD Remediation | 1. SR086585

## Jun
JLL |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ |  | 0 |  |  | 0
Peoria | AZ |  | 0 |  |  | 0 |  |  | 1.Site is not communicating
Tucson | AZ |  | 0 |  |  | 0 |  |  | 1.Site is not communicating
Hialeah | FL
Jacksonville | FL
Miami Gardens | FL
Fort Myers | FL
Orlando | FL
Port St. Lucie | FL
Tampa | FL
Roswell | GA
Charlotte | NC
Raleigh | NC
Cordova | TN
Austin | TX
Frisco | TX
Copperfield | TX
Charlotte - B of A - 1 BAC | NC
Charlotte - B of A - 401 N Tryon | NC
Chandler - B of A Campus Bldg A | AZ
Chandler - B of A Campus Bldg B | AZ
Chandler - B of A Campus Bldg C | AZ
Chandler - B of A Campus Bldg D | AZ
Tampa - BoA Ekman | FL
Charlotte - B of A - Sherrill | NC

## Jul
JLL |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ |  | 0 |  |  | 0
Peoria | AZ |  | 0 |  |  | 0
Tucson | AZ |  | 0 |  |  | 0 |  |  | 1. Gateway has not reported since 7/27. | 1. SR091354
Hialeah | FL
Jacksonville | FL
Miami Gardens | FL
Fort Myers | FL
Orlando | FL
Port St. Lucie | FL
Tampa | FL
Roswell | GA
Charlotte | NC
Raleigh | NC
Cordova | TN
Austin | TX
Frisco | TX
Copperfield | TX
Charlotte - B of A - 1 BAC | NC
Charlotte - B of A - 401 N Tryon | NC
Chandler - B of A Campus Bldg A | AZ
Chandler - B of A Campus Bldg B | AZ
Chandler - B of A Campus Bldg C | AZ
Chandler - B of A Campus Bldg D | AZ
Tampa - BoA Ekman | FL
Charlotte - B of A - Sherrill | NC

## Aug
JLL |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ |  | 0 |  |  | 0
Peoria | AZ |  | 0 |  |  | 0
Tucson | AZ |  | 0 |  |  | 0 |  |  | 1. Gateway has not reported since 7/27. | 1. SR091354
Hialeah | FL
Jacksonville | FL
Miami Gardens | FL
Fort Myers | FL
Orlando | FL
Port St. Lucie | FL
Tampa | FL
Roswell | GA
Charlotte | NC
Raleigh | NC
Cordova | TN
Austin | TX
Frisco | TX
Copperfield | TX
Charlotte - B of A - 1 BAC | NC
Charlotte - B of A - 401 N Tryon | NC
Chandler - B of A Campus Bldg A | AZ
Chandler - B of A Campus Bldg B | AZ
Chandler - B of A Campus Bldg C | AZ
Chandler - B of A Campus Bldg D | AZ
Tampa - BoA Ekman | FL
Charlotte - B of A - Sherrill | NC

## Sep
JLL |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ |  | 0 |  |  | 0
Peoria | AZ |  | 0 |  |  | 0
Tucson | AZ |  | 0 |  |  | 0 |  |  | 1. Gateway has not reported since 7/27. | 1. SR091354
Hialeah | FL
Jacksonville | FL
Miami Gardens | FL
Fort Myers | FL
Orlando | FL
Port St. Lucie | FL
Tampa | FL
Roswell | GA
Charlotte | NC
Raleigh | NC
Cordova | TN
Austin | TX
Frisco | TX
Copperfield | TX
Charlotte - B of A - 1 BAC | NC
Charlotte - B of A - 401 N Tryon | NC
Chandler - B of A Campus Bldg A | AZ
Chandler - B of A Campus Bldg B | AZ
Chandler - B of A Campus Bldg C | AZ
Chandler - B of A Campus Bldg D | AZ
Tampa - BoA Ekman | FL
Charlotte - B of A - Sherrill | NC

## Oct
JLL |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ |  | 0 |  |  | 0
Peoria | AZ |  | 0 |  |  | 0
Tucson | AZ |  | 0 |  |  | 0 |  |  | 1. Site experienced daily power generation off by command alerts from 11/14/24. wassue resolved on 11/24 | 1. SR093471
Hialeah | FL
Jacksonville | FL
Miami Gardens | FL
Fort Myers | FL
Orlando | FL
Port St. Lucie | FL
Tampa | FL
Roswell | GA
Charlotte | NC
Raleigh | NC
Cordova | TN
Austin | TX
Frisco | TX
Copperfield | TX
Charlotte - B of A - 1 BAC | NC
Charlotte - B of A - 401 N Tryon | NC
Chandler - B of A Campus Bldg A | AZ
Chandler - B of A Campus Bldg B | AZ
Chandler - B of A Campus Bldg C | AZ
Chandler - B of A Campus Bldg D | AZ
Tampa - BoA Ekman | FL
Charlotte - B of A - Sherrill | NC

## Nov
JLL |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ |  | 0 |  |  | 0
Peoria | AZ |  | 0 |  |  | 0
Tucson | AZ |  | 0 |  |  | 0 |  |  | 1. SIte regained communication on 11/14 | 1. SR091354
Hialeah | FL
Jacksonville | FL
Miami Gardens | FL
Fort Myers | FL
Orlando | FL
Port St. Lucie | FL
Tampa | FL
Roswell | GA
Charlotte | NC
Raleigh | NC
Cordova | TN
Austin | TX
Frisco | TX
Copperfield | TX
Charlotte - B of A - 1 BAC | NC
Charlotte - B of A - 401 N Tryon | NC
Chandler - B of A Campus Bldg A | AZ
Chandler - B of A Campus Bldg B | AZ
Chandler - B of A Campus Bldg C | AZ
Chandler - B of A Campus Bldg D | AZ
Tampa - BoA Ekman | FL
Charlotte - B of A - Sherrill | NC

## Dec
JLL |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Bullhead | AZ |  | 0 |  |  | 0
Peoria | AZ |  | 0 |  |  | 0
Tucson | AZ |  | 0 |  |  | 0
Hialeah | FL
Jacksonville | FL
Miami Gardens | FL
Fort Myers | FL
Orlando | FL
Port St. Lucie | FL
Tampa | FL
Roswell | GA
Charlotte | NC
Raleigh | NC
Cordova | TN
Austin | TX
Frisco | TX
Copperfield | TX
Charlotte - B of A - 1 BAC | NC
Charlotte - B of A - 401 N Tryon | NC
Chandler - B of A Campus Bldg A | AZ
Chandler - B of A Campus Bldg B | AZ
Chandler - B of A Campus Bldg C | AZ
Chandler - B of A Campus Bldg D | AZ
Tampa - BoA Ekman | FL
Charlotte - B of A - Sherrill | NC

## Sites
Portfolio: | JLL
Site DAS Name | Site | State | Update | DAS
Bank of America - AZW-167 (Bullhead City, AZ) | Bullhead | AZ |  | Enlighten
Bank of America - AZW-166 (Peoria, AZ) | Peoria | AZ |  | Enlighten
Bank of America - AZ5-135 (Midvale Park, AZ) | Tucson | AZ |  | Enlighten
Bank of America - FL7-551 (Hialeah Miami Springs, FL) | Hialeah | FL |  | Enlighten
Bank of America - FLW-B75 (Jacksonville, FL) | Jacksonville | FL |  | Enlighten
Bank of America - FLW-B89 (Miami Gardens, FL) | Miami Gardens | FL |  | Enlighten
Bank of America - FL4-199 (North Fort Myers, FL) | Fort Myers | FL |  | Enlighten
Bank of America - FLW-D01 (Orlando, FL) | Orlando | FL |  | Enlighten
Bank of America - FL5-644 (Port St. Lucie, FL) | Port St. Lucie | FL |  | Enlighten
Bank of America - FL2-201 (Tampa, FL) | Tampa | FL |  | Enlighten
Bank of America - GA7-247 (Roswell, GA) | Roswell | GA |  | Enlighten
Bank of America - NC2-225 (Charlotte, NC) | Charlotte | NC |  | Enlighten
Bank of America - NC7-430 (Raleigh, NC) | Raleigh | NC |  | Enlighten
Bank of America - TN3-844 (Cordova, TN) | Cordova | TN |  | Enlighten
Bank of America - TX9-794 (Austin, TX) | Austin | TX |  | Enlighten
Bank of America - TX2-736 (Frisco, TX) | Frisco | TX |  | Enlighten
Bank of America - TX5-204 (Copperfield, TX) (240 VAC High Leg Delta) (FC - Copperfield (High Leg Delta)) | Copperfield | TX |  | Enlighten
150 North College St - Bank of America Corporation | Charlotte - B of A - 1 BAC | NC |  | Power Track
401 North Tryon St - Bank of America Corporation | Charlotte - B of A - 401 N Tryon | NC |  | Power Track
B of A Chandler - Building A | Chandler - B of A Campus Bldg A | AZ |  | Power Track
B of A Chandler - Building B | Chandler - B of A Campus Bldg B | AZ |  | Power Track
B of A Chandler - Building C1 (Rooftop) | Chandler - B of A Campus Bldg C | AZ |  | Power Track
B of A Chandler - Building D1 (Rooftop) | Chandler - B of A Campus Bldg D | AZ |  | Power Track
Bank of America FL | Tampa - BoA Ekman | FL |  | Power Track
Charlotte - B of A - Sherrill | Charlotte - B of A - Sherrill | NC |  | Power Track