## Year to Date
True Green Capital Management LLC |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 10941069.0056 | 9669983.5 | 1271085.5056 | 13.14% | 12328063.1 | -1386994.0944 | -11.25%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 5343616 | 5701533.7 | -357917.7 | -6.278% | 5784347.8 | -440731.8 | -7.619%
Warsaw - Hemings | VA | 2666589.2 | 2169665.9 | 496923.3 | 22.9% | 2851822.2 | -185233 | -6.495%
Mount Jackson - Randolf | VA | 1487657.3056 | 1604813.6 | -117156.2944 | -7.3% | 1884738 | -397080.6944 | -21.07%
Callands Gretna - Monroe | VA | 1235996 | 193970.3 | 1042025.7 | 537.2% | 1269470.1 | -33474.1 | -2.637%
Rockbridge Baths - Small Mouth Bass | VA | 207210.5 | 0 | 207210.5 |  | 537685 | -330474.5 | -61.46%

## 1st Qtr
True Green Capital Management LLC |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 2648764.2 | 2517326.9 | 131437.3 | 5.221% | 2572633.7 | 76130.5 | 2.959%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 1225301 | 1270191.7 | -44890.7 | -3.534% | 1235871.8 | -10570.8 | -0.8553%
Warsaw - Hemings | VA | 682045.5 | 732528.3 | -50482.8 | -6.892% | 626767.2 | 55278.3 | 8.82%
Mount Jackson - Randolf | VA | 415293.7 | 440760.6 | -25466.9 | -5.778% | 428529 | -13235.3 | -3.089%
Callands Gretna - Monroe | VA | 326124 | 73846.3 | 252277.7 | 341.6% | 281465.7 | 44658.3 | 15.87%
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
True Green Capital Management LLC |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 8292304.8056 | 7152656.6 | 1139648.2056 | 15.93% | 9755429.4 | -1463124.5944 | -15%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 4118315 | 4431342 | -313027 | -7.064% | 4548476 | -430161 | -9.457%
Warsaw - Hemings | VA | 1984543.7 | 1437137.6 | 547406.1 | 38.09% | 2225055 | -240511.3 | -10.81%
Mount Jackson - Randolf | VA | 1072363.6056 | 1164053 | -91689.3944 | -7.877% | 1456209 | -383845.3944 | -26.36%
Callands Gretna - Monroe | VA | 909872 | 120124 | 789748 | 657.4% | 988004.4 | -78132.4 | -7.908%
Rockbridge Baths - Small Mouth Bass | VA | 207210.5 | 0 | 207210.5 |  | 537685 | -330474.5 | -61.46%

## 3rd Qtr
True Green Capital Management LLC |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 0 | 0 | 0 |  | 0 | 0
Warsaw - Hemings | VA | 0 | 0 | 0 |  | 0 | 0
Mount Jackson - Randolf | VA | 0 | 0 | 0 |  | 0 | 0
Callands Gretna - Monroe | VA | 0 | 0 | 0 |  | 0 | 0
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
True Green Capital Management LLC |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Rochester - 5516 Valleyhigh NW | MN | 0 | 0 | 0 |  | 0 | 0
Warsaw - Hemings | VA | 0 | 0 | 0 |  | 0 | 0
Mount Jackson - Randolf | VA | 0 | 0 | 0 |  | 0 | 0
Callands Gretna - Monroe | VA | 0 | 0 | 0 |  | 0 | 0
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## Jan
True Green Capital Management LLC |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Feb
True Green Capital Management LLC |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Mar
True Green Capital Management LLC |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 2648764.2 | 2517326.9 | 131437.3 | 5.221% | 2572633.7 | 76130.5 | 2.959%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW |  | 1225301 | 1270191.7 | -44890.7 | -3.534% | 1235871.8 | -10570.8 | -0.8553% | 1.Inverter 13 has been underproducing by approximately 30 kW compared to its peers since the MC4 connectors were replaced in early December 2024 to resolve ongoing tripping issues. On 03/11, technician replaced 3 fuses with no continuity and inverter started producing inline with peers. 2.Inverter 28 tripped offline at 12:15PM on 03/31 due to permanent fault of power module - Fault0010 and Power Module Protection - Protect0120. 3.Strings down on inverters 29 and 30 from 03/17. 4.Inverter 66 tripped offline at 16:15 on 03/31 due to AC SPD Fault. 5.Inverter 64 was offline from 12/18/24 which was LOTO'd. 6.Inverters 29, 30, 64, 68, 69, 78,79 and 80 are offline from 12/26/24 and confirmed with Hunt these inverters are LOTOd and back online at 12:15PM on 03/17. 7.Soltec Tracker Full T01: Motors 22, 77, 138 were stuck. Soltec Tracker Full T02: Motors 4, 21, 23, 32, 37, 58, 61, 83 were stuck. Soltec Tracker Full T03: Motors 13, 52 were stuck. Soltec Tracker Full T04: Motors 1, 11, 27, 28, 29, 32, 39, 51, 57, 65, 75, 88, 94, 112, 113 were stuck. 8. Energy values are updated from 03/11 , and till 03/10 the data is in Ecofin client templete. | 1.SR098364 2.SR099220 3.SR099222 4.SR099295 5.SR099221 6.SR095849 7.SR099224 | SR099220 | SR099222 | SR099295 | SR099221 | SR095849 | SR099224
Warsaw - Hemings |  | 682045.5 | 732528.3 | -50482.8 | -6.892% | 626767.2 | 55278.3 | 8.82% | 1.Inverter 21 was derating approximately by 50KW due to external fan fault on high irradiance days. Additionally 5 trackers were stuck. 2.Energy values are updated from 03/11 , and till 03/10 the data is in Ecofin client templete. | 1.SR097728,SR098569, SR096181 & SR098568. | SR098569 | SR096181 | SR098568
Mount Jackson - Randolf |  | 415293.7 | 440760.6 | -25466.9 | -5.778% | 428529 | -13235.3 | -3.089% | 1.Inverter 15 tripped offline at 14:30 on 03/11 due to Inverter Over Current and self-resolved and back online on 03/12. 2.Inverter 18 tripped offline at 12:15PM on 03/22 due to Inverter Over Current - ProtectOO30 and self resolved and back online on 03/23. On 03/26, technician performed firmware upgrade for inverter. 3.All inverters tripped offline from 13:15 on 03/29 due to Grid Phase Voltage Out of Range - GridV.OutLim fault additionally meter stopped communicating. 4.NCU 1 motors 10 and 46 were stuck. On 03/17, the technician ran several reset commands via the Mission Control dashboard—motor 10 resumed tracking, while motor 46 remained stuck and requires motor replacement. 5.NCU 2 motor 7 was stuck and motor was being RMA'd 6.Site tripped tripped offline on 03/16 at 14:15, and later back online on 03/17 (We started monitoring these sites again from 03/21 as per the information provided. Due to this we dont have any SR's for this issue.). 7.Inverter 7 tripped offline at 15:15 on 03/17 and back online on 03/18. (We started monitoring these sites again from 03/21 as per the information provided.Due to this we dont have any SR's for this issue.). 8.Energy values are updated from 03/11 , and till 03/10 the data is in Ecofin client templete. | 1.SR098302 2.SR098925 3.SR099141 4.SR097757 5.SR098566 | SR098925 | SR099141 | SR097757 | SR098566
Callands Gretna - Monroe |  | 326124 | 73846.3 | 252277.7 | 341.6% | 281465.7 | 44658.3 | 15.87% | 1.Hukseflux SR15-D1-POA & Huskseflux SR15-D1-BPOA stopped communicating from 03/16/25. Huskseflux SR15-D1-BPOA has resumed communication on 03/29. 2.Energy values are updated from 03/11 , and till 03/10 the data is in Ecofin client templete. | 1.SR099420
Rockbridge Baths - Small Mouth Bass |  | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month due to bad modem. | 1.SR097305 & SR098700 | SR098700

## Apr
True Green Capital Management LLC |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 3804632.0056 | 3568997.8 | 235634.2056 | 6.602% | 4304859.3 | -500227.2944 | -11.62%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW |  | 1778353 | 1925780 | -147427 | -7.655% | 2098765 | -320412 | -15.27% | 1.Inverter 28 tripped offline at 12:15 on 03/31 due to a permanent power module fault (Fault0010) and Power Module Protection error (Protect0120). The technician initiated an RMA for the powerhead on 04/07 and replaced it with a new unit on 04/24. The inverter is back online and producing in line with its peers. 2.Inverter 64 was offline from 12/18/24 which was LOTO'd. 3.Inverters 29 and 30 have strings down due to missing panels caused by storm damage. 4.Inverter 66 tripped offline at 16:15 on 03/31 due to an AC SPD fault. The technician RMA’d the powerhead on 04/07 and replaced it with a new one on 04/11. The inverter is now back online and producing normally. 5.Inverter 50 tripped offline at 09:45 on 04/12 due to Permanent fault of power module - Fault0010 Power Module Protection - Protect0120 fault. On 04/14 technician RMA'D powerhead of the inverter and on 04/24 technician replaced with new powerhead and inverter started for production according to peers. 6.Inverter 36 tripped offline at 14:15 on 04/15 due to Bus (sum) Over Voltage (firmware) - Protect0090. On 04/24, Technicians responded to a permanent power failure. Chint was contacted for an RMA, and the inverter was replaced using a spare from inventory. The unit has been commissioned and is now producing power. 7.Inverter 42 was tripped offline at 16:30 on 04/16 due to Bus Imbalance - Protect0070 fault. On 04/24, Technicians responded to a permanent power failure. Chint was contacted for an RMA, and the inverter was replaced using a spare from inventory. The unit has been commissioned and is now producing power. 8.Soltec Tracker Full T01: Motors 22, 77, 138 were stuck. Soltec Tracker Full T02: Motors 4, 21, 23, 32, 37, 58, 61, 83 were stuck. Soltec Tracker Full T03: Motors 13, 52 were stuck. Soltec Tracker Full T04: Motors 1, 11, 27, 28, 29, 32, 39, 51, 57, 65, 75, 88, 94, 112, 113 were stuck. | 1.SR099220 2.SR099221 3.SR099222 4.SR099295 5.SR099759 6.SR099835 7.SR099913 8.SR099224 | SR099221 | SR099222 | SR099295 | SR099759 | SR099835 | SR099913 | SR099224
Warsaw - Hemings |  | 997106.8 | 1042780 | -45673.2 | -4.38% | 1046855 | -49748.2 | -4.752% | 1.Inverter 21 was derating by 50 kW from 02/24 due to an "External Fan Error" fault. This issue occurred on days with high irradiance and was resolved on 04/22 after the technician replaced the faulted fan. 2.Mutiple trackers are stuck, and Solectria is actively working on troubleshooting the issue. | 1.SR098569,SR099625 2.SR098568,SR098376, | SR099625 | SR098568 | SR098376
Mount Jackson - Randolf |  | 563764.2056 | 600437.8 | -36673.5944 | -6.108% | 698984.1 | -135219.8944 | -19.35% | 1. Site tripped offline at 11:45 on 03/31 due to blown MV fuse and back online at 12:15 on 04/03 after technician along with MV crew replaced MV fuse and utility re-energized the site. 2.Inverter 18 was tripped offline at 11:30 on 04/16 due to Inverter Over Current fault and back online on 04/17. 3.Inverter 15 tripped offline at 13:00 on 04/21 due to an Inverter Over Current fault and was back online on 04/22. It tripped again at 15:00 on 04/28 with the same fault and was restored on 04/29. 4.Site tripped offline at 15:56 on 04/27 due to Grid Phase Voltage Out of Range - GridV.OutLim fault and back online at 13:30 on 04/28. 5.Inverter 7 tripped offline at 18:00 on 04/29 due to Inverter Over Current fault and back online on 04/30. 6.NCU 2 motor 7 was stuck and motor was being RMA'd and on 04/17/25, the technician confirmed a defective tracker motor, replaced it, power cycled the controller, cleared the fault in Mission Control, and verified the tracker is now operating correctly with its peers. | 1.SR099141 2.SR099914 3.SR100087 & SR100473 4.SR100473 5.SR100673 6.SR098566 | SR099914 | SR100087 | SR100473 | SR100473 | SR100673 | SR098566
Callands Gretna - Monroe |  | 465408 | 0 | 465408 |  | 460255.2 | 5152.8 | 1.12% | 1.On 04/18 the technician attempted to add a new tracker using the Soltec computer onsite, but the system showed it wasn't connected to the server. The previously installed tracker (C30) remains in stow and Soltec has not responded. 2.The POA sensor (Hukseflux SR15-D1-POA) stopped communicating on 03/16/25 due to a fault and is currently being RMA'd. Additionally, the wire for the BPOA was found to be damaged. | 1.SR098567 2.SR099419 & SR099420 | SR099419 | SR099420
Rockbridge Baths - Small Mouth Bass |  | 0 | 0 |  |  | 0 |  |  | 1. Site was not communicated for whole month due to bad modem. 2. Inverter 19 all 3 external fans were RMA'D due to external fan fault. 3. The client reported that the site tripped offline between 10:30 AM and 11:30 AM on 04/23 and was producing at a steady but low output of 23.824 kW. Normal production resumed on 04/24, but data backfilling is progressing slowly with 4,962,922 files in the queue. Confirmation is needed to proceed with the internet provider switch. 4.Stuck tracker reported by Nick Lindsholm. Troubleshooting will proceed once communication is restored. A Soltec ticket cannot be created until the serial number of the affected unit is identified. | 1.SR097305 & SR098700 2.SR099878 3.SR100221 4.SR100415 | SR098700 | SR099878 | SR100221 | SR100415

## May
True Green Capital Management LLC |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 4487672.8 | 3583658.8 | 904014 | 25.23% | 5450570.1 | -962897.3 | -17.67%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW |  | 2339962 | 2505562 | -165600 | -6.609% | 2449711 | -109749 | -4.48% | 1. Site production was low on 05/25, 05/26, 05/27, 05/28 due to technician was on site for preventive maintenance work. 2. Inverter 58 tripped offline at 11:30 on 05/03 due to a "Permanent Fault of Power Module". A technician later replaced the power head on site, and the inverter came back online at 08:45 on 05/05. 3. Inverter 14 tripped offline at 10:15 on 05/06 due to "Permanent fault of power module - Fault0010". Later, a technician on site replaced the power head, and the inverter came back online at 09:30 on 05/08. 4. Inverter 21 tripped offline at 10:12 on 05/13 due to "Grid Line Voltage Out of Range - GridV.OutLim". Later, a technician on site power-cycled the inverter, and it came back online at 17:04 on 05/13. 5. Inverter 72 tripped offline at 17:30 on 05/23 due to "Permanent fault of power module - Fault0010, Power Module Protection - Protect0120". Later, with support from Chint, the technician was able to remotely reset the inverter, and it came back online at 13:30 on 05/27. 6. Inverter 72 tripped offline at 11:06 on 05/29 due to "Permanent fault of power module - Fault0010, Power Module Protection - Protect0120". Inverter RMA dispatch has been scheduled for the month of June | 1. PM9696 2. SR100960 3. SR101064 4. SR101885 5. SR101923 6. SR102146 | SR101064 | SR101885 | SR101923 | SR102146
Warsaw - Hemings |  | 987436.9 | 394357.6 | 593079.3 | 150.4% | 1178200 | -190763.1 | -16.19% | 1. The weather station Hukseflux SR15 – POA has been communicating intermittently since 05/14. | 1. SR102509
Mount Jackson - Randolf |  | 508599.4 | 563615.2 | -55015.8 | -9.761% | 757224.9 | -248625.5 | -32.83% | 1. Inverter 15 tripped offline at 14:40 on 05/07 due to 'Inverter Over Current - Protect0030' and came back online at 06:00 on 05/08. 2. The site tripped offline due to "Grid Phase Voltage Out of Range - GridV.OutLim" at 10:45 on 05/10 and came back online at 07:15 on 05/12. 3. The site tripped offline due to "Grid Phase Voltage Out of Range - GridV.OutLim" at 11:15 on 05/24 and came back online at 11:03 on 05/27. | 1. SR100087 2. SR100473 3. SR101911 | SR100473 | SR101911
Callands Gretna - Monroe |  | 444464 | 120124 | 324340 | 270% | 527749.2 | -83285.2 | -15.78% | 1. The Hukseflux SR15-D1-BPOA had intermittent communication since 03/16. During a site visit on 05/22, the technician found the SCADA was defective, installed a new one, and stated that the BPOA will remain offline until the correct cable is installed. Additional troubleshooting was also recommended. | 1. SR099420
Rockbridge Baths - Small Mouth Bass |  | 207210.5 | 0 | 207210.5 |  | 537685 | -330474.5 | -61.46% | 1. The site has been experiencing a power quality issue affecting generation since 05/10. | 1. SR101462

## Jun
True Green Capital Management LLC |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Jul
True Green Capital Management LLC |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Aug
True Green Capital Management LLC |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Sep
True Green Capital Management LLC |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Oct
True Green Capital Management LLC |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Nov
True Green Capital Management LLC |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Dec
True Green Capital Management LLC |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Rochester - 5516 Valleyhigh NW
Warsaw - Hemings
Mount Jackson - Randolf
Callands Gretna - Monroe
Rockbridge Baths - Small Mouth Bass

## Sites
Portfolio: | True Green Capital Management LLC
Site DAS Name | Site | State | Update | DAS
Fund IV - WestSide Solar MN | Rochester - 5516 Valleyhigh NW | MN | AEF | Powertrack
Fund IV - Hemings | Warsaw - Hemings | VA | AEF | Powertrack
Fund IV - Randolf | Mount Jackson - Randolf | VA | AEF | Powertrack
Fund IV - Monroe Solar | Callands Gretna - Monroe | VA | AEF | Powertrack
Fund IV - Smallmouth Bass | Rockbridge Baths - Small Mouth Bass | VA | AEF | Powertrack