## Year to Date
Altus Power |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 6494080 | 11470722.072 | -4976642.072 | -43.39% | 11480146.63 | -4986066.63 | -43.43%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Pratt Solar Farm | KS | 6494080 | 11470722.072 | -4976642.072 | -43.39% | 11480146.63 | -4986066.63 | -43.43%

## 1st Qtr
Altus Power |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 1654930 | 3097059.909 | -1442129.909 | -46.56% | 2716093.93 | -1061163.93 | -39.07%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Pratt Solar Farm | KS | 1654930 | 3097059.909 | -1442129.909 | -46.56% | 2716093.93 | -1061163.93 | -39.07%

## 2nd Qtr
Altus Power |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 1996740 | 3212449.46 | -1215709.46 | -37.84% | 3399757.06 | -1403017.06 | -41.27%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Pratt Solar Farm | KS | 1996740 | 3212449.46 | -1215709.46 | -37.84% | 3399757.06 | -1403017.06 | -41.27%

## 3rd Qtr
Altus Power |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 1658850 | 3252416.119 | -1593566.119 | -49% | 3435205.41 | -1776355.41 | -51.71%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Pratt Solar Farm | KS | 1658850 | 3252416.119 | -1593566.119 | -49% | 3435205.41 | -1776355.41 | -51.71%

## 4th Qtr
Altus Power |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 1183560 | 1908796.584 | -725236.584 | -37.99% | 1929090.23 | -745530.23 | -38.65%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Pratt Solar Farm | KS | 1183560 | 1908796.584 | -725236.584 | -37.99% | 1929090.23 | -745530.23 | -38.65%

## Jan
Altus Power |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 641110 | 959485.1 | -318375.1 | -33.18% | 865991.1 | -224881.1 | -25.97%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 641110 | 959485.1 | -318375.1 | -33.18% | 865991.1 | -224881.1 | -25.97% | 1. Inverter 1 is derating by 1000kW due to Impulsion fan comms issue from 11/20 | 1.SR093458

## Feb
Altus Power |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 609030 | 919002.6 | -309972.6 | -33.73% | 811213.8 | -202183.8 | -24.92%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 609030 | 919002.6 | -309972.6 | -33.73% | 811213.8 | -202183.8 | -24.92% | 1. Inverter 1 is derating by 1000kW due to Impulsion fan comms issue since 11/20. Waiting on DGA syringe to group with the dispatch. | 1.SR093458

## Mar
Altus Power |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 404790 | 1218572.209 | -813782.209 | -66.78% | 1038889.03 | -634099.03 | -61.04%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 404790 | 1218572.209 | -813782.209 | -66.78% | 1038889.03 | -634099.03 | -61.04% | 1.Inverter 1 was derating by 1000kw due to Impulsion fan Comms issue since 11/20/24. On 03/04, technician replaced bad exhaust fan with new fan and re-energized the inverter but didn't have the required software needed to configure it for proper operation. Again inverter started derating by 1.7MW due to fan fault from 03/29. 2.Inverter 1 tripped offline at 13:45 on 03/15 due to Fault:197 and back online at 11AM on 03/16 again tripped offline at 12:30 on 03/16 and back online by remote reset at 10:15AM on 03/17. Again tripped offline at 12PM on 03/21 and self resolved and back online on 03/24. 3.Inverter 2 was offline from 03/07 due to Isolation fault and was offline through out the month. | 1.SR093458 & SR099185 2.SR098335 3.SR098248 | SR099185 | SR098335 | SR098248

## Apr
Altus Power |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 323630 | 1020112 | -696482 | -68.28% | 1092313 | -768683 | -70.37%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 323630 | 1020112 | -696482 | -68.28% | 1092313 | -768683 | -70.37% | 1. Inverter 1 was derating for whole month fan being replaced and during visit on 04/14 technician found twelve AC capacitors requiring replacement. 2. Inverter 2 was tripped offline on 04/06 at 18:00 due to GFDI. inverter 2 needs DC contactors and possibly capacitors. | 1. SR099994, SR099185 2.SR099478 | SR099185 | SR099478

## May
Altus Power |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 610590 | 1070510 | -459920 | -42.96% | 1172680 | -562090 | -47.93%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 610590 | 1070510 | -459920 | -42.96% | 1172680 | -562090 | -47.93% | 1. Inverter B tripped offline on 04/06 at 18:00 due to a GFDI fault. The inverter requires new DC contactors and possibly capacitors. A technician visited the site on 05/15, installed a new LS filter, and de-energized the inverter; it came back online at 12:00 the same day.Later, on 05/21 at 07:00, Inverter B tripped offline again, reporting an F45 insulation fault. It was remotely reset and came back online at 14:00. Additionally, on 05/22, Inverter B was offline again from 08:45 to 10:30 due to Pratt being on site to replace the SEL-651R reclosing relay on the inverter. 2. Inverter A was derated by 1000KW down on 05/15 at 09:15 technician took the inverter offline to replace capacitors and exhaust fan. later inverter was re-energized at EOD. Additionally, Inverter A was offline from 15:30 to 17:15 on 05/17 while a technician was on site and performing preventive maintenance inspection. Inverter A was intermittently tripping on and off throughout the day on 05/30. | 1. SR099478 SR101785, SR101822 2. SR099994, SR099185, SR102003, SR102210 PM8642 | SR101785 | SR101822 | SR099994 | SR099185 | SR102003 | SR102210

## Jun
Altus Power |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 1062520 | 1121827.46 | -59307.46 | -5.287% | 1134764.06 | -72244.06 | -6.366%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 1062520 | 1121827.46 | -59307.46 | -5.287% | 1134764.06 | -72244.06 | -6.366% | 1. Inverter 1 has tripped offline at 19:26 on 06/03 and is reporting "GFDI fuse or fuse holder open." Inverter 1 came back online at 10:15 on 06/04. 2.Inverter 2 started production late at 15:15 on 06/24, and has been derating by 500 kW since 06/15 3.Inverter 1 offline from 06/30 | 1.SR102433 2.SR103157 3.SR103746 | SR103157 | SR103746

## Jul
Altus Power |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 477710 | 1137108.382 | -659398.382 | -57.99% | 1189387.36 | -711677.36 | -59.84%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 477710 | 1137108.382 | -659398.382 | -57.99% | 1189387.36 | -711677.36 | -59.84% | 1.Inverter 1 offline from 06/30. On 07/23 inverter came back online at 09:00 2. Inverter B was derating by 1000kW from 07/01 to 07/10. Inverter B offline from 07/11. On 07/23 inverter came back online at 11:15 and again started derating byn 500kW from 07/23 to 07/31 at peek hours. 3. Inverter 1 is derating by 300 kW during high irradiance starting from 07/26 due to down a module. 4. The ratio of meter to inverter production is 97%, it could be a CT issue affecting the total meter production v/s the inverter production for whole month. | 1. SR103746 , SR103157 2. SR103157 3.SR105299 4. SR104462 | SR103157 | SR103157 | SR105299 | SR104462

## Aug
Altus Power |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 442700 | 1070863.358 | -628163.358 | -58.66% | 1150995.84 | -708295.84 | -61.54%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 442700 | 1070863.358 | -628163.358 | -58.66% | 1150995.84 | -708295.84 | -61.54% | 1.Inverter 2 was offline on 08/01, and Inverter 1 also went offline on 08/04 at 17:00. Both inverters came back online at 10:00 on 08/06. Again inverter 2 stated late for the production at 14:30 on 08/07. Inverter 2 went offline again on 08/22, followed by Inverter 1 on 08/26. Both inverters came back online at 07:45 on 08/28 2.Inverter 1 went offline on 08/11, and Inverter 2 went offline on 08/12. Both inverters came back online at 11:00 on 08/19. Inverter 1 tripped offline again from 12:00 to 13:00 on 08/20 3.The site was offline from 07:45 to 10:45 on 08/28 because a technician was on-site to take transformer DGA samples. 4. The ratio of meter to inverter production is 97%, it could be a CT issue affecting the total meter production v/s the inverter production for whole month. | 1.SR103157 , SR106097 2.SR106001 , SR105299 3.PM8643 4.SR104462 | SR106097 | SR106001 | SR105299 | SR104462

## Sep
Altus Power |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 738440 | 1044444.379 | -306004.379 | -29.3% | 1094822.21 | -356382.21 | -32.55%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS | 738440 | 1044444.379 | -306004.379 | -29.3% | 1094822.21 | -356382.21 | -32.55% | 1. Inverter 1 was offline at 16:00 on 09/14 and back online at 08:30 on 09/15 2. Inverter 2 was taken offline by PE at 12:45 on 09/22 and back online at 10:00 on 09/23 3. Inverter 1 was taken offline by PE at 10:45 to 14:00 on 09/23 4. Inverter 2 is offline from 09/25 till end of the month 5. Inverter 1 was offline from 09/27 till end of the month 6. Inverter 1 and 2 was derated for whole month. | 1.SR106001 2.SR108348 3.SR108442 4.SR106097 5.SR108673 6. SR103157, SR103746 | SR108348 | SR108442 | SR106097 | SR108673 | SR103157 | SR103746

## Oct
Altus Power |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 874760 | 972750.23 | -97990.23 | -10.07% | 972750.23 | -97990.23 | -10.07%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Pratt Solar Farm | KS | 874760 | 972750.23 | -97990.23 | -10.07% | 972750.23 | -97990.23 | -10.07% | 1. Inverter 1 tripped offline at 13:30 on 09/30, reporting "IMI has detected an insulation problem," and was back online at 12:15 on 10/01. and again tripped offline at 11:45 on 10/29 and back online at 13:30 on 10/30. 2. Inverter 2 tripped offline at 13:30 on 09/30, and after a remote reset, it was back online at 16:30 on 10/01. | 1. SR108673, SR110226 2. SR110267 | 1. pending 2. Closed | SR110226 | SR110267

## Nov
Altus Power |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 308800 | 936046.354 | -627246.354 | -67.01% | 956340 | -647540 | -67.71%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Pratt Solar Farm | KS | 308800 | 936046.354 | -627246.354 | -67.01% | 956340 | -647540 | -67.71% | 1. Inverter 1 was offline from 12:00 on 11/01 to 14:00 on 11/04 and again inverter 1 was offline from 11:30 on 11/08 to 08:15 on 11/10 and again the inverter 1 was offline from 06:00 on 11/14 to end of the month. 2. Inverter 2 was offline from 17:00 on 11/05 to 08:15 on 11/24. | 1. SR110226, SR111088 2. SR110717 | 1. Closed, Pending 2. Pending. | SR111088 | SR110717

## Dec
Altus Power |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Pratt Solar Farm | KS |  |  |  |  | 0

## Sites
Portfolio: | Altus Power
Site DAS Name | Site | State | Update | DAS
Kenyon Energy KS Solar | Pratt Solar Farm | KS |  | PowerTrack