## Year to Date
Cushman & Wakefield |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 552043.83 | 0 | 552043.83 | 0% | 0 | 552043.83 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Adelanto - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Apple Valley - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Arvin - Bank of America | CA | 1005.139 | 0 | 1005.139 |  | 0 | 0
Bell - Bank of America | CA | 21830.532 | 0 | 21830.532 |  | 0 | 0
Chula Vista - Bank of America | CA | 13078.738 | 0 | 13078.738 |  | 0 | 0
Cupertino - Bank of America | CA | 16644.072 | 0 | 16644.072 |  | 0 | 0
Diamond Bar - Bank of America | CA | 29084.788 | 0 | 29084.788 |  | 0 | 0
El Centro - Bank of America | CA | 28351.521 | 0 | 28351.521 |  | 0 | 0
Moreno Valley - Bank of America | CA | 45039.661 | 0 | 45039.661 |  | 0 | 0
Redlands - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Roseville - Bank of America | CA | 65427.227 | 0 | 65427.227 |  | 0 | 0
San Bernardino - Bank of America | CA | 788.101 | 0 | 788.101 |  | 0 | 0
San Diego - Bank of America | CA | 965.769 | 0 | 965.769 |  | 0 | 0
Stockton - Bank of America | CA | 16096.231 | 0 | 16096.231 |  | 0 | 0
Victorville - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Aurora - BA - Colfax Ave | CO | 16574.843 | 0 | 16574.843 |  | 0 | 0
Aurora - BA - Parker Rd | CO | 25470.587 | 0 | 25470.587 |  | 0 | 0
Broomfield - Bank of America | CO | 15263.198 | 0 | 15263.198 |  | 0 | 0
Colorado Springs - Bank of America | CO | 26500.398 | 0 | 26500.398 |  | 0 | 0
Denver - BA - 49th Ave | CO | 11954.797 | 0 | 11954.797 |  | 0 | 0
Denver - BA Wadsworth Blvd | CO | 22720.22 | 0 | 22720.22 |  | 0 | 0
Fort Collins - Bank of America | CO | 14992.417 | 0 | 14992.417 |  | 0 | 0
Lafayette - Bank of America | CO | 21475.815 | 0 | 21475.815 |  | 0 | 0
Lakewood - Bank of America | CO | 12079.181 | 0 | 12079.181 |  | 0 | 0
Longmont - Bank of America | CO | 9648.268 | 0 | 9648.268 |  | 0 | 0
Thornton - Bank of America | CO | 12971.629 | 0 | 12971.629 |  | 0 | 0
Calumet City - Bank of America | IL | 22956.521 | 0 | 22956.521 |  | 0 | 0
Downers Grove - Bank of America | IL | 25459.993 | 0 | 25459.993 |  | 0 | 0
Bloomington - Bank of America | MN | 9162.683 | 0 | 9162.683 |  | 0 | 0
Clayton - Bank of America | MO | 21025.511 | 0 | 21025.511 |  | 0 | 0
Manchester - Bank of America | MO | 16772.216 | 0 | 16772.216 |  | 0 | 0
Las Vegas - BA - Eastern Ave | NV | 508.676 | 0 | 508.676 |  | 0 | 0
Las Vegas - BA - Town Ctr Dr | NV | 0 | 0 | 0 |  | 0 | 0
Riverton - Bank of America | UT | 24708.188 | 0 | 24708.188 |  | 0 | 0
Salt Lake City - Bank of America | UT | 3486.91 | 0 | 3486.91 |  | 0 | 0

## 1st Qtr
Cushman & Wakefield |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 109546.9 | 0 | 109546.9 | 0% | 0 | 109546.9 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Adelanto - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Apple Valley - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Arvin - Bank of America | CA | 242.4 | 0 | 242.4 |  | 0 | 0
Bell - Bank of America | CA | 5494 | 0 | 5494 |  | 0 | 0
Chula Vista - Bank of America | CA | 2635.3 | 0 | 2635.3 |  | 0 | 0
Cupertino - Bank of America | CA | 2148.1 | 0 | 2148.1 |  | 0 | 0
Diamond Bar - Bank of America | CA | 6675.8 | 0 | 6675.8 |  | 0 | 0
El Centro - Bank of America | CA | 6302.5 | 0 | 6302.5 |  | 0 | 0
Moreno Valley - Bank of America | CA | 9931.2 | 0 | 9931.2 |  | 0 | 0
Redlands - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Roseville - Bank of America | CA | 13690.4 | 0 | 13690.4 |  | 0 | 0
San Bernardino - Bank of America | CA | 164.1 | 0 | 164.1 |  | 0 | 0
San Diego - Bank of America | CA | 519.6 | 0 | 519.6 |  | 0 | 0
Stockton - Bank of America | CA | 3168.1 | 0 | 3168.1 |  | 0 | 0
Victorville - Bank of America | CA | 0 | 0 | 0 |  | 0 | 0
Aurora - BA - Colfax Ave | CO | 2330.4 | 0 | 2330.4 |  | 0 | 0
Aurora - BA - Parker Rd | CO | 6937.7 | 0 | 6937.7 |  | 0 | 0
Broomfield - Bank of America | CO | 2685.2 | 0 | 2685.2 |  | 0 | 0
Colorado Springs - Bank of America | CO | 5772.9 | 0 | 5772.9 |  | 0 | 0
Denver - BA - 49th Ave | CO | 2811.7 | 0 | 2811.7 |  | 0 | 0
Denver - BA Wadsworth Blvd | CO | 3998.8 | 0 | 3998.8 |  | 0 | 0
Fort Collins - Bank of America | CO | 2483.9 | 0 | 2483.9 |  | 0 | 0
Lafayette - Bank of America | CO | 3988.5 | 0 | 3988.5 |  | 0 | 0
Lakewood - Bank of America | CO | 2180.9 | 0 | 2180.9 |  | 0 | 0
Longmont - Bank of America | CO | 817.1 | 0 | 817.1 |  | 0 | 0
Thornton - Bank of America | CO | 2589.5 | 0 | 2589.5 |  | 0 | 0
Calumet City - Bank of America | IL | 4081.5 | 0 | 4081.5 |  | 0 | 0
Downers Grove - Bank of America | IL | 4372.3 | 0 | 4372.3 |  | 0 | 0
Bloomington - Bank of America | MN | 732.3 | 0 | 732.3 |  | 0 | 0
Clayton - Bank of America | MO | 4230.2 | 0 | 4230.2 |  | 0 | 0
Manchester - Bank of America | MO | 3265.5 | 0 | 3265.5 |  | 0 | 0
Las Vegas - BA - Eastern Ave | NV | 88.2 | 0 | 88.2 |  | 0 | 0
Las Vegas - BA - Town Ctr Dr | NV | 0 | 0 | 0 |  | 0 | 0
Riverton - Bank of America | UT | 4602.2 | 0 | 4602.2 |  | 0 | 0
Salt Lake City - Bank of America | UT | 606.6 | 0 | 606.6 |  | 0 | 0

## 2nd Qtr
Cushman & Wakefield |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 193421.44 | 0 | 193421.44 | 0% | 0 | 193421.44 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Adelanto - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Apple Valley - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Arvin - Bank of America | CA | 320.526 | 0 | 320.526 |  |  | 0
Bell - Bank of America | CA | 6647.688 | 0 | 6647.688 |  |  | 0
Chula Vista - Bank of America | CA | 4183.342 | 0 | 4183.342 |  |  | 0
Cupertino - Bank of America | CA | 7810.127 | 0 | 7810.127 |  |  | 0
Diamond Bar - Bank of America | CA | 9042.05 | 0 | 9042.05 |  |  | 0
El Centro - Bank of America | CA | 9536.975 | 0 | 9536.975 |  |  | 0
Moreno Valley - Bank of America | CA | 15867.794 | 0 | 15867.794 |  |  | 0
Redlands - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Roseville - Bank of America | CA | 23639.884 | 0 | 23639.884 |  |  | 0
San Bernardino - Bank of America | CA | 292.03 | 0 | 292.03 |  |  | 0
San Diego - Bank of America | CA | 193.694 | 0 | 193.694 |  |  | 0
Stockton - Bank of America | CA | 7033.036 | 0 | 7033.036 |  |  | 0
Victorville - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Aurora - BA - Colfax Ave | CO | 4022.693 | 0 | 4022.693 |  |  | 0
Aurora - BA - Parker Rd | CO | 7467 | 0 | 7467 |  |  | 0
Broomfield - Bank of America | CO | 5397.397 | 0 | 5397.397 |  |  | 0
Colorado Springs - Bank of America | CO | 8614.213 | 0 | 8614.213 |  |  | 0
Denver - BA - 49th Ave | CO | 3854.313 | 0 | 3854.313 |  |  | 0
Denver - BA Wadsworth Blvd | CO | 7985.949 | 0 | 7985.949 |  |  | 0
Fort Collins - Bank of America | CO | 5335.039 | 0 | 5335.039 |  |  | 0
Lafayette - Bank of America | CO | 7397.195 | 0 | 7397.195 |  |  | 0
Lakewood - Bank of America | CO | 4315.261 | 0 | 4315.261 |  |  | 0
Longmont - Bank of America | CO | 3815.243 | 0 | 3815.243 |  |  | 0
Thornton - Bank of America | CO | 4433.688 | 0 | 4433.688 |  |  | 0
Calumet City - Bank of America | IL | 7962.201 | 0 | 7962.201 |  |  | 0
Downers Grove - Bank of America | IL | 8850.595 | 0 | 8850.595 |  |  | 0
Bloomington - Bank of America | MN | 6266.156 | 0 | 6266.156 |  |  | 0
Clayton - Bank of America | MO | 6674.488 | 0 | 6674.488 |  |  | 0
Manchester - Bank of America | MO | 5301.011 | 0 | 5301.011 |  |  | 0
Las Vegas - BA - Eastern Ave | NV | 215.647 | 0 | 215.647 |  |  | 0
Las Vegas - BA - Town Ctr Dr | NV | 0 | 0 | 0 |  |  | 0
Riverton - Bank of America | UT | 8706.453 | 0 | 8706.453 |  |  | 0
Salt Lake City - Bank of America | UT | 2239.752 | 0 | 2239.752 |  |  | 0

## 3rd Qtr
Cushman & Wakefield |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 175733.89 | 0 | 175733.89 | 0% | 0 | 175733.89 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Adelanto - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Apple Valley - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Arvin - Bank of America | CA | 297.832 | 0 | 297.832 |  |  | 0
Bell - Bank of America | CA | 6517.664 | 0 | 6517.664 |  |  | 0
Chula Vista - Bank of America | CA | 4171.522 | 0 | 4171.522 |  |  | 0
Cupertino - Bank of America | CA | 3961.265 | 0 | 3961.265 |  |  | 0
Diamond Bar - Bank of America | CA | 8534.218 | 0 | 8534.218 |  |  | 0
El Centro - Bank of America | CA | 8195.093 | 0 | 8195.093 |  |  | 0
Moreno Valley - Bank of America | CA | 13191.314 | 0 | 13191.314 |  |  | 0
Redlands - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Roseville - Bank of America | CA | 20894.943 | 0 | 20894.943 |  |  | 0
San Bernardino - Bank of America | CA | 258.261 | 0 | 258.261 |  |  | 0
San Diego - Bank of America | CA | 192.042 | 0 | 192.042 |  |  | 0
Stockton - Bank of America | CA | 4803.046 | 0 | 4803.046 |  |  | 0
Victorville - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Aurora - BA - Colfax Ave | CO | 8586.684 | 0 | 8586.684 |  |  | 0
Aurora - BA - Parker Rd | CO | 6351.502 | 0 | 6351.502 |  |  | 0
Broomfield - Bank of America | CO | 5338.341 | 0 | 5338.341 |  |  | 0
Colorado Springs - Bank of America | CO | 8108.991 | 0 | 8108.991 |  |  | 0
Denver - BA - 49th Ave | CO | 3818.318 | 0 | 3818.318 |  |  | 0
Denver - BA Wadsworth Blvd | CO | 7473.448 | 0 | 7473.448 |  |  | 0
Fort Collins - Bank of America | CO | 5108.207 | 0 | 5108.207 |  |  | 0
Lafayette - Bank of America | CO | 7085.251 | 0 | 7085.251 |  |  | 0
Lakewood - Bank of America | CO | 4060.442 | 0 | 4060.442 |  |  | 0
Longmont - Bank of America | CO | 3619.177 | 0 | 3619.177 |  |  | 0
Thornton - Bank of America | CO | 4228.186 | 0 | 4228.186 |  |  | 0
Calumet City - Bank of America | IL | 8101.004 | 0 | 8101.004 |  |  | 0
Downers Grove - Bank of America | IL | 8995.058 | 0 | 8995.058 |  |  | 0
Bloomington - Bank of America | MN | 1699.778 | 0 | 1699.778 |  |  | 0
Clayton - Bank of America | MO | 7322.462 | 0 | 7322.462 |  |  | 0
Manchester - Bank of America | MO | 6014.883 | 0 | 6014.883 |  |  | 0
Las Vegas - BA - Eastern Ave | NV | 130.455 | 0 | 130.455 |  |  | 0
Las Vegas - BA - Town Ctr Dr | NV | 0 | 0 | 0 |  |  | 0
Riverton - Bank of America | UT | 8144.08 | 0 | 8144.08 |  |  | 0
Salt Lake City - Bank of America | UT | 530.423 | 0 | 530.423 |  |  | 0

## 4th Qtr
Cushman & Wakefield |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 73341.6 | 0 | 73341.6 | 0% | 0 | 73341.6 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Adelanto - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Apple Valley - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Arvin - Bank of America | CA | 144.381 | 0 | 144.381 |  |  | 0
Bell - Bank of America | CA | 3171.18 | 0 | 3171.18 |  |  | 0
Chula Vista - Bank of America | CA | 2088.574 | 0 | 2088.574 |  |  | 0
Cupertino - Bank of America | CA | 2724.58 | 0 | 2724.58 |  |  | 0
Diamond Bar - Bank of America | CA | 4832.72 | 0 | 4832.72 |  |  | 0
El Centro - Bank of America | CA | 4316.953 | 0 | 4316.953 |  |  | 0
Moreno Valley - Bank of America | CA | 6049.353 | 0 | 6049.353 |  |  | 0
Redlands - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Roseville - Bank of America | CA | 7202 | 0 | 7202 |  |  | 0
San Bernardino - Bank of America | CA | 73.71 | 0 | 73.71 |  |  | 0
San Diego - Bank of America | CA | 60.433 | 0 | 60.433 |  |  | 0
Stockton - Bank of America | CA | 1092.049 | 0 | 1092.049 |  |  | 0
Victorville - Bank of America | CA | 0 | 0 | 0 |  |  | 0
Aurora - BA - Colfax Ave | CO | 1635.066 | 0 | 1635.066 |  |  | 0
Aurora - BA - Parker Rd | CO | 4714.385 | 0 | 4714.385 |  |  | 0
Broomfield - Bank of America | CO | 1842.26 | 0 | 1842.26 |  |  | 0
Colorado Springs - Bank of America | CO | 4004.294 | 0 | 4004.294 |  |  | 0
Denver - BA - 49th Ave | CO | 1470.466 | 0 | 1470.466 |  |  | 0
Denver - BA Wadsworth Blvd | CO | 3262.023 | 0 | 3262.023 |  |  | 0
Fort Collins - Bank of America | CO | 2065.271 | 0 | 2065.271 |  |  | 0
Lafayette - Bank of America | CO | 3004.869 | 0 | 3004.869 |  |  | 0
Lakewood - Bank of America | CO | 1522.578 | 0 | 1522.578 |  |  | 0
Longmont - Bank of America | CO | 1396.748 | 0 | 1396.748 |  |  | 0
Thornton - Bank of America | CO | 1720.255 | 0 | 1720.255 |  |  | 0
Calumet City - Bank of America | IL | 2811.816 | 0 | 2811.816 |  |  | 0
Downers Grove - Bank of America | IL | 3242.04 | 0 | 3242.04 |  |  | 0
Bloomington - Bank of America | MN | 464.449 | 0 | 464.449 |  |  | 0
Clayton - Bank of America | MO | 2798.361 | 0 | 2798.361 |  |  | 0
Manchester - Bank of America | MO | 2190.822 | 0 | 2190.822 |  |  | 0
Las Vegas - BA - Eastern Ave | NV | 74.374 | 0 | 74.374 |  |  | 0
Las Vegas - BA - Town Ctr Dr | NV | 0 | 0 | 0 |  |  | 0
Riverton - Bank of America | UT | 3255.455 | 0 | 3255.455 |  |  | 0
Salt Lake City - Bank of America | UT | 110.135 | 0 | 110.135 |  |  | 0

## Jan
Cushman & Wakefield |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 25654.3 | 0 | 25654.3 | 0% | 0 | 25654.3 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 81.5 | N/A |  |  | N/A |  |  | 1. Site was offline on 01/03/25 at 07:30AM due to a power generation shutdown by command. Enphase later sent a command to reset the site remotely, but it remained offline until the gateway reported back, and the issue was resolved at 13:00 the same day. | 1. SR095278
Bell - Bank of America | CA | 1491.7 | N/A |  |  | N/A
Chula Vista - Bank of America | CA | 458.5 | N/A |  |  | N/A |  |  | 1. Site was offline from 12/30/24 because someone had turned OFF the disconnect. It was remotely turned back ON on 01/15/25 at 15:15, bringing the site back online | 1. SR095189
Cupertino - Bank of America | CA | 0 | N/A |  |  | N/A |  |  | 1. Gateway stopped reporting since 12/19/24. | 1. SR095095
Diamond Bar - Bank of America | CA | 1557.8 | N/A |  |  | N/A |  |  | 1. 12 microinverters have not reported since 9/28/24 due to improper mapping with Enphase. On 01/13/25, the technician found the site map inadequate for locating them. To resolve this, we’ll schedule a follow-up visit with an additional technician and a lift to update the site information in the Enphase Enlighten portal. | 1. SR091352
El Centro - Bank of America | CA | 1875.6 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 3150 | N/A |  |  | N/A |  |  | 1. 10 microinverters have not producing since 01/13/25 and remained offline through the month. | 1. SR095528
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 4319 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 29.9 | N/A |  |  | N/A |  |  | 1. Site has been offline since 01/21/25 due to a possible disconnection.This indicates it was shut off from its past history and back online at 09:00 on 01/31/25. | 1. SR095900
San Diego - Bank of America | CA | 42.2 | N/A |  |  | N/A
Stockton - Bank of America | CA | 935.3 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 484.6 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 1419.2 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 491.3 | N/A |  |  | N/A |  |  | 1. 1 microinverter have not producing since 01/08/25 and remained offline through the month. | 1. SR095596
Colorado Springs - Bank of America | CO | 1148.4 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 966.8 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 358.8 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 219.5 | N/A |  |  | N/A |  |  | 1. Site has been offline since 08/21/24 due to heat anomalies on the breaker affecting the conduit. On 01/15/25, the technician re-energized it and brought it back online at 14:00 | 1. SR095597, SR089922 & SR095037 | SR089922 | SR095037
Lafayette - Bank of America | CO | 514.2 | N/A |  |  | N/A |  |  | 1. Meter was capturing only half of the inverter production due to a faulty CT since 10/31/24. On 01/15/25 at 11:15AM, the technician replaced the RMA'd IQ Gateway, installed 3 new CTs on the supply wires, updated the software, and re-paired all devices. Proper current readings were verified through the Enphase app, and the system back to normal. | 1. SR092849, SR095290 | SR095290
Lakewood - Bank of America | CO | 346.1 | N/A |  |  | N/A
Longmont - Bank of America | CO | 281.1 | N/A |  |  | N/A |  |  | 1. 1 microinverter have not producing since 01/18/25 and remained offline through the month. | 1. SR096191
Thornton - Bank of America | CO | 481 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 1023.4 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 997.5 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 156.4 | N/A |  |  | N/A |  |  | 1. Microinverter 1 (202305093235) has not been reporting since 12/02/24 and was RMA'd on 12/22/24. Parts are needed to bring it back online. | 1. SR094909
Clayton - Bank of America | MO | 804 | N/A |  |  | N/A
Manchester - Bank of America | MO | 686.6 | N/A |  |  | N/A
Las Vegas - BA - Eastern Ave | NV | 56.2 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 1155.6 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 122.1 | N/A |  |  | N/A

## Feb
Cushman & Wakefield |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 31847.3 | 0 | 31847.3 | 0% | 0 | 31847.3 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 73 | N/A |  |  | N/A
Bell - Bank of America | CA | 1743 | N/A |  |  | N/A
Chula Vista - Bank of America | CA | 968 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 293 | N/A |  |  | N/A |  |  | 1. The gateway stopped reporting on 12/19/24. On 02/18/25, the technician found the disconnect open and re-energized the site at 06:30 AM. It stopped reporting again on 02/20/25 and was restored at 06:30 AM on 02/24 after contacting the site. | 1. SR095095, SR097621 | SR097621
Diamond Bar - Bank of America | CA | 2229 | N/A |  |  | N/A |  |  | 1. 12 microinverters have not reported since 9/28/24 due to improper mapping with Enphase. On 01/13/25, the technician found the site map inadequate for locating them. To resolve this, we’ll schedule a follow-up visit with an additional technician and a lift to update the site information in the Enphase Enlighten portal. | 1. SR091352
El Centro - Bank of America | CA | 1684 | N/A |  |  | N/A |  |  | 1. Site was offline from 02/07/25 due to a power off command and brought back online on 02/11/25 after remote reset by enphase | 1. SR096470
Moreno Valley - Bank of America | CA | 3058 | N/A |  |  | N/A |  |  | 1. 10 microinverters have not producing since 01/13/25 and remained offline through the month. | 1. SR095528
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 3965.3 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 43 | N/A |  |  | N/A |  |  | 1. Site was offline from 12:45 on 02/03/25 due to a disconnect, which self-resolved on 02/07 at 08:15. It went offline again from 15:30 on 02/09 and self-resolved on 02/11 at 06:00. The site was offline from 02/14 and came back online on 02/17. On 02/19, the technician updated the gateway firmware as per Enphase instructions. | 1. SR095900
San Diego - Bank of America | CA | 33 | N/A |  |  | N/A
Stockton - Bank of America | CA | 758 | N/A |  |  | N/A |  |  | 1. Site was offline from 02/07/25 due to a power off command and brought back online on 02/10/25 at 14:30 after remote reset by enphase. | 1. SR095166
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 699 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 2054 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 760 | N/A |  |  | N/A |  |  | 1. One microinverter has not been producing since 01/08/25. It was RMA'd on 02/27/25 and remained offline throughout the month. | 1. SR095596
Colorado Springs - Bank of America | CO | 1767 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 653 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 1289 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 794 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 1223 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 611 | N/A |  |  | N/A
Longmont - Bank of America | CO | 536 | N/A |  |  | N/A |  |  | 1. One microinverter has not been producing since 01/18/25 and self-resolved, coming back online on 02/03. | 1. SR096191
Thornton - Bank of America | CO | 774 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 1028 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 1081 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 130 | N/A |  |  | N/A |  |  | 1. Microinverter 1 (202305093235) has not been reporting since 12/02/24 and was RMA'd on 12/22/24. Parts are needed to bring it back online. | 1. SR094909
Clayton - Bank of America | MO | 1206 | N/A |  |  | N/A
Manchester - Bank of America | MO | 894 | N/A |  |  | N/A |  |  | 1. Microinverter 121938054429 has not been reporting from 7:15 on 02/20/25 and remained offline throughout the month. | 1. SR097762
Las Vegas - BA - Eastern Ave | NV | 12 | N/A |  |  | N/A |  |  | 1. Site stopped reporting from 02/08/25. Likely AC Disconnect is off. | 1. SR096627
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 1326 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 163 | N/A |  |  | N/A

## Mar
Cushman & Wakefield |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 52045.3 | 0 | 52045.3 | 0% | 0 | 52045.3 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 87.9 | N/A |  |  | N/A
Bell - Bank of America | CA | 2259.3 | N/A |  |  | N/A
Chula Vista - Bank of America | CA | 1208.8 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 1855.1 | N/A |  |  | N/A
Diamond Bar - Bank of America | CA | 2889 | N/A |  |  | N/A |  |  | 1. 12 microinverters haven't reported since 09/28/24 due to incorrect mapping with Enphase. On 01/13/25, the tech found the site map inadequate. On 03/20/25, the technician lifted all modules on Array 2, optimizers photographed, and manual mapping started. Enphase portal mapping doesn't match on-site. Need to return to finish mapping Arrays 1 & 2, then submit to Enphase for correction. | 1. SR091352
El Centro - Bank of America | CA | 2742.9 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 3723.2 | N/A |  |  | N/A |  |  | 1. 10 microinverters have not producing since 01/13/25.On 03/25/25, technician tested Array 1 J-Box connections – all passed, NEC compliant. Replaced all wire nuts and Wagos with new ones. Found 18 microinverters offline and unmapped. Started mapping all 84 units and confirmed with Enphase; all serials added and mapped. Restored 83 units. One unit (S/N: 202403005673, Array 1, Row 4, Col 5) still offline – MCI head damaged. AC/DC tests passed. Opened RMA with Enphase. Installed spare (S/N: 202401030429) from van, updated mapping. Enphase confirmed new unit is producing the same day. | 1. SR095528
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 5406.1 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 91.2 | N/A |  |  | N/A
San Diego - Bank of America | CA | 444.4 | N/A |  |  | N/A
Stockton - Bank of America | CA | 1474.8 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 1146.8 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 3464.5 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1433.9 | N/A |  |  | N/A |  |  | 1. One microinverter (202305093235) has not been producing since 01/08/25. It was RMA'd on 02/27/25 and remained offline throughout the month. | 1. SR095596
Colorado Springs - Bank of America | CO | 2857.5 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 1191.9 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 2351 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1470.4 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 2251.3 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 1223.8 | N/A |  |  | N/A
Longmont - Bank of America | CO |  | N/A |  |  | N/A
Thornton - Bank of America | CO | 1334.5 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 2030.1 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 2293.8 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 445.9 | N/A |  |  | N/A
Clayton - Bank of America | MO | 2220.2 | N/A |  |  | N/A
Manchester - Bank of America | MO | 1684.9 | N/A |  |  | N/A |  |  | 1. Microinverter 121938054429 has not been reporting from 7:15 on 02/20/25 and remained offline throughout the month. | 1. SR097762, PM9175
Las Vegas - BA - Eastern Ave | NV | 20 | N/A |  |  | N/A |  |  | 1.The site stopped reporting from 02/08/25, likely due to the AC disconnect being off. Site is communicating and producing normally from 03/22 | 1.SR096627
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 2120.6 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 321.5 | N/A |  |  | N/A

## Apr
Cushman & Wakefield |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 64215.7 | 0 | 64215.7 | 0% | 0 | 64215.7 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 89.6 | N/A |  |  | N/A
Bell - Bank of America | CA | 2536.2 | N/A |  |  | N/A
Chula Vista - Bank of America | CA | 1426.9 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 2190.9 | N/A |  |  | N/A
Diamond Bar - Bank of America | CA | 2886.7 | N/A |  |  | N/A |  |  | 1. 12 microinverters have not reported since 09/28/24 due to incorrect mapping in the Enphase system. On 01/13/25, a technician identified the site map as inadequate. On 03/20/25, all modules on Array 2 were lifted, optimizers photographed, and manual mapping was started. However, the Enphase portal mapping still doesn't match the physical layout. The technician needs to return to complete mapping for Arrays 1 and 2 and submit the corrected map to Enphase. On 04/17/25, Array 3 was mapped, and on 04/18/25, mapping continued on the west-facing array, with modules removed to retrieve microinverter serial numbers. Despite these efforts, the microinverters are still not reporting. | 1. SR091352
El Centro - Bank of America | CA | 3171.8 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 4841 | N/A |  |  | N/A
Redlands - Bank of America | CA |  | N/A |  |  | N/A
Roseville - Bank of America | CA | 6982.8 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 111.9 | N/A |  |  | N/A
San Diego - Bank of America | CA | 62.5 | N/A |  |  | N/A
Stockton - Bank of America | CA | 1974.5 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A |  |  | 1. Three SMAs have been offline since 04/15. On 04/23, the technician found major thermal damage around the capacitors, which need to be replaced in order to bring the inverters back online. | 1. SR099807
Aurora - BA - Colfax Ave | CO | 1222.2 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 3514.4 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1547.5 | N/A |  |  | N/A |  |  | 1. One microinverter (202305093235) has not been producing since 01/08/25. It was RMA'd on 02/27/25 and remained offline throughout the month. | 1.SR095596
Colorado Springs - Bank of America | CO | 2757.6 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 1212.4 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 2345.5 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1644.4 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 2243 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 1280.4 | N/A |  |  | N/A
Longmont - Bank of America | CO | 1194.3 | N/A |  |  | N/A
Thornton - Bank of America | CO | 1347.7 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 2184.3 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 2439.1 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 5105.3 | N/A |  |  | N/A |  |  | 1. One microinverter (202305093235) is not reporting the production data.Issue to be addressed on PM | 1.SR101279
Clayton - Bank of America | MO | 1970.4 | N/A |  |  | N/A
Manchester - Bank of America | MO | 1474 | N/A |  |  | N/A |  |  | 1. Microinverter 121938054429 has not been reporting from 7:15 on 02/20/25 and remained offline throughout the month. | 1. SR097762, PM9175
Las Vegas - BA - Eastern Ave | NV | 70.8 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 2575.5 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 1812.1 | N/A |  |  | N/A

## May
Cushman & Wakefield |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 66518.4 | 0 | 66518.4 | 0% | 0 | 66518.4 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 112.1 | N/A |  |  | N/A
Bell - Bank of America | CA | 2216.4 | N/A |  |  | N/A |  |  | 1. 8 microinverters have been offline since 5/10 due to an AC frequency out-of-range issue. Enphase approved a remote RMA on 5/19, pending confirmation and shipping details from ROC and the OEM. 2. Gateway not reporting since 05/22 at 16:16 and later self resolved on 05/29. | 1. SR101589, SR101905 2. SR101905 | SR101905 | SR101905
Chula Vista - Bank of America | CA | 1383.4 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 2776.4 | N/A |  |  | N/A
Diamond Bar - Bank of America | CA | 2908.8 | N/A |  |  | N/A |  |  | 1. 12 microinverters(gray) have not reported since 09/28/24; 9 of them were previously RMA’d. On 05/29/25, Enphase confirmed 13 microinverters(white) are missing from the array builder. A device scan was run waiting 24 hours before replacing old SNs with new ones via the self-service install replacement option. Awaiting Enphase's response on data. | 1. SR102087, SR091352 | SR091352
El Centro - Bank of America | CA | 3257.5 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 5356 | N/A |  |  | N/A |  |  | 1. one microinverter have not reporting since 05/28 and remained offline throughout the month. | 1. SR102088
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 8405.8 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 108.5 | N/A |  |  | N/A |  |  | 1. Microinverters did not report from 19:10 on 05/20 to 06:35 on 05/23 due to a mapping issue, which requires further troubleshooting. | 1. SR101846
San Diego - Bank of America | CA | 64.3 | N/A |  |  | N/A
Stockton - Bank of America | CA | 2540.7 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A |  |  | 1. Three SMAs have been offline since 04/15. On 04/23, a technician found major thermal damage around the capacitors, requiring replacement. On 05/14, SMA requested as-builts to review and recommend an alternate inverter model for repowering, as the same series is no longer available | 1. SR099807
Aurora - BA - Colfax Ave | CO | 1401.3 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 3952.6 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1947.5 | N/A |  |  | N/A |  |  | 1. One microinverter (202305093235) has not produced since 01/08. It was RMA’d on 02/27, and on 05/02, the technician replaced three microinverters, which came back online at 10:15 the same day | 1. SR095596
Colorado Springs - Bank of America | CO | 2966.3 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 1348.2 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 2916.1 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1819.1 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 2615.1 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 1549.6 | N/A |  |  | N/A
Longmont - Bank of America | CO | 1309.4 | N/A |  |  | N/A
Thornton - Bank of America | CO | 1552.1 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 2801.4 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 3092.4 | N/A |  |  | N/A |  |  | 1. One microinverter have not reporting since 05/10 and remained offline throughout the month. Issue to be addressed on PM | 1. SR101326
Bloomington - Bank of America | MN | 624.6 | N/A |  |  | N/A |  |  | 1. One microinverter (202305093235) is not reporting the production data.Issue to be addressed on PM | 1. SR101279
Clayton - Bank of America | MO | 2398.7 | N/A |  |  | N/A
Manchester - Bank of America | MO | 1926.2 | N/A |  |  | N/A |  |  | 1. Microinverter 121938054429 has not been reporting from 7:15 on 02/20/25 and remained offline throughout the month. | 1. SR097762, PM9175
Las Vegas - BA - Eastern Ave | NV | 72.1 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 2895.9 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 199.9 | N/A |  |  | N/A

## Jun
Cushman & Wakefield |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 62687.34 | 0 | 62687.34 | 0% | 0 | 62687.34 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 118.826 | N/A |  |  | N/A
Bell - Bank of America | CA | 1895.088 | N/A |  |  | N/A |  |  | 1. 8 microinverters have been offline since 05/10/2025 due to "AC Frequency Out of Range" and are currently undergoing the RMA process. | 1. SR101589
Chula Vista - Bank of America | CA | 1373.042 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 2842.827 | N/A |  |  | N/A
Diamond Bar - Bank of America | CA | 3246.55 | N/A |  |  | N/A |  |  | 1. 12 microinverters are not reporting (gray) and have possibly been offline since 04/18/2025. Out of these, 9 have already been RMA'd. Additionally, it was confirmed that 13 microinverters are missing (white) from the Array Builder. A device scan was initiated, and a 24-hour wait period is being observed before replacing the old serial numbers with new ones using the Self-Service "Install Replacement" option. Awaiting Enphase’s response regarding the data | 1. SR102087
El Centro - Bank of America | CA | 3107.675 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 5670.794 | N/A |  |  | N/A |  |  | 1. One microinverter has not been reporting since 05/28/2025 and is currently undergoing the RMA process. | 1. SR102088
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 8251.284 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 71.63 | N/A |  |  | N/A |  |  | 1. The site experienced communication losses on 06/01, 06/02, 06/03, 06/05, 06/06, 06/07, 06/11, 06/21, 06/22, 06/23, 06/24, 06/25, 06/26, and 06/28, and production during these periods cannot be confirmed. Additionally, site production dropped to 13 W from 08:30 to 14:15 on 06/19. The site resumed production later at 15:30 on 06/20 and again at 17:45 on 06/29. | 1. SR101846
San Diego - Bank of America | CA | 66.894 | N/A |  |  | N/A
Stockton - Bank of America | CA | 2517.836 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 1399.193 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 0 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1902.397 | N/A |  |  | N/A
Colorado Springs - Bank of America | CO | 2890.313 | N/A |  |  | N/A |  |  | 1. Microinverter 202305093250 lost communications on 6/4. Possibly offline. | 1. SR102639
Denver - BA - 49th Ave | CO | 1293.713 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 2724.349 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1871.539 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 2539.095 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 1485.261 | N/A |  |  | N/A
Longmont - Bank of America | CO | 1311.543 | N/A |  |  | N/A
Thornton - Bank of America | CO | 1533.888 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 2976.501 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 3319.095 | N/A |  |  | N/A |  |  | 1. One microinverter has not been reporting since 06/15 | 1. SR103077
Bloomington - Bank of America | MN | 536.256 | N/A |  |  | N/A
Clayton - Bank of America | MO | 2305.388 | N/A |  |  | N/A |  |  | 1. Microinverters 202305094113 and 202305090271 have been offline since 06/27 and are currently undergoing the RMA process. | 1. SR103670
Manchester - Bank of America | MO | 1900.811 | N/A |  |  | N/A
Las Vegas - BA - Eastern Ave | NV | 72.747 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 3235.053 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 227.752 | N/A |  |  | N/A

## Jul
Cushman & Wakefield |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 64324.219 | 0 | 64324.219 | 0% | 0 | 64324.219 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 114.86 | N/A |  |  | N/A
Bell - Bank of America | CA | 2361.962 | N/A |  |  | N/A |  |  | 1. 8 microinverters have been offline since 05/10/2025 due to "AC Frequency Out of Range" and are currently undergoing the RMA process. | 1. SR101589
Chula Vista - Bank of America | CA | 1516.12 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 273.302 | N/A |  |  | N/A |  |  | 1. Site gateway was not reported from 7/4/25 to end of the month. | 1. SR104091
Diamond Bar - Bank of America | CA | 3434.747 | N/A |  |  | N/A |  |  | 1. 12 microinverters are not reporting (gray) and have possibly been offline since 04/18/2025. Out of these, 9 have already been RMA'd. Additionally, it was confirmed that 13 microinverters are missing (white) from the Array Builder. A device scan was initiated, and a 24-hour wait period is being observed before replacing the old serial numbers with new ones using the Self-Service "Install Replacement" option. Awaiting Enphase’s response regarding the data | 1.SR102087
El Centro - Bank of America | CA | 2989.504 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 5467.241 | N/A |  |  | N/A |  |  | 1. One microinverter has not been reporting since 05/28/2025 and is currently undergoing the RMA process. | 1. SR102088
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 8164.759 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 119.12 | N/A |  |  | N/A |  |  | 1. The site experienced communication losses on 07/01, 07/08, 07/30, 07/31, and production during these periods cannot be confirmed. | 1. SR101846
San Diego - Bank of America | CA | 75.951 | N/A |  |  | N/A
Stockton - Bank of America | CA | 2381.664 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A |  |  | 1. 3 micro inverters to have major thermal damage around the capacitors were offline for whole month. | 1. SR099807
Aurora - BA - Colfax Ave | CO | 3996.95 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 1418.852 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1965.641 | N/A |  |  | N/A
Colorado Springs - Bank of America | CO | 2807.292 | N/A |  |  | N/A |  |  | 1. Microinverter 202305093250 lost communications on 6/4. Possibly offline. | 1.SR102639
Denver - BA - 49th Ave | CO | 1369.429 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 2691.256 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1926.773 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 2559.323 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 1487.777 | N/A |  |  | N/A
Longmont - Bank of America | CO | 1341.835 | N/A |  |  | N/A
Thornton - Bank of America | CO | 1538.391 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 2750.356 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 3012.697 | N/A |  |  | N/A |  |  | 1. One microinverter has not been reporting since 06/15. Micro inveretr back online on 07/18 | 1. SR103077
Bloomington - Bank of America | MN | 681.338 | N/A |  |  | N/A
Clayton - Bank of America | MO | 2435.06 | N/A |  |  | N/A |  |  | 1. Microinverters 202305094113 and 202305090271 have been offline since 06/27 and are currently undergoing the RMA process. On 07/24 technicain Replaced 3 micro inverters and 45/45 producing. | 1. SR103670
Manchester - Bank of America | MO | 2119.026 | N/A |  |  | N/A
Las Vegas - BA - Eastern Ave | NV | 41.517 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A |  |  | 1. Site stopped communicating on 7/18/25. AC disconnect may be off. Requesting the customer to check breaker | 1.SR104706
Riverton - Bank of America | UT | 3067.304 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 214.172 | N/A |  |  | N/A

## Aug
Cushman & Wakefield |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 60444.872 | 0 | 60444.872 | 0% | 0 | 60444.872 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 96.076 | N/A |  |  | N/A
Bell - Bank of America | CA | 2321.921 | N/A |  |  | N/A |  |  | 1. 8 microinverters were offline and being RMA'd. | 1. SR101589
Chula Vista - Bank of America | CA | 1411.387 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 1756.997 | N/A |  |  | N/A |  |  | 1. Site gateway was not communicated from 07/04 to 06:45 on 08/09. | 1. SR104091
Diamond Bar - Bank of America | CA | 3100.488 | N/A |  |  | N/A |  |  | 1.12 microinverter were offline for whole month. | 1. SR102087
El Centro - Bank of America | CA | 2645.955 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 4216.399 | N/A |  |  | N/A |  |  | 1. 1 micro inverter was offline for whole month. | 1. SR102088
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 7155.892 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 74.348 | N/A |  |  | N/A |  |  | 1. 2 microinverters were offline for whole month and being RMA'd. | 1. SR106651
San Diego - Bank of America | CA | 67.215 | N/A |  |  | N/A
Stockton - Bank of America | CA | 1551.023 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 1304.688 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 3807.865 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1807.407 | N/A |  |  | N/A
Colorado Springs - Bank of America | CO | 2773.904 | N/A |  |  | N/A |  |  | 1. 1 micro inverter was offline from 06/07 to 14:00 on 08/22. | 1. SR102639
Denver - BA - 49th Ave | CO | 1310.952 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 2527.152 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1692.749 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 2434.638 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 1384.051 | N/A |  |  | N/A
Longmont - Bank of America | CO | 1230.202 | N/A |  |  | N/A
Thornton - Bank of America | CO | 1438.414 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 2875.538 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 3155.116 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 550.04 | N/A |  |  | N/A
Clayton - Bank of America | MO | 2633.719 | N/A |  |  | N/A
Manchester - Bank of America | MO | 2144.528 | N/A |  |  | N/A
Las Vegas - BA - Eastern Ave | NV | 34.208 | N/A |  |  | N/A |  |  | 1. Site was offline from 07/18 to 15:45 on 08/15. | 1. SR104706
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 2757.284 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 184.716 | N/A |  |  | N/A

## Sep
Cushman & Wakefield |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 50964.799 | 0 | 50964.799 | 0% | 0 | 50964.799 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA | - | N/A |  |  | N/A
Apple Valley - Bank of America | CA | - | N/A |  |  | N/A
Arvin - Bank of America | CA | 86.896 | N/A |  |  | N/A
Bell - Bank of America | CA | 1833.781 | N/A |  |  | N/A |  |  | 1. 8 microinverters are offline from 5/10/25 and "reporting AC Frequency Out of Range" and back online on 09/30. | 1. SR101589
Chula Vista - Bank of America | CA | 1244.015 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 1930.966 | N/A |  |  | N/A
Diamond Bar - Bank of America | CA | 1998.983 | N/A |  |  | N/A |  |  | 1. 12 microinverter were offline and are being RMA'd. They remained offline for the entire month. | 1. SR102087
El Centro - Bank of America | CA | 2559.634 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 3507.674 | N/A |  |  | N/A |  |  | 1. 1 micro inverter was offline for whole month. | 1. SR102088
Redlands - Bank of America | CA | - | N/A |  |  | N/A
Roseville - Bank of America | CA | 5574.292 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 64.793 | N/A |  |  | N/A |  |  | 1. 2 microinverters were offline for whole month and being RMA'd. | 1. SR106651
San Diego - Bank of America | CA | 48.876 | N/A |  |  | N/A
Stockton - Bank of America | CA | 870.359 | N/A |  |  | N/A
Victorville - Bank of America | CA | - | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 3285.046 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 1124.785 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1565.293 | N/A |  |  | N/A
Colorado Springs - Bank of America | CO | 2527.795 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 1137.937 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 2255.04 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1488.685 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 2091.29 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 1188.614 | N/A |  |  | N/A
Longmont - Bank of America | CO | 1047.14 | N/A |  |  | N/A
Thornton - Bank of America | CO | 1251.381 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 2475.11 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 2827.245 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 468.4 | N/A |  |  | N/A
Clayton - Bank of America | MO | 2253.683 | N/A |  |  | N/A
Manchester - Bank of America | MO | 1751.329 | N/A |  |  | N/A
Las Vegas - BA - Eastern Ave | NV | 54.73 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | - | N/A |  |  | N/A
Riverton - Bank of America | UT | 2319.492 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 131.535 | N/A |  |  | N/A

## Oct
Cushman & Wakefield |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 44810.318 | 0 | 44810.318 | 0% | 0 | 44810.318 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 91.257 | N/A |  |  | N/A
Bell - Bank of America | CA | 1855.64 | N/A |  |  | N/A |  |  | 1. 8 microinverters are offline from 5/10/25 and "reporting AC Frequency Out of Range" and back online on 09/30. | 1. SR101589 | 1. pending
Chula Vista - Bank of America | CA | 1208.685 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 1668.414 | N/A |  |  | N/A
Diamond Bar - Bank of America | CA | 3048.358 | N/A |  |  | N/A |  |  | 1. 12 microinverter were offline and are being RMA'd. They remained offline for the entire month. | 1. SR102087 | 1. pending
El Centro - Bank of America | CA | 2492.575 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 3621.378 | N/A |  |  | N/A |  |  | 1. 1 micro inverter was offline on 05/28.25 and after replaceing a new microinverter is back online at 10/24. | 1. SR102088 | 1. completed
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 4735.476 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 31.06 | N/A |  |  | N/A |  |  | 1. 2 microinverters were offline was back online at 10/02. | 1. SR106651 | 1. Closed
San Diego - Bank of America | CA | 37.344 | N/A |  |  | N/A
Stockton - Bank of America | CA | 719.111 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 974.222 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 2832.681 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 1126.175 | N/A |  |  | N/A
Colorado Springs - Bank of America | CO | 2374.889 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 943.6 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 1929.5 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 1234.067 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 1803.503 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 957.311 | N/A |  |  | N/A
Longmont - Bank of America | CO | 870.776 | N/A |  |  | N/A
Thornton - Bank of America | CO | 1073.579 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 1801.3 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 2055.1 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 297.86 | N/A |  |  | N/A
Clayton - Bank of America | MO | 1652.718 | N/A |  |  | N/A
Manchester - Bank of America | MO | 1287.16 | N/A |  |  | N/A
Las Vegas - BA - Eastern Ave | NV | 45.2 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 1974.664 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 66.715 | N/A |  |  | N/A

## Nov
Cushman & Wakefield |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 28531.282 | 0 | 28531.282 | 0% | 0 | 28531.282 | 0%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Adelanto - Bank of America | CA | 0 | N/A |  |  | N/A
Apple Valley - Bank of America | CA | 0 | N/A |  |  | N/A
Arvin - Bank of America | CA | 53.124 | N/A |  |  | N/A
Bell - Bank of America | CA | 1315.54 | N/A |  |  | N/A |  |  | 1. 8 microinverters are offline from 9/3/25. tech found that 8 microinverters were offline, and String BR 3 was offline due to an AC issue. Wires are needed for repairs. | 1.SR109951 | 1.Pending
Chula Vista - Bank of America | CA | 879.889 | N/A |  |  | N/A
Cupertino - Bank of America | CA | 1056.166 | N/A |  |  | N/A
Diamond Bar - Bank of America | CA | 1784.362 | N/A |  |  | N/A |  |  | 1. 12 microinverter were offline and are being RMA'd. They remained offline for the entire month. | 1.SR102087 | 1.Pending
El Centro - Bank of America | CA | 1824.378 | N/A |  |  | N/A
Moreno Valley - Bank of America | CA | 2427.975 | N/A |  |  | N/A
Redlands - Bank of America | CA | 0 | N/A |  |  | N/A
Roseville - Bank of America | CA | 2466.524 | N/A |  |  | N/A
San Bernardino - Bank of America | CA | 42.65 | N/A |  |  | N/A
San Diego - Bank of America | CA | 23.089 | N/A |  |  | N/A
Stockton - Bank of America | CA | 372.938 | N/A |  |  | N/A
Victorville - Bank of America | CA | 0 | N/A |  |  | N/A
Aurora - BA - Colfax Ave | CO | 660.844 | N/A |  |  | N/A
Aurora - BA - Parker Rd | CO | 1881.704 | N/A |  |  | N/A
Broomfield - Bank of America | CO | 716.085 | N/A |  |  | N/A
Colorado Springs - Bank of America | CO | 1629.405 | N/A |  |  | N/A
Denver - BA - 49th Ave | CO | 526.866 | N/A |  |  | N/A
Denver - BA Wadsworth Blvd | CO | 1332.523 | N/A |  |  | N/A
Fort Collins - Bank of America | CO | 831.204 | N/A |  |  | N/A
Lafayette - Bank of America | CO | 1201.366 | N/A |  |  | N/A
Lakewood - Bank of America | CO | 565.267 | N/A |  |  | N/A
Longmont - Bank of America | CO | 525.972 | N/A |  |  | N/A
Thornton - Bank of America | CO | 646.676 | N/A |  |  | N/A
Calumet City - Bank of America | IL | 1010.516 | N/A |  |  | N/A
Downers Grove - Bank of America | IL | 1186.94 | N/A |  |  | N/A
Bloomington - Bank of America | MN | 166.589 | N/A |  |  | N/A
Clayton - Bank of America | MO | 1145.643 | N/A |  |  | N/A
Manchester - Bank of America | MO | 903.662 | N/A |  |  | N/A
Las Vegas - BA - Eastern Ave | NV | 29.174 | N/A |  |  | N/A
Las Vegas - BA - Town Ctr Dr | NV | 0 | N/A |  |  | N/A
Riverton - Bank of America | UT | 1280.791 | N/A |  |  | N/A
Salt Lake City - Bank of America | UT | 43.42 | N/A |  |  | N/A

## Dec
Cushman & Wakefield |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Adelanto - Bank of America | CA |  | 0 |  |  | 0
Apple Valley - Bank of America | CA |  | 0
Arvin - Bank of America | CA
Bell - Bank of America | CA
Chula Vista - Bank of America | CA
Cupertino - Bank of America | CA
Diamond Bar - Bank of America | CA
El Centro - Bank of America | CA
Moreno Valley - Bank of America | CA
Redlands - Bank of America | CA
Roseville - Bank of America | CA
San Bernardino - Bank of America | CA
San Diego - Bank of America | CA
Stockton - Bank of America | CA
Victorville - Bank of America | CA
Aurora - BA - Colfax Ave | CO
Aurora - BA - Parker Rd | CO
Broomfield - Bank of America | CO
Colorado Springs - Bank of America | CO
Denver - BA - 49th Ave | CO
Denver - BA Wadsworth Blvd | CO
Fort Collins - Bank of America | CO
Lafayette - Bank of America | CO
Lakewood - Bank of America | CO
Longmont - Bank of America | CO
Thornton - Bank of America | CO
Calumet City - Bank of America | IL
Downers Grove - Bank of America | IL
Bloomington - Bank of America | MN
Clayton - Bank of America | MO
Manchester - Bank of America | MO
Las Vegas - BA - Eastern Ave | NV
Las Vegas - BA - Town Ctr Dr | NV
Riverton - Bank of America | UT
Salt Lake City - Bank of America | UT

## Sites
Portfolio: | Cushman & Wakefield
Site DAS Name | Site | State | Update | DAS
| Adelanto - Bank of America | CA |  | Enlighten Manager
| Apple Valley - Bank of America | CA |  | Enlighten Manager
Bank of America - CAW-D36 (Arvin, CA) | Arvin - Bank of America | CA |  | Enlighten Manager
Bank of America - CA8-122 (Bell, CA) (240 VAC High Leg Delta) | Bell - Bank of America | CA |  | Enlighten Manager
Bank of America - CAW-G59 (Chula Vista, CA) | Chula Vista - Bank of America | CA |  | Enlighten Manager
Bank of America - CAW-F39 (Cupertino, CA) | Cupertino - Bank of America | CA |  | Enlighten Manager
Bank of America - CA7-202 (Diamond Bar, CA) | Diamond Bar - Bank of America | CA |  | Enlighten Manager
Bank of America - CA0-119 (El Centro, CA) | El Centro - Bank of America | CA |  | Enlighten Manager
Bank of America - CA6-174 (Moreno Valley, CA) | Moreno Valley - Bank of America | CA |  | Enlighten Manager
| Redlands - Bank of America | CA |  | Enlighten Manager
Bank of America - CA2-113 (Roseville, CA) | Roseville - Bank of America | CA |  | Enlighten Manager
Bank of America - CAW-E84 (San Bernardino, CA) | San Bernardino - Bank of America | CA |  | Enlighten Manager
Bank of America (San Diego, CA) | San Diego - Bank of America | CA |  | Enlighten Manager
Bank of America - CA2-154 (Stockton, CA) | Stockton - Bank of America | CA |  | Enlighten Manager
| Victorville - Bank of America | CA |  | Enlighten Manager
BOA, Arapahoe Crossings #CO1-112 | Aurora - BA - Colfax Ave | CO |  | Enlighten Manager
BOA, Chambers Plaza #COW-139 | Aurora - BA - Parker Rd | CO |  | Enlighten Manager
BOA, BroomFeild #COW-107 | Broomfield - Bank of America | CO |  | Enlighten Manager
BOA, Garden of the Gods #CO1-140 | Colorado Springs - Bank of America | CO |  | Enlighten Manager
BOA, Green Valley Ranch #CO1-121 | Denver - BA - 49th Ave | CO |  | Enlighten Manager
BOA, South Wadsworth #COW-113 | Denver - BA Wadsworth Blvd | CO |  | Enlighten Manager
BOA, Front Range Village #COW-143 | Fort Collins - Bank of America | CO |  | Enlighten Manager
Bank of America - COW-135 (Lafayette, CO) | Lafayette - Bank of America | CO |  | Enlighten Manager
BOA, Lakewood #COW-115 | Lakewood - Bank of America | CO |  | Enlighten Manager
BOA,Village at the Peaks #CO1-109 | Longmont - Bank of America | CO |  | Enlighten Manager
BOA, Thornton #COW-118 | Thornton - Bank of America | CO |  | Enlighten Manager
Bank of America - IL4-020 (River Oaks, IL) | Calumet City - Bank of America | IL |  | Enlighten Manager
BOA, WoodRidge IL2-251 | Downers Grove - Bank of America | IL |  | Enlighten Manager
| Bloomington - Bank of America | MN |  | Enlighten Manager
Bank of America - Forsyth (Clayton, MO) | Clayton - Bank of America | MO |  | Enlighten Manager
Bank of America - MO1-064 (Manchester, MO) | Manchester - Bank of America | MO |  | Enlighten Manager
Bank Of America (Las Vegas, NV) | Las Vegas - BA - Eastern Ave | NV |  | Enlighten Manager
| Las Vegas - BA - Town Ctr Dr | NV |  | Enlighten Manager
Bank of America - UTW-024 (Riverton, UT) | Riverton - Bank of America | UT |  | Enlighten Manager
Bank of America - UT3-111 (Salt Lake City, UT) | Salt Lake City - Bank of America | UT |  | Enlighten Manager