## Year to Date
Northbridge Companies |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 352761.825 | 180892.75 | 171869.075 | 95.01% | 262811.178 | 89950.647 | 34.23%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 90696.7 | 0 | 90696.7 |  | 0 | 0 | 0%
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 262065.125 | 180892.75 | 81172.375 | 44.87% | 262811.178 | -746.053 | -0.2839%

## 1st Qtr
Northbridge Companies |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 118219.085 | 79193.593 | 39025.492 | 49.28% | 51994.465 | 66224.62 | 127.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 62466.96 | 0 | 62466.96 |  | 0 | 0 | 0%
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 55752.125 | 79193.593 | -23441.468 | -29.6% | 51994.465 | 3757.66 | 7.227%

## 2nd Qtr
Northbridge Companies |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 106640.815 | 34396.06 | 72244.755 | 210% | 89142.738 | 17498.077 | 19.63%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 18456.44 | 0 | 18456.44 |  | 0 | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 88184.375 | 34396.06 | 53788.315 | 156.4% | 89142.738 | -958.363 | -1.075%

## 3rd Qtr
Northbridge Companies |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 92112.5 | 44172.071 | 47940.429 | 108.5% | 84996.659 | 7115.841 | 8.372%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 92112.5 | 44172.071 | 47940.429 | 108.5% | 84996.659 | 7115.841 | 8.372%

## 4th Qtr
Northbridge Companies |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 35789.425 | 23131.026 | 12658.399 | 54.72% | 36677.316 | -887.891 | -2.421%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 9773.3 | 0 | 9773.3 |  | 0 | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 26016.125 | 23131.026 | 2885.099 | 12.47% | 36677.316 | -10661.191 | -29.07%

## Jan
Northbridge Companies |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 32240.375 | 23990.493 | 8249.882 | 34.39% | 13578.087 | 18662.288 | 137.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 17790 | N/A |  |  | N/A
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 14450.375 | 23990.493 | -9540.118 | -39.77% | 13578.087 | 872.288 | 6.424% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Feb
Northbridge Companies |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 35400.51 | 31450.165 | 3950.345 | 12.56% | 16170.202 | 19230.308 | 118.9%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 19120.26 | N/A |  |  | N/A
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 16280.25 | 31450.165 | -15169.915 | -48.23% | 16170.202 | 110.048 | 0.6806% | 1. Inverter 2.3 has tripped offline at 09:00AM on 02/12 reporting Insulation Resistance Low and back online at 06:30AM on 02/14 and On 02/28 started late for production at 01:15PM. 2.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR096732 2.SR094280 | SR094280

## Mar
Northbridge Companies |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 50578.2 | 23752.935 | 26825.265 | 112.9% | 22246.176 | 28332.024 | 127.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 25556.7 | N/A |  |  | N/A
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 25021.5 | 23752.935 | 1268.565 | 5.341% | 22246.176 | 2775.324 | 12.48% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Apr
Northbridge Companies |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 46001.065 | 13297.438 | 32703.627 | 245.9% | 26440.769 | 19560.296 | 73.98%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 18456.44 | N/A |  |  | N/A |  |  | 1.Site tripped offline at 12:15 on 04/23,meter voltages were abnormal,techician checked in and found that site is running and producing without communication due to faulty step down transformer. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 27544.625 | 13297.438 | 14247.187 | 107.1% | 26440.769 | 1103.856 | 4.175% | 1.Inverter 2.3 didn't start for production reporting "Insulation resistance low" and was back online at 12:44 on 04/22. 2.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR098622 2.SR094280 | SR094280

## May
Northbridge Companies |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 29245.125 | 13831.293 | 15413.832 | 111.4% | 30978.309 | -1733.184 | -5.595%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 29245.125 | 13831.293 | 15413.832 | 111.4% | 30978.309 | -1733.184 | -5.595% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1. SR094280

## Jun
Northbridge Companies |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 31394.625 | 7267.329 | 24127.296 | 332% | 31723.66 | -329.035 | -1.037%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 31394.625 | 7267.329 | 24127.296 | 332% | 31723.66 | -329.035 | -1.037% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Jul
Northbridge Companies |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 32655.625 | 12807.285 | 19848.34 | 155% | 30863.213 | 1792.412 | 5.808%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 32655.625 | 12807.285 | 19848.34 | 155% | 30863.213 | 1792.412 | 5.808% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Aug
Northbridge Companies |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 34330.125 | 14682.458 | 19647.667 | 133.8% | 29110 | 5220.125 | 17.93%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1.SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 34330.125 | 14682.458 | 19647.667 | 133.8% | 29110 | 5220.125 | 17.93% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1.SR094280

## Sep
Northbridge Companies |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 25126.75 | 16682.328 | 8444.422 | 50.62% | 25023.446 | 103.304 | 0.4128%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month due to a damaged transformer affecting communications. | 1. SR100216
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 25126.75 | 16682.328 | 8444.422 | 50.62% | 25023.446 | 103.304 | 0.4128% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. | 1. SR094280

## Oct
Northbridge Companies |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 12226.125 | 7030.354 | 5195.771 | 73.9% | 21374.539 | -9148.414 | -42.8%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1.Site was not communicated for whole month. Transformer that connects to DAS needs to be replaced. Remains without communication. | 1.SR106124 | 1.Closed
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 12226.125 | 7030.354 | 5195.771 | 73.9% | 21374.539 | -9148.414 | -42.8% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. 2.Site stopped communicating at 13:30 on 10/08 and later back online at 09:00 on 10/22 | 1.SR094280 2.SR109266 | 1.Pending 2.Closed | SR109266

## Nov
Northbridge Companies |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 23563.3 | 16100.672 | 7462.628 | 46.35% | 15302.777 | 8260.523 | 53.98%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
MA: North Dartmouth - 293 Cross St (Array 1) | MA | 9773.3 | N/A |  |  | N/A |  |  | 1.Meter started communicating to DAS from 11/13 at 10:30. Created Ticket #142793 with power factors as data points require recalculation. | 1.PM9586 , SR111018 | 1.Completed, Pending
MA: North Dartmouth - 293 Cross St (Array 2) | MA | 13790 | 16100.672 | -2310.672 | -14.35% | 15302.777 | -1512.777 | -9.886% | 1.The POA irradiance sensor has intermittent communication issues and has been showing bad data since 11/03/2024. 2.Inverter 2.3 having heavy shading starting from mid day | 1.SR094280 | 1.Pending

## Dec
Northbridge Companies |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
MA: North Dartmouth - 293 Cross St (Array 1) | MA |  | 0
MA: North Dartmouth - 293 Cross St (Array 2) | MA

## Sites
Portfolio: | Northbridge Companies
Site DAS Name | Site | State | Update | DAS
MA - Northbridge Array 1 | MA: North Dartmouth - 293 Cross St (Array 1) | MA |  | Inaccess
Northbridge Array 2 | MA: North Dartmouth - 293 Cross St (Array 2) | MA |  | PowerTrack