## Year to Date
Renewable Properties |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 55199472.2617 | 62463977.293 | -7264505.0313 | -11.63% | 65328683.113 | -10129210.8513 | -15.5%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 1197432 | 983886.081 | 213545.919 | 21.7% | 1073333.537 | -57906.537 | -5.395%
Bullis | NY | 6419011.5 | 6462375.7 | -43364.2 | -0.671% | 7849400.7 | -1430389.2 | -18.22%
Rock Island | NY | 5849288.5 | 6680100 | -830811.5 | -12.44% | 9303962.47 | -3454673.97 | -37.13%
Winslow - Roderick | ME | 5892108 | 6668464.095 | -776356.095 | -11.64% | 6376310.58 | -484202.58 | -7.594%
Minoa - Clemons Rd | NY | 4035720.1255 | 4839962.025 | -804241.8995 | -16.62% | 4511643.125 | -475922.9995 | -10.55%
Manchester - Western | ME | 969385.813 | 650526.09 | 318859.723 | 49.02% | 793457.731 | 175928.082 | 22.17%
Batavia - Pike Rd | NY | 4643142.375 | 4903450.048 | -260307.673 | -5.309% | 5248056.05 | -604913.675 | -11.53%
Slayton A & B | NY | 11040701 | 12997334.52 | -1956633.52 | -15.05% | 11757282.04 | -716581.04 | -6.095%
Batavia - Alexander Rd | NY | 2612006.9482 | 3168206.977 | -556200.0288 | -17.56% | 2891925.51 | -279918.5618 | -9.679%
NC: Gibson – Henry Gibson Solar | NC | 7885534 | 9398128.2 | -1512594.2 | -16.09% | 9363769.2 | -1478235.2 | -15.79%
Bangor - Pushaw | ME | 4655142 | 5711543.557 | -1056401.557 | -18.5% | 6159542.17 | -1504400.17 | -24.42%

## 1st Qtr
Renewable Properties |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 10039467.4133 | 12321099.887 | -2281632.4737 | -18.52% | 12129549.23 | -2090081.8167 | -17.23%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 437777 | 267935.23 | 169841.77 | 63.39% | 205644.36 | 50127.64 | 24.38%
Bullis | NY | 1022641.5 | 1180915.6 | -158274.1 | -13.4% | 1367428.4 | -344786.9 | -25.21%
Rock Island | NY | 1051915 | 1305164.6 | -253249.6 | -19.4% | 1250649.1 | -198734.1 | -15.89%
Winslow - Roderick | ME | 1295575 | 1649057.2 | -353482.2 | -21.44% | 1587877 | -292302 | -18.41%
Minoa - Clemons Rd | NY | 629215.625 | 845731.6 | -216515.975 | -25.6% | 914112.3 | -284896.675 | -31.17%
Manchester - Western | ME | 174947.8125 | 0 | 174947.8125 |  | 0 | 174947.8125
Batavia - Pike Rd | NY | 768410.8751 | 975809.7 | -207398.8249 | -21.25% | 999612 | -231201.125 | -23.13%
Slayton A & B | NY | 1787409 | 2241667.2 | -454258.2 | -20.26% | 2066288.6 | -278879.6 | -13.5%
Batavia - Alexander Rd | NY | 412623.6007 | 584711.9 | -172088.2993 | -29.43% | 539206.5 | -126582.8993 | -23.48%
NC: Gibson – Henry Gibson Solar | NC | 1601858 | 1870367.4 | -268509.4 | -14.36% | 1679126 | -77268 | -4.602%
Bangor - Pushaw | ME | 857094 | 1399739.457 | -542645.457 | -38.77% | 1519604.97 | -662510.97 | -43.6%

## 2nd Qtr
Renewable Properties |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 17335160.2865 | 18317293.67 | -982133.3835 | -5.362% | 21126873.4 | -3791713.1135 | -17.95%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 230670 | 218073.51 | 12596.49 | 5.776% | 292400.5 | -61730.5 | -21.11%
Bullis | NY | 2200368 | 2131826.4 | 68541.6 | 3.215% | 2867711.1 | -667343.1 | -23.27%
Rock Island | NY | 2082820.5 | 2174807.4 | -91986.9 | -4.23% | 2382636.1 | -299815.6 | -12.58%
Winslow - Roderick | ME | 1342729 | 1374298.16 | -31569.16 | -2.297% | 1573938 | -231209 | -14.69%
Minoa - Clemons Rd | NY | 1308172.75 | 1504589.8 | -196417.05 | -13.05% | 1760486.8 | -452314.05 | -25.69%
Manchester - Western | ME | 306860.1875 | 119325.8 | 187534.3875 | 157.2% | 332824.7 | -25964.5125 | -7.801%
Batavia - Pike Rd | NY | 1601331 | 1637420.8 | -36089.8 | -2.204% | 1898336.7 | -297005.7 | -15.65%
Slayton A & B | NY | 4066592 | 4333834 | -267242 | -6.166% | 4407054 | -340462 | -7.725%
Batavia - Alexander Rd | NY | 905518.849 | 1020100.9 | -114582.051 | -11.23% | 1039419.3 | -133900.451 | -12.88%
NC: Gibson – Henry Gibson Solar | NC | 2078191 | 2539787.8 | -461596.8 | -18.17% | 2632997.2 | -554806.2 | -21.07%
Bangor - Pushaw | ME | 1211907 | 1263229.1 | -51322.1 | -4.063% | 1939069 | -727162 | -37.5%

## 3rd Qtr
Renewable Properties |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 20663234.6685 | 23704263.366 | -3041028.6975 | -12.83% | 24809935.783 | -4146701.1145 | -16.71%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 377110 | 348432.381 | 28677.619 | 8.23% | 442643.887 | -65533.887 | -14.81%
Bullis | NY | 2507081 | 2447788.2 | 59292.8 | 2.422% | 2870410.9 | -363329.9 | -12.66%
Rock Island | NY | 2041963 | 2449960.4 | -407997.4 | -16.65% | 4991919.17 | -2949956.17 | -59.09%
Winslow - Roderick | ME | 2388720 | 2620290.435 | -231570.435 | -8.838% | 2353795.58 | 34924.42 | 1.484%
Minoa - Clemons Rd | NY | 1658917.7505 | 1940181.125 | -281263.3745 | -14.5% | 1385535.125 | 273382.6255 | 19.73%
Manchester - Western | ME | 358185.813 | 380858.28 | -22672.467 | -5.953% | 338067.221 | 20118.592 | 5.951%
Batavia - Pike Rd | NY | 1720325.355 | 1734045.448 | -13720.093 | -0.7912% | 1828409.05 | -108083.695 | -5.911%
Slayton A & B | NY | 3890108 | 4991361.32 | -1101253.32 | -22.06% | 4190656.44 | -300548.44 | -7.172%
Batavia - Alexander Rd | NY | 1002641.75 | 1183189.277 | -180547.527 | -15.26% | 1035998.21 | -33356.46 | -3.22%
NC: Gibson – Henry Gibson Solar | NC | 2820248 | 3352789 | -532541 | -15.88% | 3426970 | -606722 | -17.7%
Bangor - Pushaw | ME | 1897934 | 2255367.5 | -357433.5 | -15.85% | 1945530.2 | -47596.2 | -2.446%

## 4th Qtr
Renewable Properties |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 7161609.8934 | 8121320.37 | -959710.4766 | -11.82% | 7262324.7 | -100714.8065 | -1.387%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Cedar Swamp Rd | MA | 151875 | 149444.96 | 2430.04 | 1.626% | 132644.79 | 19230.21 | 14.5%
Bullis | NY | 688921 | 701845.5 | -12924.5 | -1.842% | 743850.3 | -54929.3 | -7.384%
Rock Island | NY | 672590 | 750167.6 | -77577.6 | -10.34% | 678758.1 | -6168.1 | -0.9087%
Winslow - Roderick | ME | 865084 | 1024818.3 | -159734.3 | -15.59% | 860700 | 4384 | 0.5094%
Minoa - Clemons Rd | NY | 439414 | 549459.5 | -110045.5 | -20.03% | 451508.9 | -12094.9 | -2.679%
Manchester - Western | ME | 129392 | 150342.01 | -20950.01 | -13.93% | 122565.81 | 6826.19 | 5.569%
Batavia - Pike Rd | NY | 553075.145 | 556174.1 | -3098.955 | -0.5572% | 521698.3 | 31376.845 | 6.014%
Slayton A & B | NY | 1296592 | 1430472 | -133880 | -9.359% | 1093283 | 203309 | 18.6%
Batavia - Alexander Rd | NY | 291222.7485 | 380204.9 | -88982.1515 | -23.4% | 277301.5 | 13921.2484 | 5.02%
NC: Gibson – Henry Gibson Solar | NC | 1385237 | 1635184 | -249947 | -15.29% | 1624676 | -239439 | -14.74%
Bangor - Pushaw | ME | 688207 | 793207.5 | -105000.5 | -13.24% | 755338 | -67131 | -8.888%

## Jan
Renewable Properties |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 1767768.4685 | 2623230.695 | -855462.2265 | -32.61% | 2261375.48 | -493607.0115 | -21.83% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 61046 | 72282.67 | -11236.67 | -15.55% | 41663.38 | 19382.62 | 46.52%
Bullis | NY | 179917 | 269796.6 | -89879.6 | -33.31% | 264056.9 | -84139.9 | -31.86% | 1.Site tripped offline at 19:46 on 01/25 due to recloser trip and again back online on 10:45am on 01/26 | 1.SR095981
Rock Island | NY | 230466.5 | 342985.3 | -112518.8 | -32.81% | 246331.8 | -15865.3 | -6.441% | 1.Low generation due to weather/snow.
Winslow - Roderick | ME | 361423 | 473366.7 | -111943.7 | -23.65% | 385109 | -23686 | -6.15%
Minoa - Clemons Rd | NY | 128703.75 | 206281.4 | -77577.65 | -37.61% | 191393.5 | -62689.75 | -32.75% | 1.Site tripped offline at 04:45 on 01/05 due to SEL tripped offline later technician was able to re-energize the site on 12:45pm on 01/06 2. Tracker TCU 39 is not configured after being replaced on 12/16 and requires further troubleshooting with Suntrack. | 1.SR095317 2.SR095762
Manchester - Western | ME | 47584.8125 | 0 | 47584.8125 |  | 0 | 47584.8125
Batavia - Pike Rd | NY | 159955.8238 | 246837.6 | -86881.7762 | -35.2% | 219320.6 | -59364.7762 | -27.07% | 1.Site was taken offline for replacing the transformer fuses by United power on 01/22 from 14:54 to 15:41. 2.Tracker 11 has been stuck and reporting "Motor overcurrent detected" on 01/09 technician was able to blocking & alarm and trackers are back online at 10:30 on 01/28 | 1.SR094826 2.SR095434
Slayton A & B | NY | 353338 | 494949.8 | -141611.8 | -28.61% | 398835.4 | -45497.4 | -11.41% | 1.Low generation due to weather/snow.
Batavia - Alexander Rd | NY | 75534.5822 | 136027.1 | -60492.5178 | -44.47% | 110310.9 | -34776.3178 | -31.53% | 1.Inverter 10 has tripped at 11:45am on 01/10 while United renewables was onsite later technician has brought inverter back online on 01/14 at 11:15 2.Site was taken offline from 08:15am to 15:00 on 01/23 by Asplundh Electrical for transformer testing. 3.All trackers are no tracking due to Overcurrent and snow alarm on 01/24. | 1.SR095486 2.SR095884 3.SR095924
NC: Gibson – Henry Gibson Solar | NC
Bangor - Pushaw | ME | 169799 | 380703.525 | -210904.525 | -55.4% | 404354 | -234555 | -58.01% | 1. Low production due to snow/rain.

## Feb
Renewable Properties |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 2742058.028 | 4023644.66 | -1281586.632 | -31.85% | 3948929.33 | -1206871.302 | -30.56%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 75305 | 82808.46 | -7503.46 | -9.061% | 55035.28 | 20269.72 | 36.83% | 1. Low generation due to weather/snow.
Bullis | NY | 257310 | 328876.1 | -71566.1 | -21.76% | 421521.9 | -164211.9 | -38.96% | 1.Site tripped offline at 15:45 on 02/08/25 due to recloser trip and later auto reclosed back online at 19:00 the same day. | 1. SR096532
Rock Island | NY | 290891.5 | 392222 | -101330.5 | -25.83% | 387802 | -96910.5 | -24.99% | 1.Site tripped offline at 07:45AM on 02/19/25 due to recloser trip and was back online at 9:30AM on 02/21 after technician re-enerzied. | 1. SR097445
Winslow - Roderick | ME | 361591 | 581795.4 | -220204.4 | -37.85% | 500603 | -139012 | -27.77% | 1. Low generation due to weather/snow.
Minoa - Clemons Rd | NY | 147261.25 | 204792.3 | -57531.05 | -28.09% | 282687.4 | -135426.15 | -47.91% | 1. Site was taken offline from 09:00 AM on 02/03/25 to 09:45 AM on 02/04/25 by United Renewable Energy to paint the transformer on-site. Site again tripped offline at 14:30 on the same day and came back online at 12:30 on 02/08/25, after the technician swapped the blown transformer fuses for a new type. 2. Tracker TCU 39 was reconfigured and set back to Auto by the technician, and it was operating as expected on 02/27/25. However the tracker was stuck again on 02/28/25. | 1. SR094897 2. SR095762 | SR095762
Manchester - Western | ME | 43938.8125 | 0 | 43938.8125 |  | 0 | 43938.8125
Batavia - Pike Rd | NY | 192004.5513 | 293733.3 | -101728.7487 | -34.63% | 307523.4 | -115518.8487 | -37.56% | 1. Tracker 11 has been stuck and reporting "Motor overcurrent detected" on 02/06/25 technician was able to blocking & alarm and trackers are back online at 18:15 on 02/10/25. 2. Tracker 11 has been stuck and reporting "Motor overcurrent detected" on 02/11/25 technician was able to blocking & alarm and trackers are back online at 13:00 on 02/12/25. | 1. SR096403 2. SR096696 | SR096696
Slayton A & B | NY | 451738 | 695245.4 | -243507.4 | -35.02% | 637509.2 | -185771.2 | -29.14% | 1. Site was taken offline from 08:15 AM to 09:15 AM on 02/05/25 by United Renewable Energy to swap out parts of the transformer, and they left the GOAB open at Site A for further work. On 02/06/25, they re-energized the site and brought it back online at 11:30 AM. Additionally, they reset the AC combiner to restore voltage, bringing Inverters A 13-16 back online at 14:30 the same day. 2. Six trackers were stuck on 02/06/25. On 02/07/25, the technician secured the loose connection and found alarms for motor overcurrent. All trackers were inspected and cleared, and they returned to normal operation the same day. 3. Seven trackers were stuck on 02/10/25. On 02/11/25, the technician cleared the fault, and the trackers were operating normally the same day. 4. Multiple trackers were stuck on 02/19/25. On 02/24/25, the technician tightened the fuse holders and cleared the alarms, but further troubleshooting with Suntrack is required. On 02/26/25, the technician cleared all remaining fault alarms except for tracker 132, which requires additional troubleshooting. | 1. SR096326 2. SR096398 3. SR096626 4. SR096935 | SR096398 | SR096626 | SR096935
Batavia - Alexander Rd | NY | 106100.9142 | 176053.3 | -69952.3858 | -39.73% | 167939.4 | -61838.4858 | -36.82% | 1. Low generation due to weather/snow.
NC: Gibson – Henry Gibson Solar | NC | 689224 | 766019.4 | -76795.4 | -10.03% | 707894 | -18670 | -2.637% | 1. Inverter 1.21 has been offline throughout the month. To bring it back online, the EPC needs to replace the inverter. 2.Inverter 2.11 tripped offline at 13:45 on 02/22/25 due to a grid phase voltage out of range and remained offline throughout the month. | 1. SR097527 2. SR097650 | SR097650
Bangor - Pushaw | ME | 201998 | 502099 | -300101 | -59.77% | 480413.75 | -278415.75 | -57.95% | 1. Low production due to snow/rain.

## Mar
Renewable Properties |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 5272330.9168 | 5674224.532 | -401893.6152 | -7.083% | 5919244.42 | -646913.5032 | -10.93%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 119421 | 112844.1 | 6576.9 | 5.828% | 108945.7 | 10475.3 | 9.615% | 1. Site was taken offline from 09:05am to 11:10am on 03/14 as to replace the voltage sensing cable. | 1.SR096338
Bullis | NY | 585414.5 | 582242.9 | 3171.6 | 0.5447% | 681849.6 | -96435.1 | -14.14% | 1. The site tripped offline at 23:00 EDT on 03/16. On 03/17. The technician performed a reset and closed the recloser. The site was back online from 08:45 AM on 03/17 | 1.SR098647
Rock Island | NY | 530557 | 569957.3 | -39400.3 | -6.913% | 616515.3 | -85958.3 | -13.94% | 1. The site tripped offline at 10:15 EDT on 03/03. On 03/05, a technician found the SEL and both pad breakers open, closed them, and restored production. The site has been online and producing normally since 13:15 EDT on 03/05 | 1.SR097988
Winslow - Roderick | ME | 572561 | 593895.1 | -21334.1 | -3.592% | 702165 | -129604 | -18.46% | 1. Site production was low on 03/05, 03/16, 03/17, 03/24 and 03/30 due to bad weather.
Minoa - Clemons Rd | NY | 353250.625 | 434657.9 | -81407.275 | -18.73% | 440031.4 | -86780.775 | -19.72% | 1. Site tripped offline at 14:25 EDT on 03/05. On 03/06, a technician closed the recloser at 10:15 EDT. Tracker TSU 8 (address 39) was misaligned, deviating. After renergization,the technician adjusted it to match TSU 7, cleared the blocking, and restored proper tracking. 2. USNE technician took the site offline from 11:55am to 15:05 on 03/18 for transformer testing. 3. On 03/20, a technician visited the site to troubleshoot inverter 15's frequent trip events (since 03/17) and trackers 39, 28, and 35. Inverter 15 and two fuses are being RMA'd, with further tracker troubleshooting needed. 4. The Site is experiencing the following tracker issues: NCU-01: Tracker 39 is stuck at -56°. Tracker 28 deviates during morning hours and experiences intermittent failure. NCU-02: Tracker 35 deviates during morning hours and experiences intermittent failure. | 1.SR098176 2.SR098356 3.SR098701 4.SR098775 | SR098356 | SR098701 | SR098775
Manchester - Western | ME | 83424.1875 | 0 | 83424.1875 |  | 0 | 83424.1875
Batavia - Pike Rd | NY | 416450.5 | 435238.8 | -18788.3 | -4.317% | 472768 | -56317.5 | -11.91% | 1. NCU-01 (120): Tracker Position TCU 11 stuck at -54 degrees from 10:15 EDT on 03/27 | 1.SR098907
Slayton A & B | NY | 982333 | 1051472 | -69139 | -6.575% | 1029944 | -47611 | -4.623% | 1. NCU-A.01-tracker 132 was stuck on 02/19/25. On 03/10, a technician power-cycled all NCUs, restoring communication except for tracker 132, which had wind damage. Further troubleshooting was needed. On 03/28, a technician cleared faults and aligned all trackers except tracker 132. Inverter A.22 has one string (11) disconnected until tracker repairs are complete 2. Site was de-energized by the USNE technician at 08:45 AM on 03/13 to work on the transformers.Site was Re-energized at 12:00 EDT on 03/13 3. Inverter A.34 is derating 50% during morning hours becuase of the trackers stuck | 1.SR096935,SR098375,SR098777 2.SR097819 | SR098375 | SR098777 | SR097819
Batavia - Alexander Rd | NY | 230988.1043 | 272631.5 | -41643.3957 | -15.27% | 260956.2 | -29968.0957 | -11.48% | 1.NSU 02 - Tracker 49 motor is stuck at -16.9 degrees on 02/08/25 from 08:45AM from then it started reporting in different values which is impacting Inverter 05 production after mid-day. | 1.SR098763
NC: Gibson – Henry Gibson Solar | NC | 912634 | 1104348 | -191714 | -17.36% | 971232 | -58598 | -6.033% | 1. Inverter 1.21 was offline from 03/01. On 03/18, a USNE technician replaced it but noted further troubleshooting was needed. The site remained offline until the punch list was completed on 03/19, when it was re-energized at 18:15 EDT. Inverters 1.04, 2.10, and 2.11 are offline due to removed faulty AC combiner fuses. Inverter 1.22 is producing power but not communicating, likely due to a daisy chain issue with the unprogrammed inverter 1.21. 2. Inverter 2.11 was offline from 03/01. On 03/04, a technician found the fault "Out of phase-Occur" and identified a blown fuse. Technician mentioned a fuse replacement is needed, and the inverter will remain offline.On 03/27, a technician replaced the blown fuse and re-powdered AC combiner and inverter2.11 .Inverter 2.11 is back online and producing as expected from 10:25 EDT. 3. Inverter 2.09 tripped offline at 14:30 on 03/24. On 03/27, a technician replaced the blown Phase B fuse and re-powered the inverter. It was back online at 12:00 EDT. 4. Inverters 1.04 and 2.10 went offline after USNE technician's checkout on 03/19 due to faulty AC combiner fuses. On 03/27, a technician found Inverter 2.10 had a damaged insulated fuse stud preventing fuse installation, while Inverter 1.04 was unresponsive and mentioned Both the inverters will remain offline until repaired. 5. Inverter 2.05 tripped offline at 14:15 after a USNE technician check out and remained offline for rest of the month. | 1.SR097527 2.SR097650,SR098979 3.SR098946, SR098979 4.SR098979,SR099163 5.SR099057 | SR097650 | SR098979 | SR098946 | SR098979 | SR098979 | SR099163 | SR099057
Bangor - Pushaw | ME | 485297 | 516936.932 | -31639.932 | -6.121% | 634837.22 | -149540.22 | -23.56% | 1. Site production was low on 03/05 to 03/07, 03/16 to 03/17, 03/20 to 03/21, 03/24 to 03/25 and 03/30 to 03/31.

## Apr
Renewable Properties |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 6111269.163 | 6474775.4 | -363506.237 | -5.614% | 6741811.7 | -630542.537 | -9.353%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 132729 | 124295.4 | 8433.6 | 6.785% | 137919.5 | -5190.5 | -3.763% | 1.Inverter 2 started late for production at 13:30 on 04/23 and found inverter DC voltages are high. Inverter 2 tripped offline at 12:30pm on 04/26. Inverter 2 has started for production on 04/27 ,voltages are normalized ,issue got self resolved. | 1.SR100208
Bullis | NY | 716355 | 704002.3 | 12352.7 | 1.755% | 820770.1 | -104415.1 | -12.72% | 1.Since 03/18/25, Inverter 8 has been derating by ~25–30 kW during high irradiance due to increase in internal temperatures, possibly from a fan fault. On 04/19, a technician found string 6 on CB 8 reading low voltage (1135V vs. 1165V), suggesting a possible bad panel. CB 8 location differs from plans; further troubleshooting is needed. 2.Site tripped offline at 11:33 AM on 04/19 and was back online at 16:30 after the technician closed the relay. | 1.SR099753 2.SR100017 | SR100017
Rock Island | NY | 577733 | 639667.7 | -61934.7 | -9.682% | 633812.4 | -56079.4 | -8.848% | 1. Site tripped offline at 14:18 on 04/03 and was back online at 10:15 after the technician closed the relay on 04/05 2.Inverter 17 was offline on 04/26 and then started for production next day issue self resolved. | 1.SR099376 2.SR100451 | SR100451
Winslow - Roderick | ME | 658339 | 684937.9 | -26598.9 | -3.883% | 697456 | -39117 | -5.609%
Minoa - Clemons Rd | NY | 392341 | 467637.9 | -75296.9 | -16.1% | 499299.5 | -106958.5 | -21.42% | 1.Inverter 15 is being RMAD from 04/10 due to its multiple trip events.On 04/30 ,technician troubleshoot the inverter came back online at 14:45 on 04/30 2.The site was offline from 17:15 on 04/29 to 06:45 EDT on 04/30 due to transformer testing conducted by USNE. 3.The site tripped offline at 12:30 EDT on 04/30 and back online at 13:30 the same day. The issue got self-resolved. 4.Multiple trackers were observed stuck on various days with no consistent pattern. | 1.SR098701 2.SR100667 3.SR100717 4.SR098775 | SR100667 | SR100717 | SR098775
Manchester - Western | ME | 96372.375 | 0 | 96372.375 |  | 104717.2 | -8344.825 | -7.969% | 1.Inverter 2 tripped offline at 11:15 AM on 04/01 and was back online at 14:48 the same day. The issue self-resolved 2. Inverter 2 tripped offline from 11:30 to 12:30 EDT. Inverter 3 tripped offline from 12:30 to 14:00 and again from 14:45 to 17:30 on 04/23.Issue got resolved after tech visit and they are operating on 04/24. | 1.SR099279 2.SR100248,SR100392 | SR100248 | SR100392
Batavia - Pike Rd | NY | 496293.064 | 499624.7 | -3331.636 | -0.6668% | 530455.1 | -34162.036 | -6.44% | 1.NCU-01 (120): Tracker Position TCU 11 stuck at -54 degrees from 03/21.Issue existed for rest of the month | 1.SR098907
Slayton A & B | NY | 1190178 | 1248265 | -58087 | -4.653% | 1237720 | -47542 | -3.841% | 1.NCU-A.01-tracker 132 was stuck on 02/19/25 .On 04/21 ,technician received the materials from FlexRack and further accessed the wind damage to the row and then also replaced the GHI sensor wiring for site A. From then POA sensor is communicating.Additional troubleshooting is required 2.All Pad A inverters and the meter tripped offline at 13:30 on 04/10 and back online at 17:30 the same day after technician closed relay on Pad A. 3.Site was offline from 12:30 to 13:45 on 04/28 due to RESA technician check into the site for repairing the breaker on a transformer 4.All trackers are stuck from 10:45AM on 04/29 All trackers has resumed tracking on 04/30 except - NCU A.01 - Tracker S132 still struck , NCU A.02 - Trackers S71 & S72 still struck , NCU B.01 - Tracker S2 still struck. | 1.SR098375 2.SR099651 3.SR100352 4.SR100666 | SR099651 | SR100352 | SR100666
Batavia - Alexander Rd | NY | 272601.724 | 301844.3 | -29242.576 | -9.688% | 292096.9 | -19495.176 | -6.674% | 1.Tracker 76 motor has been observed stuck at 30.76° across multiple days, with no consistent time pattern,NSU 02 - Tracker 49 motor is stuck at -16.9 degrees on 02/08/25 from 08:45AM,NSU 02 - Tracker 27 motor is struck at -1.01 DEG .Inverter 05 is impacting production after mid-day. | 1.SR098763
NC: Gibson – Henry Gibson Solar | NC | 1024404 | 1232185 | -207781 | -16.86% | 1177694 | -153290 | -13.02% | 1.Inverter 1.04 &2.10 are offline throughout the month.Inverter 2.10 has damaged insulated fuse stud which is preventing fuse from being installed. Inverter 1.04 is unresponsive and pending RMA for the wire box 2.The site remained offline from 15:45 on 04/07 to 07:45 on 04/10 due to weather-related outages in the area. Power was restored on 04/08, after a technician closed the recloser. 3.Trackers stuck at 0 degrees and set points are also reporting 0 degrees from 04/23 All trackers started tracking from 04/25 10:00AM. Issue got self resolved | 1.SR098979 2.SR099483 3.SR100204 | SR099483 | SR100204
Bangor - Pushaw | ME | 553923 | 572315.2 | -18392.2 | -3.214% | 609871 | -55948 | -9.174% | 1.The site tripped offline at 12:15 on 04/15 and was back online at 13:30 after the recloser auto-reclosed. | 1.SR099819

## May
Renewable Properties |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 5909424.9421 | 6255273.81 | -345848.8679 | -5.529% | 8160249.2 | -2250824.2579 | -27.58%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 97941 | 93778.11 | 4162.89 | 4.439% | 154481 | -56540 | -36.6% | 1. Site was tripped offline from 05/20 at 11:00 and offline for End of the month due to utility was working on substation. | 1. SR101723
Bullis | NY | 676501 | 657346 | 19155 | 2.914% | 1003046 | -326545 | -32.56% | 1. Inverter 8 was derating by 40kW down for whole month compared to its peers due to the fan being RMA'd. 2. Site was offline from 09:45 to 13:00 on 05/16 due to utility outage. 3. The site went offline on 05/25 at 14:30. On 05/27, a technician inspected the MV lines and switchgear and found that the recloser and the main breaker had tripped. He reclosed the site, and it was back online at 09:00 on 05/27. 4.The site tripped offline on 05/28 at 16:40. It was later remotely reset, and Pad 2 came back online at 21:00; however, Pad 1 remained offline. A technician later re-energized the site at 08:15 on 05/29. The site tripped offline again on 05/29 at 13:45 and was re-energized by a technician at 15:45 the same day. 5. The site tripped offline at 17:56 on 05/30 and came back online at 18:20 on the same day. Pad 2 was restored, but Pad 1 remained offline. | 1. SR099753 2. SR101577 3. SR101927 4. SR102059 5. SR102206 | SR101577 | SR101927 | SR102059 | SR102206
Rock Island | NY | 636980 | 635371.2 | 1608.8 | 0.2532% | 879182.1 | -242202.1 | -27.55% | 1. Inverter 17 had late starting issue. | 1.SR100451
Winslow - Roderick | ME | 626213 | 636729 | -10516 | -1.652% | 797959 | -171746 | -21.52% | Based on actual weather station data, the site is performing close to expected levels, with no major events or anomalies observed during the reporting period
Minoa - Clemons Rd | NY | 379990.25 | 419545.1 | -39554.85 | -9.428% | 620710.4 | -240720.15 | -38.78% | 1. Site tripped offline on 05/04 at 18:15 due to storm activity. On 05/05 technician reclosed the recloser site came back online at 13:45 2. NCU 01 tracker 39, NCU 02 trackers 44 & 47 (tracker and setpoint 0 DEG) were stuck technician was on site on 05/15 to troubleshoot the trackers NCU 1 TCU 39 was set to auto and resumed tracking. The NCU 2 TCU 44 & 47 have blown fuses and will remain stuck until replacements can be installed. On 05/18 NCU 01 tracker 39 got stuck again. | 1. SR100717 2. SR098775 | SR098775
Manchester - Western | ME | 94785.4375 | N/A |  |  | 114913.1 | -20127.6625 | -17.52% | While expected energy data is not available, weather station data indicates normal irradiance levels, and no major issues were observed on site. Based on available information, system performance appears consistent with typical operating conditions.
Batavia - Pike Rd | NY | 456032.9097 | 509437.7 | -53404.7903 | -10.48% | 673777.4 | -217744.4903 | -32.32% | 1. Site tripped offline on 05/11 at 13:30 due to utility had a line outage for emergency work. On 05/12 at 10:00 technician re-energized the site. 2. Site tripped offline on 05/02 at 16:00 due to fiuse blown on transformer and later technician re-energised the site on 05/06 at 09:00 but inverters 1, 2, 3, 4 and 5 remained offline and back online on 05/12 at 10:00 after technician reclose the breaker. | 1. SR101280 2. SR101153, SR100944 | SR101153 | SR100944
Slayton A & B | NY | 1382406 | 1432195 | -49789 | -3.476% | 1549451 | -167045 | -10.78% | 1. NCU A.01 - Tracker S132 struck, NCU A.02 - Trackers S71 & S72 struck, NCU B.01 - Tracker S2 struck for whole month. | 1. SR100666
Batavia - Alexander Rd | NY | 280555.3448 | 318829 | -38273.6552 | -12% | 361911.2 | -81355.8552 | -22.48% | 1. Site tripped offline at 13:30 on 05/11 due to Utility line outage for emergency work. On 05/12 at 09:00 the technician re-energised the site. | 1. SR101281
NC: Gibson – Henry Gibson Solar | NC | 926206 | 1171619 | -245413 | -20.95% | 1329520 | -403314 | -30.34% | 1. United Renewable Energy checked in to work on punch list items and combiner boxes. They de-energized the site at 08:00 on 05/09 and re-energized it later at 18:30 the same day. 2. The site tripped offline 11:45 on 05/19 due to blown fuse on phase B and lighting arrester was disconnected and later on 05/22 client hired MV Crew to close in the site. the site was back online at 08:00 on 05/22. 3. Inverter 1.04 went offline on 05/22. A technician later replaced the AC fuse, and the inverter was back online on 05/28 at 09:00. 4. Multiple inverters are underperforming intermittentle due to defective modules. Site has already had 300+ modules swapped before turnover. | 1. SR101218 2. SR101676 3. SR101870 4. SR101433 | SR101676 | SR101870 | SR101433
Bangor - Pushaw | ME | 351814 | 380423.7 | -28609.7 | -7.52% | 675298 | -323484 | -47.9% | 1. Site tripped offline at 00:30 on 05/18, later technician re-energised the site at 11:45 and again the site tripped offline at 15:00 on 05/18. On 05/19 technician re-energised the site and came back online at 08:00. 2. The site tripped offline at 18:00 on 05/19 due to an osprey building a nest on the GOAB pole and later MV crew removed nest and site was back online at 09:00am on 05/20 3. Site tripped offline at 02:15 on 05/23, later technician confirmed that the site will remain offline. On 05/27 USNE checked in to remove bird nest after clearing the bird nest and installing a bird deterrent on the pole. However, the USNE technician discovered that two CTs on the meter cluster were damaged due to arcing and showed signs of physical damage. As a result, technician was unable to re-energize the site. | 1. SR101630 2. SR101682 3. SR101874, SR101953, SR102195 | SR101682 | SR101874 | SR101953 | SR102195

## Jun
Renewable Properties |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 5314466.1814 | 5587244.46 | -272778.2786 | -4.882% | 6224812.5 | -910346.3186 | -14.62%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 0 | 0 | 0 |  | 0 | 0 |  | 1. The site tripped offline on 05/20 at 11:00 and remained offline through the end of the month due to utility work at the substation. | 1. SR101723
Bullis | NY | 807512 | 770478.1 | 37033.9 | 4.807% | 1043895 | -236383 | -22.64% | 1.Inverter 8 was derating by 40kW down for whole month compared to its peers. The inverter was being RMA'd on 06/26. 2.Pad 2 offline from 05/30 and came back online at 12:15 on 06/02 3. The site tripped offline at 12:00 on 06/13 due to a wire damaged by a mouse inside the grounding transformer. The site came back online at 19:00 on 06/16. 4. Site tripped offline from 14:26 to 19:56 on 06/19 due to SEL relay open and site was came back online by remote reset. | 1.SR099753 2.SR102206 3.SR102976 4. SR103173 | SR102206 | SR102976 | SR103173
Rock Island | NY | 868107.5 | 899768.5 | -31661 | -3.519% | 869641.6 | -1534.1 | -0.1764%
Winslow - Roderick | ME | 58177 | 52631.26 | 5545.74 | 10.54% | 78523 | -20346 | -25.91% | Based on actual weather station data, the site is performing close to expected levels, with no major events or anomalies observed during the reporting period
Minoa - Clemons Rd | NY | 535841.5 | 617406.8 | -81565.3 | -13.21% | 640476.9 | -104635.4 | -16.34% | 1.NCU 01 tracker 39 and NCU 02 trackers 44 and 47 (tracker and setpoint at 0°) were stuck. A technician was on site on 05/15 to troubleshoot the trackers. NCU 1 TCU 39 was set to auto and resumed tracking. However, NCU 2 TCU 44 and 47 had blown fuses and will remain stuck until replacements can be installed. On 05/18, NCU 01 tracker 39 got stuck again. 2.Site was offline from 08:00 to 08:30 on 06/13 due to EPC work. | 1. SR098775 2.SR102835 | SR102835
Manchester - Western | ME | 115702.375 | 119325.8 | -3623.425 | -3.037% | 113194.4 | 2507.975 | 2.216%
Batavia - Pike Rd | NY | 649005.0262 | 628358.4 | 20646.6262 | 3.286% | 694104.2 | -45099.1737 | -6.497%
Slayton A & B | NY | 1494008 | 1653374 | -159366 | -9.639% | 1619883 | -125875 | -7.771% | 1.Inverter B.14 underproduced by 40kW and later tripped offline from 14:50 to 15:07 on 06/18. 2. Inverters A.01 through A.24 tripped offline at 09:30 from 06/25 and remained offline rest of the month. Dispatch has been scheduled on 07/01. | 1. SR103146 2. SR103521 | SR103521
Batavia - Alexander Rd | NY | 352361.7802 | 399427.6 | -47065.8198 | -11.78% | 385411.2 | -33049.4198 | -8.575% | 1.NCU 2 tracker 34 struck at 4.96 DEG and 65 struck at -50.74 DEG and also Inverter 05 was impacting production after mid-day. Will need to be investigate. | 1.SR098763
NC: Gibson – Henry Gibson Solar | NC | 127581 | 135983.8 | -8402.8 | -6.179% | 125783.2 | 1797.8 | 1.429% | 1.Site was offline due to relay open on 06/02. On 06/05 at 09:45 site came back online. 2.Site tripped offline at 17:00 from 06/07 due to utility outage. On 06/09 site came back online at 12:45. 3.Inverter 2.08 is derating at 78kW from 06/19 and reporting "External Fan Err". All three fans are being RMA'd. 4.The site tripped offline at 07:30 on 06/20. It came back online at 10:00 on 06/25, but tripped offline again at 17:30 on the same day due to utility voltage fluctuations. The site came back online at 06:30 on 06/27. | 1.SR102290 2. SR102653 3.SR103179 4. SR103189 | SR102653 | SR103179 | SR103189
Bangor - Pushaw | ME | 306170 | 310490.2 | -4320.2 | -1.391% | 653900 | -347730 | -53.18% | 1.Site tripped offline at 02:15 from 05/23. On 06/16 after completing the CT work and the site cam eback onlline at 16:45 on 06/16. | 1.SR101874, SR101953, SR102195 | SR101953 | SR102195

## Jul
Renewable Properties |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 7562208.011 | 8530129.466 | -967921.455 | -11.35% | 8535880.258 | -973672.247 | -11.41%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 82970 | 76440.281 | 6529.719 | 8.542% | 161203.487 | -78233.487 | -48.53% | 1. Site was offline since 05/20 due to substation work. The site was re-energized on 07/17. | 1. SR101723
Bullis | NY | 1043715 | 1019490 | 24225 | 2.376% | 1093836.4 | -50121.4 | -4.582% | 1. Inverter 8 was being RMA'd since 06/26 and it has been replaced on 07/30. The derating issue has been resolved. 2. Site tripped offline at 11:30 on 07/25, PAD A back online at 12:15 and PAD B back online at 18:00. | 1. SR099753 2. SR105028, SR105036 | 11
Rock Island | NY | 646247 | 763663.1 | -117416.1 | -15.38% | 939544.27 | -293297.27 | -31.22% | 1. Inverter 26 started late for the production at 11:45 on 07/14. 2. Site tripped offlie at 15:15 pn 07/21 and re-energized on 07/29. PAD 2 was still with no communications from 07/29 at 11:45 and remained offline. And later back online at 13:30 07/30 | 1. SR104396 2. SR104727
Winslow - Roderick | ME | 753844 | 842287.635 | -88443.635 | -10.5% | 889593.58 | -135749.58 | -15.26% | 1. Site tripped offline at 8:30 and back online at 11:00 on 07/01. 2. Site tripped offline at 7:30 on 07/28 and back online at 14:30 on 07/28. | 1. SR103826 2. SR105144
Minoa - Clemons Rd | NY | 621300.323 | 694368.125 | -73067.802 | -10.52% | 654645.2 | -33344.877 | -5.094% | 1. On 07/02 technician replaced fuses for trackers NCU 1 TCU 39, NCU 2 TCU 44, 46, 47. 2. Site was offline from 9:15 to 10:15 due to MV work on 07/02. 3. Site was offline from 8:30 to 10:45 on 07/08 and from 8:15 to 9:00 on 07/09 due to MV work. 4. Inverter 12 did not start for production on 07/31 and later back online at 11:00AM on same day. | 1. SR098775 SR103960 2. SR103825 3. SR104125 4. SR105427
Manchester - Western | ME | 117215.438 | 123043.68 | -5828.242 | -4.737% | 121217.421 | -4001.983 | -3.301%
Batavia - Pike Rd | NY | 712536 | 696115.648 | 16420.352 | 2.359% | 710823.05 | 1712.95 | 0.241%
Slayton A & B | NY | 1436736 | 1840750.32 | -404014.32 | -21.95% | 1621237.44 | -184501.44 | -11.38% | 1. Inverters A.01 to A.12 are offline since 07/01, additional torubleshooting required. | 1. SR103521, SR104611
Batavia - Alexander Rd | NY | 349084.25 | 426182.177 | -77097.927 | -18.09% | 399752.41 | -50668.16 | -12.67% | 1. On 07/29 technician tighten the loose connections and all trackers were started operating. 2. Site tripped offline at 7:15 and back online at 16:30 on 07/18. | 1. SR098763 2. SR104607
NC: Gibson – Henry Gibson Solar | NC | 1073135 | 1302969 | -229834 | -17.64% | 1253294 | -180159 | -14.37% | 1. On 07/11 technician replaced fuses for inverter 2.08 and the derating issue got reslolved. 2. Total of 17 trackers were struck since 07/07, waitimg for the response from manufacturer for RMA. 3. Inverter 2.12 stopped communicating at 13:30 on 07/17, production cannot confirmed. Inverter required new external fans and remains offline. 4. Inverter 1.13 is derating and reporting a fan error - issue ivery intermittent from 07/25 | 1. SR103179 2. SR104107 3. SR104588 4. SR105061
Bangor - Pushaw | ME | 725425 | 744819.5 | -19394.5 | -2.604% | 690733 | 34692 | 5.022%

## Aug
Renewable Properties |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 7178488.8025 | 8308463.1 | -1129974.2975 | -13.6% | 10167301.9 | -2988813.0975 | -29.4%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 168637 | 156706.7 | 11930.3 | 7.613% | 151369 | 17268 | 11.41%
Bullis | NY | 891570 | 869443.9 | 22126.1 | 2.545% | 982613.9 | -91043.9 | -9.265% | 1. Site was offline from 09:15 to 17:15 on 08/21. 2. Site was offline from 10:00 to 14:30 on 08/01. | 1. SR106633 2. SR105480 | SR105480
Rock Island | NY | 718602 | 911981 | -193379 | -21.2% | 3363879 | -2645277 | -78.64% | 1. Inverter 10 was underproduced 25kW for whole month. 2. inverter 7 was underproduced 45kW from 08/01 to 16:00 on 08/12. On 08/12 the inverter started underperform 13kW compared to peers to end of month 3. Inverter 18 was offline from 11:00 on 08/12 to end of the month. 4. Inverter 28 was offline from 08/01 to 16:00 on 08/11 5. Inverter 1 is underproducing by 11kW, Inverter 2 is underproducing by 12kW, Inverter 6 is underproducing by 20kW, Inverter 11 is underproducing by 20kW, and Inverter 12 is underperforming by 13kW. | 1. SR105851 2.SR105935 3. SR106139 4. SR105541 5. SR107166 | SR105935 | SR106139 | SR105541 | SR107166
Winslow - Roderick | ME | 897010 | 981976.6 | -84966.6 | -8.653% | 733602 | 163408 | 22.27% | 1.Site offline from 09:45 to 11:00 on 08/11 due to technicin was on site | 1.PM2962
Minoa - Clemons Rd | NY | 557804.4275 | 670958.9 | -113154.4725 | -16.86% | 593130.7 | -35326.2725 | -5.956% | 1. All trackers associated with NCU-01 and NCU-02 were stuck from 08/01 to 08/11. For 2 trackers fuses need to be replaced. | 1. SR106818
Manchester - Western | ME | 132513.375 | 141350.8 | -8837.425 | -6.252% | 115894.1 | 16619.275 | 14.34% | 1.Inverter 4 was offline from 06:00 to 09:15 on 08/31 | 1.SR107243
Batavia - Pike Rd | NY | 629972.5 | 613038.7 | 16933.8 | 2.762% | 609270.8 | 20701.7 | 3.398% | 1. NCU 01 TCUs 47 & 117 and setpoints stuck for whole month. | 1. SR098907
Slayton A & B | NY | 1225315 | 1704157 | -478842 | -28.1% | 1453321 | -228006 | -15.69% | 1. Inverters A.01 through A.12 were offline for whole month. Inverters A13 to A40 were offline from 10:45 to 13:00 on 08/12 | 1. SR104611, SR103521 | SR103521
Batavia - Alexander Rd | NY | 346455.5 | 398681.1 | -52225.6 | -13.1% | 350374.2 | -3918.7 | -1.118% | 1. NCU 2 tracker 30 was stuck for whole month, NCU 2 Tracker 13 and setpoint are stuck at 50.76 DEG at 16:30 on 08/18 to end of month. | 1. SR105504
NC: Gibson – Henry Gibson Solar | NC | 872551 | 1022619 | -150068 | -14.67% | 1147040 | -274489 | -23.93% | 1. Inverter 2.09 was derated by 40kW for whole month. 2. Inverter 2.08 was derated at 78kW from 08/01 to 08/15 3. Inverter 1.13 was derated by 50kW from 07/25 to 08/15 4. Inverter 2.12 was offline from 07/23 to 16:00 on 08/01 5. GW01A tracker #3, 9, 15, 16, 26, 48, 50, 52, 56, 60, 62, 68 - 12 trackers and GW01B #86, 101, 107, 111, 113, 114, 123, 125, 129, 130, 131, 135, 137, 145, 146, 149, 150 - 17 trackers total were stuck for whole month | 1. SR106949 2. SR106207 3. SR105061 4. SR104588 5. SR104107 | SR106207 | SR105061 | SR104588 | SR104107
Bangor - Pushaw | ME | 738058 | 837549.4 | -99491.4 | -11.88% | 666807.2 | 71250.8 | 10.69% | 1. Site was offline from 16:00 on 08/17 to 12:00 on 08/20. | 1. SR106400

## Sep
Renewable Properties |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 5922537.855 | 6865670.8 | -943132.945 | -13.74% | 6106753.625 | -184215.77 | -3.017%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA | 125503 | 115285.4 | 10217.6 | 8.863% | 130071.4 | -4568.4 | -3.512%
Bullis | NY | 571796 | 558854.3 | 12941.7 | 2.316% | 793960.6 | -222164.6 | -27.98% | 1.Site tripped offline at 14:19 on 09/10 and back online at 10:15 on 09/15. 2.Site tripped offline at 00:45 on 09/26 and back onine at 8:45 on 09/30. | 1.SR107777 2.SR108597 | SR108597
Rock Island | NY | 677114 | 774316.3 | -97202.3 | -12.55% | 688495.9 | -11381.9 | -1.653% | 1. Inverter 18 was offline from 11:00 on 08/12 and back online at 13:00 on 09/03 2. Inverter 1 has been underproducing by 11 kW since 08:00 on 08/02, while Inverter 2 has been underproducing by 12 kW since 13:15 on 08/05. Inverter 6 has been underproducing by 20 kW since 13:45 on 08/06, and Inverter 12 has been underproducing by 13 kW since 14:30 on the same day. Additionally, Inverter 11 has been underproducing by 20 kW since 16:15 on 08/08. 3.Inverter 10 is underperforming approx. 40kW compared to its peers. 4. Site has tripped offline at 9:30 on 09/22 and back online at 09:15 on 09/23 5. Inverter 17 started late at 09:15 for the production on 09/23 6. Inverter 18 started late at 10:00 for the production on 09/23 | 1.SR106139 2.SR107166 3.SR105851 4.SR108383 5.SR108401 6.SR108402 | SR107166 | SR105851 | SR108383 | SR108401 | SR108402
Winslow - Roderick | ME | 737866 | 796026.2 | -58160.2 | -7.306% | 730600 | 7266 | 0.9945%
Minoa - Clemons Rd | NY | 479813 | 574854.1 | -95041.1 | -16.53% | 137759.225 | 342053.775 | 248.3% | 1.Inverter 12 was offline for whole day on 09/05 and later back online at 13:30 on 09/06. 2. The forecasted values are based on long-term average weather data, typically covering 10–15 years. These values are appear lower; however, the previous month’s figures in PowerTrack seem accurate. The discrepancy observed this month is most likely due to a data glitch. | 1.SR107544
Manchester - Western | ME | 108457 | 116463.8 | -8006.8 | -6.875% | 100955.7 | 7501.3 | 7.43%
Batavia - Pike Rd | NY | 377816.855 | 424891.1 | -47074.245 | -11.08% | 508315.2 | -130498.345 | -25.67% | 1.All inverters tripped offline at 12:30 on 09/05 and later back online at 18:00 on 09/11 2.NCU 01 TCUs 47 & 117 and setpoints stuck for whole month. | 1.SR107531 2.SR098907 | SR098907
Slayton A & B | NY | 1228057 | 1446454 | -218397 | -15.1% | 1116098 | 111959 | 10.03% | 1. Site was taken offline from 12:45 to 14:00 on 09/11 while UNSE was onsite and inverter A.01 through A.12 are back online at 14:00 on 09/11 | 1.SR104611
Batavia - Alexander Rd | NY | 307102 | 358326 | -51224 | -14.3% | 285871.6 | 21230.4 | 7.427% | 1. NCU 2 tracker 30 was stuck for whole month, NCU 2 Tracker 13 and setpoint are stuck at 50.76 DEG at 16:30 on 08/18 to end of month. | 1.SR105504
NC: Gibson – Henry Gibson Solar | NC | 874562 | 1027201 | -152639 | -14.86% | 1026636 | -152074 | -14.81% | 1.Site tripped offline from 10:00 to 10:30 on 09/25 while technician on site. 2. GW01A tracker #3, 9, 15, 16, 26, 48, 50, 52, 56, 60, 62, 68 - 12 trackers and GW01B #86, 101, 107, 111, 113, 114, 123, 125, 129, 130, 131, 135, 137, 145, 146, 149, 150 - 17 trackers total were stuck for whole month | 1.SR108534 2.SR104107 | SR104107
Bangor - Pushaw | ME | 434451 | 672998.6 | -238547.6 | -35.45% | 587990 | -153539 | -26.11% | 1.Inverter tripped offline at 17:00 on 09/09 and back online at 09:30 on 09/17 | 1.SR107648

## Oct
Renewable Properties |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 4685983.145 | 5148255.84 | -462272.695 | -8.979% | 4372914.08 | 313069.065 | 7.159%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Cedar Swamp Rd | MA | 92006 | 88723.21 | 3282.79 | 3.7% | 79875.1 | 12130.9 | 15.19% | 1.Inverter 7 offline on 10/13 and back online on 10/14. | 1.SR109467 | 1.Closed
Bullis | NY | 506507 | 503382.5 | 3124.5 | 0.6207% | 462215.4 | 44291.6 | 9.582% | 1.Site tripped offline at 09:00 on 10/23 and it came back online at 17:45 on 10/24 | 1.SR109868 | 1.Closed
Rock Island | NY | 501417 | 559946.1 | -58529.1 | -10.45% | 428730.6 | 72686.4 | 16.95% | 1.Site tripped offline at 07:15 on 10/05 and it came back online at 09:00 on 10/06 | 1.SR109058 | 1.Closed
Winslow - Roderick | ME | 561151 | 634441.8 | -73290.8 | -11.55% | 524300 | 36851 | 7.029% | 1. Inverter 28 is underproducing by 15kW, inverter 30 is underproducing by 30kW, Inverter 29 is underproducing by 38kW for whole month | 1. SR110592 | 1. New
Minoa - Clemons Rd | NY | 323089 | 403882.4 | -80793.4 | -20% | 284002 | 39087 | 13.76% | 1. 2 trackers being RMA'd. | 1. SR106818 | 1. Pending
Manchester - Western | ME | 83727 | 93869.53 | -10142.53 | -10.8% | 72087.08 | 11639.92 | 16.15% | 1. Inverter 4 has evening shading.
Batavia - Pike Rd | NY | 379610.145 | 371062.9 | 8547.245 | 2.303% | 317743.3 | 61866.845 | 19.47% | 1.The forecasted values are based on long-term average weather data, typically covering 10–15 years. These values are appear lower; however, the previous month’s figures in PowerTrack seem accurate. The discrepancy observed this month is most likely due to a data glitch.
Slayton A & B | NY | 903523 | 984868.3 | -81345.3 | -8.26% | 677584.4 | 225938.6 | 33.34% | 1.Multiple trackers are stuck through out the month | 1. SR109334 | 1.Pending
Batavia - Alexander Rd | NY | 213412 | 265099.1 | -51687.1 | -19.5% | 174711.2 | 38700.8 | 22.15% | 1.NCU 2 tracker 31 and setpoint are tracking out of line with their peers. NCU 2 tracker 9 and setpoint are also out of line from 10/27 at 15:00. | 1.SR109872 | 1.Pending
NC: Gibson – Henry Gibson Solar | NC | 669315 | 755136.1 | -85821.1 | -11.36% | 919844 | -250529 | -27.24% | 1. Tracker were stuck at 0.26 degree from 10/01 to 10/29. | 1. SR109240 | 1. Pending
Bangor - Pushaw | ME | 452226 | 487843.9 | -35617.9 | -7.301% | 431821 | 20405 | 4.725% | 1.Weather station reporting as expected since 10/23 | 1. SR104395 | 1.Closed

## Nov
Renewable Properties |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 2475626.7484 | 2973064.53 | -497437.7816 | -16.73% | 2889410.62 | -413783.8716 | -14.32%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Cedar Swamp Rd | MA | 59869 | 60721.75 | -852.75 | -1.404% | 52769.69 | 7099.31 | 13.45% | 1Inverters 1 and 2 are experiencing a morning shading issue.
Bullis | NY | 182414 | 198463 | -16049 | -8.087% | 281634.9 | -99220.9 | -35.23% | 1. Site tripped and recloser opened at 09:31 on 11/24 and back online at 11:00 on 11/25. Again site was offline from 09:45 to 12:45 on 11/26. Site again tripped offline from 22:30 to 11/30. 2.Site tripped offline at 11:19 and back online at 11:48 on 11/16 | 1.SR111519 2.SR111170 | 1.Pending 2.Closed | SR111170
Rock Island | NY | 171173 | 190221.5 | -19048.5 | -10.01% | 250027.5 | -78854.5 | -31.54% | 1. Inverters 17 & 18 are offline on 11/10 to 11/12 and back online on 11/13. On 11/19 technician has reduced the settings to the inevrters. Inverters 17 & 18 were starting late for the production most of the days throughout the month. | 1.SR110394 | 1.Pending
Winslow - Roderick | ME | 303933 | 390376.5 | -86443.5 | -22.14% | 336400 | -32467 | -9.651% | 1.Inverter 28 is underproducing by 15kW, inverter 30 is underproducing by 30kW, Inverter 29 is underproducing by 38kW. On 11/06 technician stated that these 3 inverters are at the front of the field, obscured by a high treeline. | 1.SR110592 | 1.Closed
Minoa - Clemons Rd | NY | 116325 | 145577.1 | -29252.1 | -20.09% | 167506.9 | -51181.9 | -30.56% | 1.NCU 01 TCU 18, 28, 39, 46, & 50 NCU 02 TCU 12 & 47 has been stuck later technician has replaced replaced fuses and RMA'd 3 TCUs on 11/23. 2.Site tripped offline from 20:45 on 11/03 and later back online at 11:00 on 11/04 3.2 trackers being RMA'd. | 1.SR111071 2.SR110573 3.Pending | 1.Pending 2.Closed | SR110573
Manchester - Western | ME | 45665 | 56472.48 | -10807.48 | -19.14% | 50478.73 | -4813.73 | -9.536% | 1. Inverter 4 has evening shading.
Batavia - Pike Rd | NY | 173465 | 185111.2 | -11646.2 | -6.291% | 203955 | -30490 | -14.95% | 1.TCUs 81 & 100 are stuck. | 1.SR111075 | 1.Pending
Slayton A & B | NY | 393069 | 445603.7 | -52534.7 | -11.79% | 415698.6 | -22629.6 | -5.444% | 1. On 11/07 Tech power cycled tracker system, trackers tracking as expected from 11/07 2.NCU-A.01 tracker 132 and NCU-A.02 tracker 70 are stuck from 11/26 | 1.SR109334 2.SR111761 | 1.Closed 2.Pending | SR111761
Batavia - Alexander Rd | NY | 77810.7484 | 115105.8 | -37295.0516 | -32.4% | 102590.3 | -24779.5516 | -24.15% | 1.NCU 2 tracker 37 and setpoint became stuck soon after the site was re-energized on 11/20. 2.Site tripped offline at 01:30 on 11/19 and back online at 09:15 on 11/20 3.Site tripped offline at 08:15 on 11/28 and back online at remained offline rest of the month. | 1.SR111445 2.SR111293 3.SR111818 | 1.Pending 2.Closed 3.Work in progress | SR111293 | SR111818
NC: Gibson – Henry Gibson Solar | NC | 715922 | 880047.9 | -164125.9 | -18.65% | 704832 | 11090 | 1.573% | 1. Inverters 1 through 19 derating at 1.5kW on 11/26 and later issue resolved by remotely at 14:00 on 11/26 | 1.SR111773 | 1.Closed
Bangor - Pushaw | ME | 235981 | 305363.6 | -69382.6 | -22.72% | 323517 | -87536 | -27.06% | 1.Site production was low due snow or rain on 11/09 , 11/10 , 11/16 , 11/30

## Dec
Renewable Properties |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Cedar Swamp Rd | MA
Bullis | NY
Rock Island | NY
Winslow - Roderick | ME
Minoa - Clemons Rd | NY
Manchester - Western | ME
Batavia - Pike Rd | NY
Slayton A & B | NY
Batavia - Alexander Rd | NY
NC: Gibson – Henry Gibson Solar | NC
Bangor - Pushaw | ME

## Sites
Portfolio: | Renewable Properties
Site DAS Name | Site | State | Update | DAS
60 Cedar Swamp Rd. (Renewable Properties) | Cedar Swamp Rd | MA |  | PowerTrack
Bullis | Bullis | NY | AEF | PowerTrack
Rock Island NY (Renew Prop) | Rock Island | NY |  | PowerTrack
Roderick Road | Winslow - Roderick | ME |  | PowerTrack
Clemons Road | Minoa - Clemons Rd | NY |  | PowerTrack
Western Ave Solar | Manchester - Western | ME |  | PowerTrack
Batavia - Pike Rd | Batavia - Pike Rd | NY |  | PowerTrack
Lockport - Slayton A & B | Slayton A & B | NY |  | PowerTrack
Alexander Road | Batavia - Alexander Rd | NY |  | PowerTrack
Henry Gibson | NC: Gibson – Henry Gibson Solar | NC | AEF | PowerTrack
Pushaw | Bangor - Pushaw | ME | AEF | PowerTrack