## Year to Date
Tortoise |  |  | Year to Date Actual v. Expected |  |  | Year to Date Actual v. Forecasted
Total |  | 11785677.3279 | 15246861.5414 | -3461184.2135 | -22.7% | 13827681.1729 | -2042003.845 | -14.77%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 907332.868 | 1144647.3611 | -237314.4931 | -20.73% | 1115715.8459 | -208382.9779 | -18.68%
San Luis Valley | CO | 2319842.013 | 2144843.64 | 174998.373 | 8.159% | 1165962.856 | 1153879.157 | 98.96%
Golden NREL 2 | CO | 113464.455 | 114665.0682 | -1200.6132 | -1.047% | 132425.991 | -18961.536 | -14.32%
Golden NREL Wind 3 | CO | 655043.0886 | 1291621.934 | -636578.8454 | -49.29% | 715357.6 | -60314.5114 | -8.431%
Pratt Solar Farm | KS | 2589150 | 5187681.909 | -2598531.909 | -50.09% | 4981086.93 | -2391936.93 | -48.02%
Rochester - 5516 Valleyhigh NW | MN | 2374799 | 2609126.2 | -234327.2 | -8.981% | 2510275.5 | -135476.5 | -5.397%
Warsaw - 2201 Richmond | VA | 1384836.1 | 1541238.5 | -156402.4 | -10.15% | 1483119.35 | -98283.25 | -6.627%
Mount Jackson - Randolf | VA | 775388.8032 | 778421.839 | -3033.0358 | -0.3896% | 1000099.6 | -224710.7968 | -22.47%
Callands Gretna - Monroe | VA | 665821 | 434615.09 | 231205.91 | 53.2% | 723637.5 | -57816.5 | -7.99%
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 1st Qtr
Tortoise |  |  | 1st Quarter Actual v. Expected |  |  | 1st Quarter Actual v. Forecasted
Total |  | 7828410.9973 | 9581522.0904 | -1753111.0932 | -18.3% | 8684356.08 | -855945.0827 | -9.856%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 207937 | 274034.5753 | -66097.5753 | -24.12% | 222541.9 | -14604.9 | -6.563%
San Luis Valley | CO | 547486.375 | 553969.5 | -6483.125 | -1.17% | 0 | 547486.375
Golden NREL 2 | CO | 24178 | 22334.8621 | 1843.1379 | 8.252% | 28588.3 | -4410.3 | -15.43%
Golden NREL Wind 3 | CO | 193034.719 | 270721.615 | -77686.896 | -28.7% | 0 | 193034.719
Pratt Solar Farm | KS | 1654930 | 3097059.909 | -1442129.909 | -46.56% | 2716093.93 | -1061163.93 | -39.07%
Rochester - 5516 Valleyhigh NW | MN | 2374799 | 2609126.2 | -234327.2 | -8.981% | 2510275.5 | -135476.5 | -5.397%
Warsaw - 2201 Richmond | VA | 1384836.1 | 1541238.5 | -156402.4 | -10.15% | 1483119.35 | -98283.25 | -6.627%
Mount Jackson - Randolf | VA | 775388.8032 | 778421.839 | -3033.0358 | -0.3896% | 1000099.6 | -224710.7968 | -22.47%
Callands Gretna - Monroe | VA | 665821 | 434615.09 | 231205.91 | 53.2% | 723637.5 | -57816.5 | -7.99%
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 2nd Qtr
Tortoise |  |  | 2nd Quarter Actual v. Expected |  |  | 2nd Quarter Actual v. Forecasted
Total |  | 2153023.2556 | 3627509.5827 | -1474486.3271 | -40.65% | 2716685.012 | -563661.7564 | -20.75%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 210907.068 | 366678.8226 | -155771.7546 | -42.48% | 410180.85 | -199273.782 | -48.58%
San Luis Valley | CO | 712510.75 | 681959.403 | 30551.347 | 4.48% | 0 | 712510.75
Golden NREL 2 | CO | 37323.751 | 36197.9061 | 1125.8449 | 3.11% | 41511.162 | -4187.411 | -10.09%
Golden NREL Wind 3 | CO | 258061.6866 | 452051.451 | -193989.7644 | -42.91% | 0 | 258061.6866
Pratt Solar Farm | KS | 934220 | 2090622 | -1156402 | -55.31% | 2264993 | -1330773 | -58.75%
Rochester - 5516 Valleyhigh NW | MN | 0 | 0 | 0 |  | 0 | 0
Warsaw - 2201 Richmond | VA | 0 | 0 | 0 |  | 0 | 0
Mount Jackson - Randolf | VA | 0 | 0 | 0 |  | 0 | 0
Callands Gretna - Monroe | VA | 0 | 0 | 0 |  | 0 | 0
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 3rd Qtr
Tortoise |  |  | 3rd Quarter Actual v. Expected |  |  | 3rd Quarter Actual v. Forecasted
Total |  | 1194242.564 | 1373129.7533 | -178887.1893 | -13.03% | 1649012.8819 | -454770.3179 | -27.58%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 319437 | 328424.5883 | -8987.5883 | -2.737% | 368930.9259 | -49493.9259 | -13.42%
San Luis Valley | CO | 693812.75 | 610051.393 | 83761.357 | 13.73% | 762465 | -68652.25 | -9.004%
Golden NREL 2 | CO | 35422.001 | 37606.174 | -2184.173 | -5.808% | 41957.956 | -6535.955 | -15.58%
Golden NREL Wind 3 | CO | 145570.813 | 397047.598 | -251476.785 | -63.34% | 475659 | -330088.187 | -69.4%
Pratt Solar Farm | KS | 0 | 0 | 0 |  | 0 | 0
Rochester - 5516 Valleyhigh NW | MN | 0 | 0 | 0 |  | 0 | 0
Warsaw - 2201 Richmond | VA | 0 | 0 | 0 |  | 0 | 0
Mount Jackson - Randolf | VA | 0 | 0 | 0 |  | 0 | 0
Callands Gretna - Monroe | VA | 0 | 0 | 0 |  | 0 | 0
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## 4th Qtr
Tortoise |  |  | 4th Quarter Actual v. Expected |  |  | 4th Quarter Actual v. Forecasted
Total |  | 610000.511 | 664700.1149 | -54699.6039 | -8.229% | 777627.199 | -167626.688 | -21.56%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | %
Alamosa School District | CO | 169051.8 | 175509.3749 | -6457.5749 | -3.679% | 114062.17 | 54989.63 | 48.21%
San Luis Valley | CO | 366032.138 | 298863.344 | 67168.794 | 22.47% | 403497.856 | -37465.718 | -9.285%
Golden NREL 2 | CO | 16540.703 | 18526.126 | -1985.423 | -10.72% | 20368.573 | -3827.87 | -18.79%
Golden NREL Wind 3 | CO | 58375.87 | 171801.27 | -113425.4 | -66.02% | 239698.6 | -181322.73 | -75.65%
Pratt Solar Farm | KS | 0 | 0 | 0 |  | 0 | 0
Rochester - 5516 Valleyhigh NW | MN | 0 | 0 | 0 |  | 0 | 0
Warsaw - 2201 Richmond | VA | 0 | 0 | 0 |  | 0 | 0
Mount Jackson - Randolf | VA | 0 | 0 | 0 |  | 0 | 0
Callands Gretna - Monroe | VA | 0 | 0 | 0 |  | 0 | 0
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0

## Jan
Tortoise |  |  | January Actual v. Expected |  |  | January Actual v. Forecasted
Total |  | 2501712.4954 | 3032066.66 | -530354.1646 | -17.49% | 3048208 | -546495.5046 | -17.93%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 57157 | 78953 | -21796 | -27.61% | 92539.7 | -35382.7 | -38.24% | 1. Inverter 1 was offline on 01/10 and back online on 1/11 and again inverter 1 was offline from 01/21 to 01/25 Inverter 1 will hard starts with low IR., Inverter 2 started late on 01/21 at 12:30pm and inverter 2 tripping on and offline throughout the month due to ZERO SEQUENCE fault | 1.SR095491, SR095824 | SR095824
San Luis Valley | CO | 144650.5 | 160327.5 | -15677 | -9.778% | 0 | 144650.5 |  | 1.Inverter 1 has been offline since 12/02 due to a common-mode fault. Bold Renewables advised replacing the AC contactor, which was replaced on 01/29, and the inverter was brought back online. | 1. SR093905
Golden NREL 2 | CO | 5628 | 5616.3 | 11.7 | 0.2083% | 7739.1 | -2111.1 | -27.28% | 1.Low generation due to weather/snow.
Golden NREL Wind 3 | CO | 45016.5922 | 65286.76 | -20270.1678 | -31.05% | 0 | 45016.5922 |  | 1. As per the meter, 1 inverter is offline and also according to the meter, some trackers do appear to be stuck. | 1. SR096263
Pratt Solar Farm | KS | 641110 | 959485.1 | -318375.1 | -33.18% | 865991.1 | -224881.1 | -25.97% | 1. Inverter 1 is derating by 1000kW due to Impulsion fan comms issue from 11/20 | 1. SR093458
Rochester - 5516 Valleyhigh NW | MN | 748299 | 805370.6 | -57071.6 | -7.086% | 885341.6 | -137042.6 | -15.48% | 1. Inverter 57 was offline throughout the month due to fault permanent power module failure. 2. Inverters 29, 30, 32, 64, 68, 69, 78, and 80 are offline due to a hunt. The LOTO has been applied to the inverters, and all trackers are stuck. | 1. SR094033 2. SR095849 | SR095849
Warsaw - 2201 Richmond | VA | 479142.2 | 554593.9 | -75451.7 | -13.6% | 548915 | -69772.8 | -12.71% | 1. Trackers group A to J are currently in wind stow status for whole month. | 1. SR096181
Mount Jackson - Randolf | VA | 127473.2032 | 147694.2 | -20220.9968 | -13.69% | 364481.5 | -237008.2968 | -65.03% | 1. Site tripped offline on 12/30 due to a squirrel climbing the utility pole and shorting the phase B fuse after installing cut out fuse on 01/21 the site was back online at 11:00am on 01/21. 2. Site was tripped offline at 14:15 on 01/29 due to inverter voltages was dropped & reported "Grid Phase Voltage Out of Range" and site was back online at 16:20 on 01/21. 3. Inverter 23 is underproducing due to FTC tracker - network control unit 2: tracker motor 7 is not tracking. | 1. SR095130 2. SR096122 3. SR096074 | SR096122 | SR096074
Callands Gretna - Monroe | VA | 253236 | 254739.3 | -1503.3 | -0.5901% | 283200 | -29964 | -10.58% | 1.Trackers D28, A27, and C26 are stuck for whole month due to defective batteries. | 1. SR091277
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month due to bad modem. | 1. SR094062

## Feb
Tortoise |  |  | February Actual v. Expected |  |  | February Actual v. Forecasted
Total |  | 3345331.7429 | 3654038.1055 | -308706.3626 | -8.448% | 3375549.1 | -30217.3571 | -0.8952%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 70710 | 90943.2728 | -20233.2728 | -22.25% | 9724.2 | 60985.8 | 627.2% | 1. Inverter 2 was tripping offline for several hours in the middle of the day throughout the month. A synchronization card is required to bring the inverter back to normal. | 1. SR095824
San Luis Valley | CO | 194848 | 185624.7 | 9223.3 | 4.969% | 0 | 194848
Golden NREL 2 | CO | 7116 | 6946.0427 | 169.9573 | 2.447% | 8817.9 | -1701.9 | -19.3% | 1. Low generation due to weather/snow.
Golden NREL Wind 3 | CO | 55115.1429 | 83777.1 | -28661.9571 | -34.21% | 0 | 55115.1429 |  | 1. As per meter data, 1 inverter was offline. Additionally few trackers were struck. Working with NREL for dispatch. | 1. SR096263
Pratt Solar Farm | KS | 609030 | 919002.6 | -309972.6 | -33.73% | 811213.8 | -202183.8 | -24.92% | 1. Inverter 1 is derating by 1000kW due to Impulsion fan comms issue since 11/20. Waiting on DGA syringe to group with the dispatch. | 1. SR093458
Rochester - 5516 Valleyhigh NW | MN | 1053549 | 1144122 | -90573 | -7.916% | 1113658 | -60109 | -5.397% | 1. Inverter 2 tripped offline at 09:04 AM on 02/06/25, reporting a Permanent fault of power module. On 02/07/25, the technician reset the inverter, but the same fault occurred. Chint confirmed a power head failure, and a ticket was issued for replacement. On 02/27/25, the technician replaced the malfunctioning inverter with a new one brought back online at 10:15AM the same day. 2. Inverter 57 back online at 11:45AM on 02/07/25 after technician replaced old powerhead with new. 3.Inverter 9 tripped offline at 09:30 AM on 02/18/25 due to a permanent power module failure. Parts are required to bring it back online, and it remained offline throughout the month 4. Inverter 65 is derated by 50 kW due to an external fan error on 02/21, 02/22. On 02/24/25, a technician found no faults, compared output with nearby inverters (which were similar), and confirmed with Chint that no issues were detected. 5. Inverter 42 was derated by approximately 54 kW compared to its peers due to an external fan error on 02/21 to 02/23. On 02/24/25, a technician discovered a string wrapped around the fans, removed the old pull from the unit, and brought it to the expected production level the same day. 6. Inverter 60 was derating by approximately 50 kW due to an external fan fault issue from 02/27/25. 7. Inverters 29, 30, 64, 68, 69, 78,79 and 80 are offline and confirmed with Hunt these inverters are LOTOd. Additionally all trackers were struck. | 1.SR096391 2. SR094033 3. SR097304 4. SR097622 5. SR097663 6. SR097884 7. SR095849, SR083529, SR085269 | SR094033 | SR097304 | SR097622 | SR097663 | SR097884 | SR095849 | SR083529 | SR085269
Warsaw - 2201 Richmond | VA | 638142.1 | 701308.1 | -63166 | -9.007% | 663175 | -25032.9 | -3.775% | 1. Inverter 21 was derating by 50kW from 02/24 due to External Fan fault. 2. Trackers A to J have been stuck since 01/31/25. On 02/04/25, a technician found 56 stuck trackers across the site. On 02/13/25, the technician removed the fuse and power-cycled each tracker, restoring tracking on most of the site. However, 22 trackers remained stuck, and a ticket was submitted to meet with Soltec technicians to diagnose the recurring communication issue. On 02/18/25, the technician found some trackers were not communicating with RSUs. After installing a new tracker, 12 trackers still required additional troubleshooting. | 1. SR097728 2. SR096181 | SR096181
Mount Jackson - Randolf | VA | 437522.5 | 422842.5 | 14680 | 3.472% | 449760.2 | -12237.7 | -2.721% | 1. Inverter 23 is underproducing due to FTC tracker - network control unit 2 and tracker motor 7 are not tracking. On 02/03/25, the technician found 3 trackers stuck and power-cycled them. After 30 minutes, they resumed tracking, but tracker motor 7 requires additional troubleshooting. On 02/19/25, the technician confirmed with steven and RMA'd the motor. 2. Trackers 8, 10, 45, and 46 have been stuck since 02/16/25. On 02/19/25, the technician found them in the stow position due to defective batteries, requiring additional troubleshooting. By 02/27/25, motors 8 and 45 self-resolved, while 10 and 46 remain stuck. | 1. SR096074, SR096778 2. SR097433, SR097757 | SR096778 | SR097433 | SR097757
Callands Gretna - Monroe | VA | 279299 | 99471.79 | 179827.21 | 180.8% | 319200 | -39901 | -12.5% | 1.The Hukseflux SR15-D1 - POA is missing communication since 02/14/25. GHI, double mod, and BPOA are currently communicating. 2. Trackers D28, A27, and C26 are stuck for whole month due to defective batteries. 3. Multiple tracker motors have been stuck since 02/11/25 due to snow | 1. SR097908 2. SR091277 3. SR096700 | SR091277 | SR096700
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month due to bad modem. | 1. SR094062

## Mar
Tortoise |  |  | March Actual v. Expected |  |  | March Actual v. Forecasted
Total |  | 1981366.759 | 2895417.325 | -914050.566 | -31.57% | 2260598.98 | -279232.221 | -12.35%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 80070 | 104138.3025 | -24068.3025 | -23.11% | 120278 | -40208 | -33.43% | 1.Inverter 2 was tripping offline for several hours in the middle of the day throughout the month. A synchronization card and logic board are required to bring the inverter back to normal. | 1.SR095824
San Luis Valley | CO | 207987.875 | 208017.3 | -29.425 | -0.01415% | 0 | 207987.875 |  | 1.Meter power dropped to zero from 13:15 to 15:30 on 03/06. | 1.SR098228
Golden NREL 2 | CO | 11434 | 9772.5195 | 1661.4805 | 17% | 12031.3 | -597.3 | -4.965%
Golden NREL Wind 3 | CO | 92902.984 | 121657.755 | -28754.771 | -23.64% | 0 | 92902.984 |  | 1. As per meter data, 1 inverter was offline. Additionally few trackers were struck. Working with NREL for dispatch. | 1.SR096263
Pratt Solar Farm | KS | 404790 | 1218572.209 | -813782.209 | -66.78% | 1038889.03 | -634099.03 | -61.04% | 1.Inverter 1 was derating by 1000kw due to Impulsion fan Comms issue since 11/20/24. On 03/04, technician replaced bad exhaust fan with new fan and re-energized the inverter but didn't have the required software needed to configure it for proper operation. Again inverter started derating by 1.7MW due to fan fault from 03/29. 2.Inverter 1 tripped offline at 13:45 on 03/15 due to Fault:197 and back online at 11AM on 03/16 again tripped offline at 12:30 on 03/16 and back online by remote reset at 10:15AM on 03/17. Again tripped offline at 12PM on 03/21 and self resolved and back online on 03/24. 3.Inverter 2 was offline from 03/07 due to Isolation fault and was offline through out the month. | 1.SR093458 & SR099185 2.SR098335 3.SR098248 | SR099185 | SR098335 | SR098248
Rochester - 5516 Valleyhigh NW | MN | 572951 | 659633.6 | -86682.6 | -13.14% | 511275.9 | 61675.1 | 12.06% | 1.Inverter 9 was offline from 02/18 due to Bus (sum) Over Voltage fault and inverter power head was being RMA'D from 02/24. On 03/07, the technician replaced the RMA'd inverter power head with a new unit, and the inverter is now operating in line with peer inverters. 2.Inverter 60 was derating by approximately 50 kW due to an external fan fault issue from 02/27/25 and producing normal after technician replaced RMA'D fan with new fan on 03/10. 3.Inverter 13 has been underproducing by approximately 30 kW compared to its peers since the MC4 connectors were replaced in early December 2024 to resolve ongoing tripping issues. 4.Inverter 64 was offline from 12/18/24 which was LOTO'd. 5.Inverters 29, 30, 64, 68, 69, 78,79 and 80 are offline from 12/26/24 and confirmed with Hunt these inverters are LOTOd. 6.Soltec Tracker Full T01: Motors 22, 77, 138 were stuck. Soltec Tracker Full T02: Motors 4, 21, 23, 32, 37, 58, 61, 83 were stuck. Soltec Tracker Full T03: Motors 13, 52 were stuck. Soltec Tracker Full T04: Motors 1, 11, 27, 28, 29, 32, 39, 51, 57, 65, 75, 88, 94, 112, 113 were stuck through out the month. 7.Energy values are updated till 03/10, and from 03/11 the data is in TrueGreen client templete. | 1.SR097304 2.SR097884 3.SR098364 4.SR099221 5.SR095849 6.SR099224 | SR097884 | SR098364 | SR099221 | SR095849 | SR099224
Warsaw - 2201 Richmond | VA | 267551.8 | 285336.5 | -17784.7 | -6.233% | 271029.35 | -3477.55 | -1.283% | 1.Inverter 21 was derating by 50kW on high irradiance days from 02/24 due to External Fan fault. 2.12 trackers were stuck from 02/18. On 03/10 technician checked in and worked with erika and brought back 5 trackers back online and 4 trackers were still truck. One new tracker has no lights good fuse and module is only putting out 30 V. Will need a new module. 3.Energy values are updated till 03/10 , and from 03/11 the data is in TrueGreen client templete. | 1.SR097728 2.SR096181 | SR096181
Mount Jackson - Randolf | VA | 210393.1 | 207885.139 | 2507.961 | 1.206% | 185857.9 | 24535.2 | 13.2% | 1.Inverter 18 tripped offline at 11:45AM on 03/01 due to Inverter Over Current and self resolved and back online on 03/02. 2.Inverter 15 tripped offline at 13:30 on 03/08 due to Inverter Over Current and self resolved and back online on 03/09. 3.NCU 1 motors 10, & 46 were stuck from 02/16. 4.NCU 2 motor 7 was stuck and motor was being RMA'd from 02/19. 5. Energy values are updated till 03/10, and from 03/11 the data is in TrueGreen client templete. | 1.SR097945 2.SR098302 3.SR097757 4.SR096778 &SR098566 | SR098302 | SR097757 | SR096778 | SR098566
Callands Gretna - Monroe | VA | 133286 | 80404 | 52882 | 65.77% | 121237.5 | 12048.5 | 9.938% | 1.The Hukseflux SR15-D1 - POA is missing communication since 02/14/25 and resumed communication at 16:00 on 03/03. 2.Trackers D28, A27, and C26 have been stuck all month due to bad batteries. On March 3, tech installed 2 new batteries, but 5 trackers remain stuck—3 not yet added, 2 showing low voltage. HMI login failed due to system error. 3.Multiple tracker motors have been stuck since 02/11/25. Shared SPS info with Soltec; awaiting response. Unable to access Soltec internal HMI onsite due to server connection issue. 4.Energy values are updated till 03/10 , and from 03/11 the data is in TrueGreen client templete. | 1.SR097908 2.SR091277 3.SR096700 | SR091277 | SR096700
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1. Site was not communicated for whole month due to bad modem. | 1.SR097305

## Apr
Tortoise |  |  | April Actual v. Expected |  |  | April Actual v. Forecasted
Total |  | 722747.5611 | 1521830.6158 | -799083.0547 | -52.51% | 1234101.5 | -511353.9389 | -41.44%
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 83870 | 117297.4118 | -33427.4118 | -28.5% | 128953.72 | -45083.72 | -34.96% | 1. Inverter 1 was tripped offline at 03:45pm on 04/14 due to damage to the internal components from a thermal event. 2. Bold and ameresco technicians were on site on 04/01 to troubleshoot inverters. Inverter 2 remained offline on 04/01 after installing the new AC contactor and its feeders inverter 2 was back online on 04/02 at 02:25pm. | 1. SR099790 2. SR095824 | SR095824
San Luis Valley | CO | 224573.25 | 232450.6 | -7877.35 | -3.389% | 0 | 224573.25 |  | 1. Meter dropped production upto 219kW on 04/08 and later on 04/11 technician found inverter 4 was offline and was able to reenergize the inverter. | 1. SR099593
Golden NREL 2 | CO | 11155 | 10312.404 | 842.596 | 8.171% | 12834.78 | -1679.78 | -13.09% | 1. On 04/18 and 04/19 the production was low due to bad weather.
Golden NREL Wind 3 | CO | 79519.3111 | 141658.2 | -62138.8889 | 0% | 0 | 79519.3111 |  | 1.As per the meter 1 inverter was offline and also there were struck trackers. Additionally, meter was down about another 146KW and likely 1 inveter offline and another inverter at half production.Working with NREL for dispatch. | 1.SR096263
Pratt Solar Farm | KS | 323630 | 1020112 | -696482 | -68.28% | 1092313 | -768683 | -70.37% | 1. Inverter 1 was derating for whole month fan being replaced and during visit on 04/14 technician found twelve AC capacitors requiring replacement. 2. Inverter 2 was tripped offline on 04/06 at 18:00 due to GFDI. inverter 2 needs DC contactors and possibly capacitors. | 1. SR099994, SR099185 2. SR099478 | SR099185 | SR099478
Rochester - 5516 Valleyhigh NW | MN | 0 | 0 | 0 |  | 0 | 0 |  | 1.These sites are moved to true green portifolio
Warsaw - 2201 Richmond | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1.These sites are moved to true green portifolio
Mount Jackson - Randolf | VA | 0 | 0 | 0 |  | 0 | 0 |  | 1.These sites are moved to true green portifolio
Callands Gretna - Monroe | VA | 0 |  |  |  | 0 | 0 |  | 1.These sites are moved to true green portifolio
Rockbridge Baths - Small Mouth Bass | VA | 0 | 0 | 0 |  | 0

## May
Tortoise |  |  | May Actual v. Expected |  |  | May Actual v. Forecasted
Total |  | 984300.2825 | 1591676.7005 | -607376.418 | -38.16% | 1329590.57 | -345290.2875 | -25.97% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 21782 | 123116.8514 | -101334.8514 | -82.31% | 143312.46 | -121530.46 | -84.8% | 1.Inverter 1 was offline due to damage to internal components caused by a thermal event. On 05/13, a Bold Renewables technician inspected both inverters and site was remained offline from 05/13 to End of the month due to exposed wires and safety concerns and the inverters need further troubleshooting due to faulty parts. | 1.SR101579, SR099790, SR101399 | SR099790 | SR101399
San Luis Valley | CO | 243865.25 | 227071.9 | 16793.35 | 7.396% | 0 | 243865.25
Golden NREL 2 | CO | 13138.97 | 12195.7491 | 943.2209 | 7.734% | 13598.11 | -459.14 | -3.376% | 1. The site was taken offline at 12:35 on 05/27 while a technician was on-site performing a DAS retrofit to the power track, and it was brought back online at 14:21 on 05/28. | 1. SR093280
Golden NREL Wind 3 | CO | 94924.0625 | 158782.2 | -63858.1375 | -40.22% | 0 | 94924.0625 |  | 1. As per the meter 1 inverter was offline for whole month and also there were struck trackers. Additionally, meter was down about another 146KW and likely 1 inveter offline and another inverter at half production.Working with NREL for dispatch. | 1. SR096263
Pratt Solar Farm | KS | 610590 | 1070510 | -459920 | -42.96% | 1172680 | -562090 | -47.93% | 1. Inverter B tripped offline on 04/06 at 18:00 due to a GFDI fault. The inverter requires new DC contactors and possibly capacitors. A technician visited the site on 05/15, installed a new LS filter, and de-energized the inverter; it came back online at 12:00 the same day.Later, on 05/21 at 07:00, Inverter B tripped offline again, reporting an F45 insulation fault. It was remotely reset and came back online at 14:00. Additionally, on 05/22, Inverter B was offline again from 08:45 to 10:30 due to Pratt being on site to replace the SEL-651R reclosing relay on the inverter. 2. Inverter A was derated by 1000KW down on 05/15 at 09:15 technician took the inverter offline to replace capacitors and exhaust fan. later inverter was re-energized at EOD. Additionally, Inverter A was offline from 15:30 to 17:15 on 05/17 while a technician was on site and performing preventive maintenance inspection. Inverter A was intermittently tripping on and off throughout the day on 05/30. | 1. SR099478 SR101785, SR101822 2. SR099994, SR099185, SR102003, SR102210 PM8642 | SR101785 | SR101822 | SR099994 | SR099185 | SR102003 | SR102210
Rochester - 5516 Valleyhigh NW | MN | [7 empty] | 1. These sites are moved to true green portifolio
Warsaw - 2201 Richmond | VA | [7 empty] | 1. These sites are moved to true green portifolio
Mount Jackson - Randolf | VA | [7 empty] | 1. These sites are moved to true green portifolio
Callands Gretna - Monroe | VA | [7 empty] | 1. These sites are moved to true green portifolio
Rockbridge Baths - Small Mouth Bass | VA | [7 empty] | 1. These sites are moved to true green portifolio

## Jun
Tortoise |  |  | June Actual v. Expected |  |  | June Actual v. Forecasted
Total |  | 445975.412 | 514002.2665 | -68026.8544 | -13.23% | 152992.942 | 292982.47 | 191.5% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 105255.068 | 126264.5595 | -21009.4914 | -16.64% | 137914.67 | -32659.602 | -23.68% | 1. Inverter 1 was offline from 06/01 to 17:30 on 06/04 2. Inverter 2 was offline from 06/01 to 17:30 on 06/04 | 1. SR099790, SR101579 2. SR101399, PM9684 | SR101579 | SR101399
San Luis Valley | CO | 244072.25 | 222436.903 | 21635.347 | 9.727% | 0 | 244072.25
Golden NREL 2 | CO | 13029.781 | 13689.753 | -659.972 | -4.821% | 15078.272 | -2048.491 | -13.59% | 1. Site production was low on 06/03, 06/17 due to low irradiance.
Golden NREL Wind 3 | CO | 83618.313 | 151611.051 | -67992.738 | -44.85% | 0 | 83618.313 |  | 1. As per meter 1 inverter was offline for whole month. | 1. SR096263
Pratt Solar Farm | KS | [7 empty] | 1. These sites are moved to Altus portifolio
Rochester - 5516 Valleyhigh NW | MN | [7 empty] | 1. These sites are moved to true green portifolio
Warsaw - 2201 Richmond | VA | [7 empty] | 1. These sites are moved to true green portifolio
Mount Jackson - Randolf | VA | [7 empty] | 1. These sites are moved to true green portifolio
Callands Gretna - Monroe | VA | [7 empty] | 1. These sites are moved to true green portifolio
Rockbridge Baths - Small Mouth Bass | VA | [7 empty] | 1. These sites are moved to true green portifolio

## Jul
Tortoise |  |  | July Actual v. Expected |  |  | July Actual v. Forecasted
Total |  | 408649.72 | 487259.3265 | -78609.6065 | -16.13% | 585527.51 | -176877.79 | -30.21% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 111918 | 114821.1735 | -2903.1735 | -2.528% | 134380.51 | -22462.51 | -16.72% | 1. Inverter 2 was underproducing for whole month. | 1. SR102730
San Luis Valley | CO | 241428.75 | 210534.985 | 30893.765 | 14.67% | 268540 | -27111.25 | -10.1% | 1. Site was taken offline from 14:00 to 15:45 on 07/24 due to transformer work. | 1. SR103430, PM13367
Golden NREL 2 | CO | 12760.89 | 13409.368 | -648.478 | -4.836% | 15123 | -2362.11 | -15.62% | 1. Site production was low on 07/14, 07/29
Golden NREL Wind 3 | CO | 42542.08 | 148493.8 | -105951.72 | -71.35% | 167484 | -124941.92 | -74.6% | 1. Inverter 3 was offline from 07/01 to 07/29 and inverter 2 was offline for whole month. About 30 strings were down and needed connector replacements across the entire site. | 1. SR096263
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Aug
Tortoise |  |  | August Actual v. Expected |  |  | August Actual v. Forecasted
Total |  | 426349.535 | 467620.477 | -41270.942 | -8.826% | 545877.4559 | -119527.9209 | -21.9% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 109827 | 112493.967 | -2666.967 | -2.371% | 112409.4559 | -2582.4559 | -2.297% | 1. Inverter 2 was underproducing by 20 kW since 06/09. | 1. SR102730
San Luis Valley | CO | 239326.5 | 209732.226 | 29594.274 | 14.11% | 258456 | -19129.5 | -7.401%
Golden NREL 2 | CO | 11968.99 | 12742.894 | -773.904 | -6.073% | 13987 | -2018.01 | -14.43% | 1. As per site weather station data, the plant is performing as expected. The forecasted (theoretical) values appear higher because they are based on long-term average weather data (typically 10–15 years). In contrast, actual vs expected generation reflects real-time weather conditions during the period, providing a more accurate measure of current performance.
Golden NREL Wind 3 | CO | 65227.045 | 132651.39 | -67424.345 | -50.83% | 161025 | -95797.955 | -59.49% | 1. Inverter 2 was offline for whole month. About 30 strings were down and needed connector replacements across the entire site. | 1. SR096263
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Sep
Tortoise |  |  | September Actual v. Expected |  |  | September Actual v. Forecasted
Total |  | 359243.309 | 418249.9498 | -59006.6408 | -14.11% | 517607.916 | -158364.607 | -30.6% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO | 97692 | 101109.4478 | -3417.4478 | -3.38% | 122140.96 | -24448.96 | -20.02% | 1. Inverter 2 was underperforming by 20kW for whole month. | 1. SR102730
San Luis Valley | CO | 213057.5 | 189784.182 | 23273.318 | 12.26% | 235469 | -22411.5 | -9.518%
Golden NREL 2 | CO | 10692.121 | 11453.912 | -761.791 | -6.651% | 12847.956 | -2155.835 | -16.78% | 1. Few modules need to be replaced. | 1. SR106365
Golden NREL Wind 3 | CO | 37801.688 | 115902.408 | -78100.72 | -67.38% | 147150 | -109348.312 | -74.31% | 1. Inverter 3 was offline from 09/01 to 09/26. 2. Inverter 2 was offline for whole month. | 1. SR107074 2. SR107072 | SR107072
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Oct
Tortoise |  |  | October Actual v. Expected |  |  | October Actual v. Forecasted
Total |  | 336582.126 | 346016.9449 | -9434.8189 | -2.727% | 474957.199 | -138375.073 | -29.13% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | Status
Alamosa School District | CO | 85038 | 98864.1749 | -13826.1749 | -13.99% | 114062.17 | -29024.17 | -25.45% | 1. Inverter 1 was offline from 09:35 on 10/12 to 10/16. | 1. SR109398 | 1. Closed
San Luis Valley | CO | 206910.138 | 136830.244 | 70079.894 | 51.22% | 217657.856 | -10747.718 | -4.938% | 1. Site was not communicated from 09/30 to 13:00 on 10/09 due to that expected value is showing low. | 1. SR108885 | 1. Closed
Golden NREL 2 | CO | 9698.488 | 10573.856 | -875.368 | -8.279% | 11259.573 | -1561.085 | -13.86% | 1. Few modules need to be replaced. | 1. SR106365 | 1. Closed
Golden NREL Wind 3 | CO | 34935.5 | 99748.67 | -64813.17 | -64.98% | 131977.6 | -97042.1 | -73.53% | 1. Inverter 1 was offline for whole month. 2. Inverter 3 was offline on 10/16, 10/20, 10/21, 10/22, 10/26, 10/28, 10/30, 10/31 based on meter power | 1. SR107072 2. SR109606 | 1. Work in progress 2. New | SR109606
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Nov
Tortoise |  |  | November Actual v. Expected |  |  | November Actual v. Forecasted
Total |  | 273418.385 | 318683.17 | -45264.785 | -14.2% | 302670 | -29251.615 | -9.665% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests | SR Status
Alamosa School District | CO | 84013.8 | 76645.2 | 7368.6 | 9.614% | 0 | 84013.8 |  | 1. Site was offline from 10:30 to 15:15 on 11/27.
San Luis Valley | CO | 159122 | 162033.1 | -2911.1 | -1.797% | 185840 | -26718 | -14.38% | 1. Site was offline from 12:00 on 11/22 to 07:45 on 11/23 2. Site was offline from 10:00 on 11/27 to 06:00 on 11/28. | 1. SR111488 2.SR111803 | 1. Closed 2.Closed | SR111803
Golden NREL 2 | CO | 6842.215 | 7952.27 | -1110.055 | -13.96% | 9109 | -2266.785 | -24.89% | 1. Inverter has morning shading.
Golden NREL Wind 3 | CO | 23440.37 | 72052.6 | -48612.23 | -67.47% | 107721 | -84280.63 | -78.24% | 1. Inverter 3 was offline for whole month. 2. Inverter 2 was offline for whole month. | 1. SR109606 2. SR107072 | 1. Pending 2. Closed | SR107072
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Dec
Tortoise |  |  | December Actual v. Expected |  |  | December Actual v. Forecasted
Total |  | 0 | 0 | 0 | 0% | 0 | 0 | 0% | Some sites are missing actual data; if new sites were added, make sure they are aligned correctly (including prior months!)
Site | State | Actual | Expected | Delta | % | Forecasted | Delta | % | Notes | Service Requests
Alamosa School District | CO
San Luis Valley | CO
Golden NREL 2 | CO
Golden NREL Wind 3 | CO
Pratt Solar Farm | KS
Rochester - 5516 Valleyhigh NW | MN
Warsaw - 2201 Richmond | VA
Mount Jackson - Randolf | VA
Callands Gretna - Monroe | VA
Rockbridge Baths - Small Mouth Bass | VA

## Sites
Portfolio: | Tortoise
Site DAS Name | Site | State | Update | DAS
003 - Alamosa School District | Alamosa School District | CO
002 - San Luis Valley Regional MC | San Luis Valley | CO
002 - NREL 2 | Golden NREL 2 | CO
004 - NREL Wind 3 | Golden NREL Wind 3 | CO
Kenyon Energy KS Solar | Pratt Solar Farm | KS
MN WestSide Solar | Rochester - 5516 Valleyhigh NW | MN
Hemings (VA) - ODEC | Warsaw - 2201 Richmond | VA
Randolf (VA) - ODEC | Mount Jackson - Randolf | VA
Monroe Solar (MEC) - ODEC | Callands Gretna - Monroe | VA
Smallmouth Bass (BARC) - ODEC | Rockbridge Baths - Small Mouth Bass | VA